## 2009
All of the data presented below was copied verbatim from spreadsheets transcribed by Debbie Rideout, Town PLO
| pH | [6 empty] | Chlorine |  |  |  | Colour | [5 empty] | Turbidity | [5 empty] | Total Dissolved Solids |  |  |  |  | Conductivity |  |  |  |  | Hardness |  | Alkalinity |  | Aluminum | Temperature |  | Cl Used | Cl Demand | UVT |  | UVA |  | Flows within plant |  |  |  | Flows from plant |  |  | Chemical Dosages
Date | Raw | PTC | PTC (OL) | SWC | Filter | Finish (OL) | Finish | Free | Total | Sample | Analyzer | Raw A | Raw T | SWC A | Filter A | Finish A | Finish T | Raw | Raw (OL) | SWC | Filter | Finish | Finish (OL) | Raw | PTC | SWC | Filter | Finish | Raw | PTC | SWC | Filter | Finish | Raw | Finish | Raw | Finish | Finish (Free) | Raw | Finish |  |  | Raw | Filter | Raw | Filter | Raw | Finish | Filter | Backwash | Bishop's | Botwood | GFW | Chlorine | Alum | Limestone | Lime
2009-01-01 | 6.99 | 6.44 |  |  |  |  | 7.35 | 1.82 |  |  |  |  | 40 |  |  |  | 0 | 0.341 |  |  | 0.083 | 0.134 | [5 empty] | 24.3 |  |  |  |  | 48.6 |  | 20.9 |  | 10 | 0.094 |  | 3.4 | 89.96 | 1.03 |  |  |  |  | 14.612 | 14.312 | [6 empty] | 14.68 | 14.88 | 6.76
2009-01-02 | 7.18 | 6.41 |  |  |  |  | 7.22 | 1.79 |  |  |  |  | 176 |  |  |  | 0 | 0.307 |  |  | 0.085 | 0.138 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 20.2 |  | 10 | 0.043 |  | 3.7 | 89.96 | 1.09 |  |  |  |  | 14.521 | 14.201 | [6 empty] | 14.68 | 14.88 | 6.76
2009-01-03 | 6.63 | 6.52 |  |  |  |  | 7.34 | 1.82 |  |  |  |  | 54 |  |  |  | 0 | 0.518 |  |  | 0.091 | 0.12 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 23.2 |  | 10 | 0.058 |  | 3.7 | 89.96 | 1.03 |  |  |  |  | 14.66 | 14.34 | [6 empty] | 14.68 | 14.88 | 6.76
2009-01-04 | 6.735 | 6.515 |  |  |  |  | 7.29 | 1.785 |  |  |  |  | 74 |  |  |  | 0 | 0.414 |  |  | 0.143 | 0.141 | [5 empty] | 27.1 |  |  |  |  | 54.2 |  | 23.85 |  | 10 | 0.046 |  | 3.65 | 90.05 | 1.115 |  |  |  |  | 14.881 | 14.113 | [6 empty] | 14.68 | 14.88 | 6.76
2009-01-05 | 6.84 | 6.51 |  |  |  |  | 7.24 | 1.75 |  |  |  |  | 94 |  |  |  | 0 | 0.31 |  |  | 0.195 | 0.162 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 24.5 |  | 10 | 0.034 |  | 3.6 | 90.14 | 1.2 |  |  |  |  | 15.102 | 13.886 | [6 empty] | 14.68 | 14.88 | 6.76
2009-01-06 | 6.8 | 6.48 |  |  |  |  | 1.73 | 1.73 |  |  |  |  | 52 |  |  |  | 0 | 0.275 |  |  | 0.108 | 0.128 | [5 empty] | 27.5 |  |  |  |  | 55.1 |  | 22.6 |  | 10 | 0.046 |  | 3.4 | 86.28 | 1.07 |  |  |  |  | 13.909 | 13.971 | [6 empty] | 14.68 | 14.88 | 6.76
2009-01-07 | 7.32 | 6.395 |  |  |  |  | 4.51 | 4.795 |  |  |  |  | 56 |  |  |  | 0 | 0.158 |  |  | 0.1005 | 0.136 | [5 empty] | 28 |  |  |  |  | 56.05 |  | 22.9 |  | 10 | 0.049 |  | 3.9 | 91.055 | 1.205 |  |  |  |  | 14.151 | 13.7815 | [6 empty] | 14.68 | 14.88 | 6.76
2009-01-08 | 7.84 | 6.31 |  |  |  |  | 7.29 | 7.86 |  |  |  |  | 60 |  |  |  | 0 | 0.041 |  |  | 0.093 | 0.144 | [5 empty] | 28.5 |  |  |  |  | 57 |  | 23.2 |  | 10 | 0.052 |  | 4.4 | 95.83 | 1.34 |  |  |  |  | 14.393 | 13.592 | [6 empty] | 14.68 | 14.88 | 6.76
2009-01-09 | 6.74 | 6.34 |  |  |  |  | 7.22 | 1.69 |  |  |  |  | 64 |  |  |  | 0 | 0.249 |  |  | 0.08 | 0.13 | [5 empty] | 27.5 |  |  |  |  | 55.1 |  | 22.5 |  | 10 | 0.061 |  | 3.1 | 69.41 | 0.61 |  |  |  |  | 14.042 | 13.678 | [6 empty] | 14.68 | 14.88 | 6.76
2009-01-10 | 6.71 | 5.94 |  |  |  |  | 7.55 | 1.78 |  |  |  |  | 60 |  |  |  | 0 | 0.233 |  |  | 0.091 | 0.136 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 22.1 |  | 10 | 0.062 |  | 3 | 85.53 | 1.02 |  |  |  |  | 14.23 | 13.86 | [6 empty] | 14.68 | 14.88 | 6.76
2009-01-11 | 7.08 | 6.22 |  |  |  |  | 7.41 | 1.815 |  |  |  |  | 58.5 |  |  |  | 0 | 0.2895 |  |  | 0.0885 | 0.13 | [5 empty] | 26.7 |  |  |  |  | 53.4 |  | 22.25 |  | 10 | 0.055 |  | 3.2 | 92.31 | 1.23 |  |  |  |  | 14.616 | 13.7905 | [6 empty] | 14.68 | 14.88 | 6.76
2009-01-12 | 7.45 | 6.5 |  |  |  |  | 7.27 | 1.85 |  |  |  |  | 57 |  |  |  | 0 | 0.346 |  |  | 0.086 | 0.124 | [5 empty] | 26 |  |  |  |  | 52 |  | 22.4 |  | 10 | 0.048 |  | 3.4 | 99.09 | 1.44 |  |  |  |  | 15.002 | 13.721 | [6 empty] | 14.68 | 14.88 | 6.76
2009-01-13 | 6.67 | 6.41 |  |  |  |  | 7.39 | 1.91 |  |  |  |  | 74 |  |  |  | 0 | 0.215 |  |  | 0.086 | 0.194 | [5 empty] | 22.8 |  |  |  |  | 45.6 |  | 23.2 |  | 10 | 0.054 |  | 3.7 | 88.99 | 1.02 |  |  |  |  | 14.178 | 13.808 | [6 empty] | 14.68 | 14.88 | 6.76
2009-01-14 | 6.62 | 6.43 |  |  |  |  | 7.28 | 1.71 |  |  |  |  | 64 |  |  |  | 0 | 0.213 |  |  | 0.094 | 0.141 | [5 empty] | 28.6 |  |  |  |  | 57.2 |  | 22.1 |  | 10 | 0.051 |  | 3.1 | 85.55 | 1.19 |  |  |  |  | 13.852 | 13.392 | [6 empty] | 14.68 | 14.88 | 6.76
2009-01-15 | 6.53 | 5.88 |  |  |  |  | 7.36 | 1.92 |  |  |  |  | 26 |  |  |  | 0 | 0.204 |  |  | 0.058 | 0.214 | [5 empty] | 29.5 |  |  |  |  | 59 |  | 28.2 |  | 10 | 0.036 |  | 3.3 | 95.32 | 1.2 |  |  |  |  | 14.237 | 13.852 | [6 empty] | 14.68 | 14.88 | 6.76
2009-01-16 | 6.85 | 6.07 |  |  |  |  | 7.28 | 1.87 |  |  |  |  | 21 |  |  |  | 0 | 0.198 |  |  | 0.062 | 0.165 | [5 empty] | 26.4 |  |  |  |  | 52.8 |  | 28.3 |  | 10 | 0.044 |  | 3.4 | 95.34 | 1.25 |  |  |  |  | 14.288 | 13.864 | [6 empty] | 14.68 | 14.88 | 6.76
2009-01-17 | 6.51 | 6.11 |  |  |  |  | 7.01 | 1.85 |  |  |  |  | 28 |  |  |  | 0 | 0.199 |  |  | 0.061 | 0.155 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 20.5 |  | 10 | 0.048 |  | 3.6 | 94.97 | 1.07 |  |  |  |  | 15.09 | 14.75 | [6 empty] | 14.68 | 14.88 | 6.76
2009-01-18 | 6.45 | 6.19 |  |  |  |  | 7.025 | 1.81 |  |  |  |  | 44.5 |  |  |  | 0 | 0.1955 |  |  | 0.098 | 0.218 | [5 empty] | 29 |  |  |  |  | 57.95 |  | 18.1 |  | 10 | 0.1135 |  | 3.4 | 99.785 | 1.34 |  |  |  |  | 15.1965 | 14.395 | [6 empty] | 15.075 | 14.88 | 6.76
2009-01-19 | 6.39 | 6.27 |  |  |  |  | 7.04 | 1.77 |  |  |  |  | 61 |  |  |  | 0 | 0.192 |  |  | 0.135 | 0.281 | [5 empty] | 29.8 |  |  |  |  | 59.5 |  | 15.7 |  | 10 | 0.179 |  | 3.2 | 104.6 | 1.61 |  |  |  |  | 15.303 | 14.04 | [6 empty] | 15.47 | 14.88 | 6.76
2009-01-20 | 6.38 | 6.12 |  |  |  |  | 7.17 | 1.78 |  |  |  |  | 26 |  |  |  | 0 | 0.183 |  |  | 0.128 | 0.107 | [5 empty] | 26.9 |  |  |  |  | 53.7 |  | 18.6 |  | 10 | 0.087 |  | 3.9 | 90.37 | 1.14 |  |  |  |  | 14.495 | 14.069 | [6 empty] | 14.68 | 14.88 | 6.76
2009-01-21 | 6.67 | 6.08 |  |  |  |  | 7.1 | 1.92 |  |  |  |  | 30 |  |  |  | 0 | 0.18 |  |  | 0.059 | 0.147 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 19.1 |  | 10 | 0.079 |  | 3 | 100.22 | 1.2 |  |  |  |  | 14.948 | 14.579 | [6 empty] | 14.52 | 14.88 | 6.76
2009-01-22 | 6.84 | 6.2 |  |  |  |  | 7.46 | 1.74 |  |  |  |  | 20 |  |  |  | 0 | 0.178 |  |  | 0.064 | 0.157 | [5 empty] | 29.7 |  |  |  |  | 59.4 |  | 20.5 |  | 10 | 0.039 |  | 3.1 | 89.96 | 1.15 |  |  |  |  | 14.564 | 14.122 | [6 empty] | 14.52 | 14.88 | 6.76
2009-01-23 | 6.97 | 5.98 |  |  |  |  | 7.34 | 1.84 |  |  |  |  | 33 |  |  |  | 0 | 0.216 |  |  | 0.083 | 0.124 | [5 empty] | 29.1 |  |  |  |  | 58.2 |  | 21.1 |  | 10 | 0.048 |  | 2.9 | 95.34 | 1.15 |  |  |  |  | 14.868 | 14.487 | [6 empty] | 13.41 | 14.88 | 6.76
2009-01-24 | 6.99 | 5.91 |  |  |  |  | 7.23 | 1.74 |  |  |  |  | 36 |  |  |  | 0 | 0.173 |  |  | 0.093 | 0.15 | [5 empty] | 29.5 |  |  |  |  | 59 |  | 23.4 |  | 10 | 0.053 |  | 3.2 | 94.85 | 1.47 |  |  |  |  | 13.92 | 13.43 | [6 empty] | 13.41 | 14.88 | 6.76
2009-01-25 | 6.72 | 6.46 |  |  |  |  | 7.29 | 1.615 |  |  |  |  | 42 |  |  |  | 0 | 0.1715 |  |  | 0.1055 | 0.2005 | [5 empty] | 29.7 |  |  |  |  | 59.4 |  | 24.05 |  | 10 | 0.046 |  | 3.15 | 99.75 | 1.665 |  |  |  |  | 14.725 | 13.8115 | [6 empty] | 13.41 | 14.88 | 6.76
2009-01-26 | 6.45 | 7.01 |  |  |  |  | 7.35 | 1.49 |  |  |  |  | 48 |  |  |  | 0 | 0.17 |  |  | 0.118 | 0.251 | [5 empty] | 29.9 |  |  |  |  | 59.8 |  | 24.7 |  | 10 | 0.039 |  | 3.1 | 104.65 | 1.86 |  |  |  |  | 15.53 | 14.193 | [6 empty] | 13.41 | 14.88 | 6.76
2009-01-27 | 6.58 | 6.46 |  |  |  |  | 7.4 | 1.63 |  |  |  |  | 46 |  |  |  | 0 | 0.168 |  |  | 0.076 | 0.152 | [5 empty] | 30 |  |  |  |  | 60 |  | 23.7 |  | 10 | 0.049 |  | 2.8 | 92.78 | 1.41 |  |  |  |  | 14.251 | 13.833 | [6 empty] | 13.1 | 14.88 | 6.76
2009-01-28 | 6.71 | 6.37 |  |  |  |  | 7.54 | 1.62 |  |  |  |  | 39 |  |  |  | 0 | 0.165 |  |  | 0.081 | 0.21 | [5 empty] | 28.7 |  |  |  |  | 57.4 |  | 22.7 |  | 10 | 0.584 |  | 3.3 | 99.82 | 1.6 |  |  |  |  | 13.903 | 14.083 | [6 empty] | 12.62 | 14.88 | 6.76
2009-01-29 | 6.17 | 6.01 |  |  |  |  | 7.47 | 1.6 |  |  |  |  | 39 |  |  |  | 0 | 0.17 |  |  | 0.102 | 0.187 | [5 empty] | 28 |  |  |  |  | 56 |  | 23.9 |  | 10 | 0.526 |  | 3 | 54.33 | 0.21 |  |  |  |  | 14.429 | 13.622 | [6 empty] | 13.89 | 14.88 | 6.76
2009-01-30 | 6.19 | 5.9 |  |  |  |  | 7.59 | 1.76 |  |  |  |  | 43 |  |  |  | 0 | 0.16 |  |  | 0.099 | 0.18 | [5 empty] | 29.4 |  |  |  |  | 58.7 |  | 24.4 |  | 10 | 0.083 |  | 2.9 | 95.34 | 1.38 |  |  |  |  | 14.265 | 13.765 | [6 empty] | 13.89 | 14.88 | 6.76
2009-01-31 | 6.43 | 6.16 |  |  |  |  | 6.8 | 1.76 |  |  |  |  | 56 |  |  |  | 0 | 0.161 |  |  | 0.094 | 0.15 | [5 empty] | 30.1 |  |  |  |  | 60.2 |  | 24.4 |  | 10 | 0.036 |  | 3.2 | 94.42 | 1.27 |  |  |  |  | 14.56 | 14.15 | [6 empty] | 13.1 | 14.88 | 7.29
2009-02-01 | 6.435 | 6.64 |  |  |  |  | 7.045 | 1.795 |  |  |  |  | 58 |  |  |  | 0 | 0.196 |  |  | 0.089 | 0.152 | [5 empty] | 30.8 |  |  |  |  | 61.6 |  | 23.85 |  | 10 | 0.2185 |  | 3.05 | 97.31 | 1.37 |  |  |  |  | 14.597 | 13.9585 | [6 empty] | 12.7 | 14.88 | 7.73
2009-02-02 | 6.44 | 7.12 |  |  |  |  | 7.29 | 1.83 |  |  |  |  | 60 |  |  |  | 0 | 0.231 |  |  | 0.084 | 0.154 | [5 empty] | 31.5 |  |  |  |  | 63 |  | 23.3 |  | 10 | 0.401 |  | 2.9 | 100.2 | 1.47 |  |  |  |  | 14.634 | 13.767 | [6 empty] | 12.3 | 14.88 | 8.17
2009-02-03 | 6.41 | 6.2 |  |  |  |  | 7.27 | 1.67 |  |  |  |  | 63 |  |  |  | 0 | 0.161 |  |  | 0.13 | 0.192 | [5 empty] | 28.8 |  |  |  |  | 57.6 |  | 24.5 |  | 10 | 0.049 |  | 2.9 | 95.83 | 1.37 |  |  |  |  | 15.183 | 14.303 | [6 empty] | 11.51 | 14.88 | 8.17
2009-02-04 | 6.43 | 6.47 |  |  |  |  | 7.49 | 1.59 |  |  |  |  | 52 |  |  |  | 0 | 0.149 |  |  | 0.191 | 0.225 | [5 empty] | 30.3 |  |  |  |  | 60.7 |  | 23.1 |  | 10 | 0.056 |  | 3 | 94.82 | 1.56 |  |  |  |  | 14.146 | 13.685 | [6 empty] | 9.92 | 14.88 | 8.17
2009-02-05 | 6.49 | 6.29 |  |  |  |  | 7.42 | 1.43 |  |  |  |  | 60 |  |  |  | 0 | 0.145 |  |  | 0.409 | 0.381 | [5 empty] | 27.9 |  |  |  |  | 55.9 |  | 21.7 |  | 10 | 0.072 |  | 2.9 | 95.26 | 1.6 |  |  |  |  | 14.617 | 14.285 | [6 empty] | 5.96 | 14.88 | 8.17
2009-02-06 | 7.24 | 6.3 |  |  |  |  | 7.47 | 1.53 |  |  |  |  | 57 |  |  |  | 0 | 0.144 |  |  | 0.341 | 0.358 | [5 empty] | 30.7 |  |  |  |  | 61.4 |  | 20.5 |  | 10 | 0.064 |  | 3 | 110 | 1.97 |  |  |  |  | 15.137 | 14.28 | [6 empty] | 5.17 | 14.88 | 8.17
2009-02-07 | 7.45 | 6.33 |  |  |  |  | 7.51 | 1.55 |  |  |  |  | 57 |  |  |  | 0 | 0.14 |  |  | 0.391 | 0.381 | [5 empty] | 29.7 |  |  |  |  | 59.4 |  | 22.3 |  | 10 | 0.088 |  | 2.8 | 94.86 | 1.75 |  |  |  |  | 14.11 | 13.07 | [6 empty] | 5.17 | 14.88 | 8.17
2009-02-08 | 7.085 | 6.315 |  |  |  |  | 7.425 | 1.5 |  |  |  |  | 56.5 |  |  |  | 0 | 0.1355 |  |  | 0.3575 | 0.355 | [5 empty] | 28.6 |  |  |  |  | 57.15 |  | 24.05 |  | 10 | 0.1225 |  | 2.8 | 97.54 | 1.77 |  |  |  |  | 14.4875 | 13.5515 | [6 empty] | 5.17 | 14.88 | 8.17
2009-02-09 | 6.72 | 6.3 |  |  |  |  | 7.34 | 1.45 |  |  |  |  | 56 |  |  |  | 0 | 0.131 |  |  | 0.324 | 0.329 | [5 empty] | 27.5 |  |  |  |  | 54.9 |  | 25.8 |  | 10 | 0.157 |  | 2.8 | 100.22 | 1.79 |  |  |  |  | 14.865 | 14.033 | [6 empty] | 5.17 | 14.88 | 8.17
2009-02-10 | 6.82 | 6.59 |  |  |  |  | 7.37 | 1.53 |  |  |  |  | 57 |  |  |  | 0 | 0.139 |  |  | 0.334 | 0.341 | [5 empty] | 29.3 |  |  |  |  | 58.5 |  | 22.5 |  | 10 | 0.141 |  | 2.9 | 94.88 | 1.56 |  |  |  |  | 14.839 | 13.919 | [6 empty] | 5.17 | 14.88 | 8.17
2009-02-11 | 7.22 | 6.61 |  |  |  |  | 7.29 | 1.55 |  |  |  |  | 52 |  |  |  | 0 | 0.138 |  |  | 0.32 | 0.393 | [5 empty] | 31.6 |  |  |  |  | 63.2 |  | 26.9 |  | 10 | 0.095 |  | 2.7 | 100.24 | 1.58 |  |  |  |  | 15.009 | 14.534 | [6 empty] | 5.17 | 14.88 | 8.17
2009-02-12 | 7.18 | 6.85 |  |  |  |  | 7.23 | 1.49 |  |  |  |  | 41 |  |  |  | 0 | 0.14 |  |  | 0.34 | 0.312 | [5 empty] | 29.6 |  |  |  |  | 59.2 |  | 20.2 |  | 10 | 0.124 |  | 2.6 | 100.64 | 1.7 |  |  |  |  | 14.745 | 14.307 | [6 empty] | 5.17 | 14.8 | 8.17
2009-02-13 | 6.55 | 6.55 |  |  |  |  | 7.44 | 1.51 |  |  |  |  | 51 |  |  |  | 0 | 0.181 |  |  | 0.332 | 7.06 | [5 empty] | 30.5 |  |  |  |  | 61 |  | 22.3 |  | 10 | 0.163 |  | 2.7 | 94.86 | 1.56 |  |  |  |  | 14.869 | 14.012 | [6 empty] | 5.17 | 14.88 | 8.17
2009-02-14 | 6.635 | 6.3875 |  |  |  |  | 7.0525 | 1.925 |  |  |  |  | 39 |  |  |  | 0 | 0.142 |  |  | 0.09875 | 0.17825 | [5 empty] | 28.15 |  |  |  |  | 56.25 |  | 23.55 |  | 10 | 0.02425 |  | 2.675 | 97.6275 | 1.3175 |  |  |  |  | 14.7737 | 14.1595 | [6 empty] | 7.3725 | 14.88 | 8.17
2009-02-15 | 6.67 | 6.365 |  |  |  |  | 7.075 | 1.9 |  |  |  |  | 42 |  |  |  | 0 | 0.14 |  |  | 0.0965 | 0.1685 | [5 empty] | 27.9 |  |  |  |  | 55.8 |  | 23.6 |  | 10 | 0.0275 |  | 2.75 | 96.865 | 1.265 |  |  |  |  | 14.7915 | 13.917 | [6 empty] | 7.195 | 14.88 | 8.17
2009-02-16 | 6.6 | 6.41 |  |  |  |  | 7.03 | 1.95 |  |  |  |  | 36 |  |  |  | 0 | 0.144 |  |  | 0.101 | 0.188 | [5 empty] | 28.4 |  |  |  |  | 56.7 |  | 23.5 |  | 10 | 0.021 |  | 2.6 | 98.39 | 1.37 |  |  |  |  | 14.756 | 13.465 | [6 empty] | 7.55 | 14.88 | 8.17
2009-02-17 | 6.74 | 6.32 |  |  |  |  | 7.12 | 1.85 |  |  |  |  | 48 |  |  |  | 0 | 0.136 |  |  | 0.092 | 0.149 | [5 empty] | 27.4 |  |  |  |  | 54.9 |  | 23.7 |  | 10 | 0.034 |  | 2.9 | 95.34 | 1.16 |  |  |  |  | 14.827 | 14.369 | [6 empty] | 6.84 | 14.88 | 8.17
2009-02-18 | 6.98 | 6.38 |  |  |  |  | 7.25 | 1.87 |  |  |  |  | 49 |  |  |  | 0 | 0.186 |  |  | 0.096 | 0.163 | [5 empty] | 30.8 |  |  |  |  | 61.6 |  | 24.5 |  | 10 | 0.039 |  | 2.8 | 105.11 | 1.44 |  |  |  |  | 14.813 | 14.398 | [6 empty] | 5.96 | 14.88 | 8.17
2009-02-19 | 6.43 | 6.34 |  |  |  |  | 7 | 1.87 |  |  |  |  | 111 |  |  |  | 0 | 0.126 |  |  | 0.092 | 0.165 | [5 empty] | 28.5 |  |  |  |  | 57 |  | 22.6 |  | 10 | 0.038 |  | 2.5 | 94.55 | 1.25 |  |  |  |  | 14.199 | 13.739 | [6 empty] | 5.96 | 14.88 | 8.17
2009-02-20 | 6.58 | 6.24 |  |  |  |  | 7.09 | 1.79 |  |  |  |  | 42 |  |  |  | 0 | 0.122 |  |  | 0.082 | 0.14 | [5 empty] | 29.1 |  |  |  |  | 58.2 |  | 23.3 |  | 10 | 0.044 |  | 2.6 | 89.54 | 1.09 |  |  |  |  | 14.528 | 14.099 | [6 empty] | 5.96 | 14.88 | 8.17
2009-02-21 | 6.43 | 6.46 |  |  |  |  | 7.07 | 1.83 |  |  |  |  | 43 |  |  |  | 0 | 0.121 |  |  | 0.078 | 0.143 | [5 empty] | 29.1 |  |  |  |  | 58.2 |  | 21.8 |  | 10 | 0.038 |  | 2.5 | 95.34 | 1.21 |  |  |  |  | 14.69 | 14.25 | [6 empty] | 5.96 | 14.88 | 8.17
2009-02-22 | 6.71 | 6.385 |  |  |  |  | 7.845 | 1.85 |  |  |  |  | 44 |  |  |  | 0 | 0.122 |  |  | 0.0845 | 0.1525 | [5 empty] | 29.45 |  |  |  |  | 58.9 |  | 21.3 |  | 10 | 0.216 |  | 2.7 | 97.295 | 1.29 |  |  |  |  | 14.944 | 14.081 | [6 empty] | 5.8 | 14.88 | 7.73
2009-02-23 | 6.99 | 6.31 |  |  |  |  | 8.62 | 1.87 |  |  |  |  | 45 |  |  |  | 0 | 0.123 |  |  | 0.091 | 0.162 | [5 empty] | 29.8 |  |  |  |  | 59.6 |  | 20.8 |  | 10 | 0.394 |  | 2.9 | 99.25 | 1.37 |  |  |  |  | 15.198 | 13.912 | [6 empty] | 5.64 | 14.88 | 7.29
2009-02-24 | 6.51 | 6.32 |  |  |  |  | 7.26 | 1.89 |  |  |  |  | 60 |  |  |  | 0 | 0.118 |  |  | 0.083 | 0.146 | [5 empty] | 28.8 |  |  |  |  | 57.6 |  | 24 |  | 10 | 0.386 |  | 2.7 | 94.93 | 1.13 |  |  |  |  | 14.658 | 14.248 | [6 empty] | 5.64 | 14.88 | 7.29
2009-02-25 | 6.34 | 6.15 |  |  |  |  | 7.33 | 1.95 |  |  |  |  | 43 |  |  |  | 0 | 0.122 |  |  | 0.108 | 0.162 | [5 empty] | 28.8 |  |  |  |  | 57.8 |  | 22.4 |  | 10 | 0.201 |  | 2.6 | 100.7 | 1.37 |  |  |  |  | 14.258 | 13.763 | [6 empty] | 5.64 | 14.88 | 7.29
2009-02-26 | 6.48 | 6.14 |  |  |  |  | 8.01 | 1.91 |  |  |  |  | 46 |  |  |  | 0 | 0.121 |  |  | 0.114 | 0.175 | [5 empty] | 29.5 |  |  |  |  | 59.1 |  | 23.1 |  | 10 | 0.212 |  | 2.6 | 99.7 | 1.2 |  |  |  |  | 14.932 | 14.523 | [6 empty] | 5.64 | 14.88 | 7.29
2009-02-27 | 6.74 | 6.36 |  |  |  |  | 6.91 | 1.94 |  |  |  |  | 37 |  |  |  | 0 | 0.125 |  |  | 0.121 | 0.182 | [5 empty] | 29.1 |  |  |  |  | 58.2 |  | 22.6 |  | 10 | 0.101 |  | 2.7 | 99.8 | 1.28 |  |  |  |  | 14.523 | 14.085 | [6 empty] | 5.33 | 14.88 | 8.17
2009-02-28 | 6.7 | 6.53 |  |  |  |  | 7.02 | 1.91 |  |  |  |  | 45 |  |  |  | 0 | 0.126 |  |  | 0.121 | 7.02 | [5 empty] | 24.4 |  |  |  |  | 48.4 |  | 20.3 |  | 10 | 0.094 |  | 2.9 | 100.66 | 1.33 |  |  |  |  | 14.41 | 14.12 | [6 empty] | 5.33 | 14.88 | 8.17
2009-03-01 | 6.46 | 6.5075 |  |  |  |  | 7.0275 | 1.89 |  |  |  |  | 42.75 |  |  |  | 0 | 0.13125 |  |  | 0.121 | 0.1705 | [5 empty] | 29.175 |  |  |  |  | 58.45 |  | 23.375 |  | 10 | 0.1105 |  | 2.65 | 92.7875 | 1.16 |  |  |  |  | 14.5733 | 13.8032 | [6 empty] | 5.33 | 14.88 | 8.17
2009-03-02 | 6.54 | 6.425 |  |  |  |  | 7.005 | 1.91 |  |  |  |  | 44.5 |  |  |  | 0 | 0.1325 |  |  | 0.117 | 0.173 | [5 empty] | 27.55 |  |  |  |  | 55.2 |  | 22.35 |  | 10 | 0.114 |  | 2.7 | 95.125 | 1.18 |  |  |  |  | 14.6215 | 13.9675 | [6 empty] | 5.33 | 14.88 | 8.17
2009-03-03 | 6.38 | 6.59 |  |  |  |  | 7.05 | 1.87 |  |  |  |  | 41 |  |  |  | 0 | 0.13 |  |  | 0.125 | 0.168 | [5 empty] | 30.8 |  |  |  |  | 61.7 |  | 24.4 |  | 10 | 0.107 |  | 2.6 | 90.45 | 1.14 |  |  |  |  | 14.525 | 13.639 | [6 empty] | 5.33 | 14.88 | 8.17
2009-03-04 | 6.7 | 6.26 |  |  |  |  | 6.96 | 1.95 |  |  |  |  | 48 |  |  |  | 0 | 0.135 |  |  | 0.109 | 0.178 | [5 empty] | 24.3 |  |  |  |  | 48.7 |  | 20.3 |  | 10 | 0.121 |  | 2.8 | 99.8 | 1.22 |  |  |  |  | 14.718 | 14.296 | [6 empty] | 5.33 | 14.88 | 8.17
2009-03-05 | 6.92 | 6.26 |  |  |  |  | 6.94 | 1.86 |  |  |  |  | 24 |  |  |  | 20 | 0.163 |  |  | 0.188 | 0.226 | [5 empty] | 31.8 |  |  |  |  | 63.7 |  | 20.2 |  | 10 | 0.094 |  | 2.9 | 100.22 | 1.37 |  |  |  |  | 14.511 | 14.096 | [6 empty] | 5.33 | 14.88 | 9.05
2009-03-06 | 6.04 | 6.18 |  |  |  |  | 7.23 | 1.92 |  |  |  |  | 26 |  |  |  | 3 | 0.16 |  |  | 0.104 | 0.196 | [5 empty] | 31.2 |  |  |  |  | 62.4 |  | 21.1 |  | 10 | 0.048 |  | 2.9 | 100.24 | 1.33 |  |  |  |  | 14.429 | 13.983 | [6 empty] | 5.96 | 14.88 | 9.05
2009-03-07 | 5.97 | 6.3 |  |  |  |  | 5.88 | 1.85 |  |  |  |  | 30 |  |  |  | 4 | 0.231 |  |  | 0.112 | 0.108 | [5 empty] | 22.9 |  |  |  |  | 45.8 |  | 22.6 |  | 10 | 0.053 |  | 2.9 | 95.54 | 1.06 |  |  |  |  | 15.34 | 14.9 | [6 empty] | 5.96 | 14.88 | 9.05
2009-03-08 | 7.165 | 6.05 |  |  |  |  | 6.975 | 1.7475 |  |  |  |  | 74.5 |  |  |  | 0 | 0.1665 |  |  | 0.063 | 0.18425 | [5 empty] | 33.1 |  |  |  |  | 66.2 |  | 33.825 |  | 10 | 0.04675 |  | 2.875 | 91.1625 | 1.1075 |  |  |  |  | 14.8247 | 14.4415 | [6 empty] | 12.7025 | 14.88 | 9.05
2009-03-09 | 7.36 | 5.96 |  |  |  |  | 6.98 | 1.715 |  |  |  |  | 70 |  |  |  | 0 | 0.183 |  |  | 0.074 | 0.1905 | [5 empty] | 32.7 |  |  |  |  | 65.4 |  | 32.45 |  | 10 | 0.0565 |  | 2.95 | 87.645 | 1.055 |  |  |  |  | 14.6995 | 14.332 | [6 empty] | 12.305 | 14.88 | 9.05
2009-03-10 | 6.97 | 6.14 |  |  |  |  | 6.97 | 1.78 |  |  |  |  | 79 |  |  |  | 0 | 0.15 |  |  | 0.052 | 0.178 | [5 empty] | 33.5 |  |  |  |  | 67 |  | 35.2 |  | 10 | 0.037 |  | 2.8 | 94.68 | 1.16 |  |  |  |  | 14.95 | 14.611 | [6 empty] | 13.1 | 14.88 | 9.05
2009-03-11 | 7.75 | 5.78 |  |  |  |  | 6.99 | 1.65 |  |  |  |  | 61 |  |  |  | 6 | 0.216 |  |  | 0.096 | 0.203 | [5 empty] | 31.9 |  |  |  |  | 63.8 |  | 29.7 |  | 10 | 0.076 |  | 3.1 | 80.61 | 0.95 |  |  |  |  | 14.449 | 14.053 | [6 empty] | 11.51 | 14.88 | 9.05
2009-03-12 | 7.57 | 6.26 |  |  |  |  | 7.61 | 1.74 |  |  |  |  | 46 |  |  |  | 7 | 0.142 |  |  | 0.064 | 0.177 | [5 empty] | 33 |  |  |  |  | 66 |  | 23.4 |  | 10 | 0.057 |  | 3 | 79.69 | 0.76 |  |  |  |  | 14.806 | 14.477 | [6 empty] | 11.51 | 14.88 | 9.05
2009-03-13 | 6.235 | 6.11 |  |  |  |  | 7.24 | 1.77 |  |  |  |  | 41 |  |  |  | 2 | 0.146 |  |  | 0.105 | 0.226 | [5 empty] | 28.9 |  |  |  |  | 57.8 |  | 26.8 |  | 10 | 0.073 |  | 2.9 | 85.09 | 0.98 |  |  |  |  | 14.409 | 14.039 | [6 empty] | 11.51 | 14.88 | 9.05
2009-03-14 | 6.21 | 6.22 |  |  |  |  | 7.46 | 1.76 |  |  |  |  | 43 |  |  |  | 2 | 0.14 |  |  | 0.089 | 0.206 | [5 empty] | 29.7 |  |  |  |  | 59.5 |  | 26.6 |  | 10 | 0.083 |  | 3 | 90.87 | 1.08 |  |  |  |  | 14.89 | 14.53 | [6 empty] | 11.19 | 14.88 | 9.05
2009-03-15 | 6.26 | 6.37 |  |  |  |  | 7.1 | 1.745 |  |  |  |  | 42 |  |  |  | 1 | 0.177 |  |  | 0.104 | 0.2015 | [5 empty] | 27.85 |  |  |  |  | 55.75 |  | 26.25 |  | 10 | 0.083 |  | 3.05 | 90.595 | 1.15 |  |  |  |  | 15.015 | 14.2175 | [6 empty] | 11.19 | 14.88 | 9.05
2009-03-16 | 6.31 | 6.52 |  |  |  |  | 6.74 | 1.73 |  |  |  |  | 41 |  |  |  | 0 | 0.214 |  |  | 0.119 | 0.197 | [5 empty] | 26 |  |  |  |  | 52 |  | 25.9 |  | 10 | 0.083 |  | 3.1 | 90.32 | 1.22 |  |  |  |  | 15.14 | 13.905 | [6 empty] | 11.19 | 14.88 | 9.05
2009-03-17 | 6.68 | 6.42 |  |  |  |  | 7.66 | 1.68 |  |  |  |  | 46 |  |  |  | 0 | 0.213 |  |  | 0.099 | 0.246 | [5 empty] | 33.1 |  |  |  |  | 66.2 |  | 24.2 |  | 10 | 0.079 |  | 3.1 | 85.58 | 1.1 |  |  |  |  | 18.272 | 13.963 | [6 empty] | 11.19 | 14.88 | 9.05
2009-03-18 | 6.4 | 6.48 |  |  |  |  | 7.78 | 1.47 |  |  |  |  | 52 |  |  |  | 0 | 0.141 |  |  | 0.458 | 0.388 | [5 empty] | 31.5 |  |  |  |  | 63 |  | 24.4 |  | 10 | 0.146 |  | 3.2 | 79.69 | 1.24 |  |  |  |  | 21.842 | 13.352 | [6 empty] | 11.51 | 14.88 | 9.05
2009-03-19 | 6.76 | 6.54 |  |  |  |  | 6.39 | 1.28 |  |  |  |  | 36 |  |  |  | 0 | 0.142 |  |  | 0.564 | 0.771 | [5 empty] | 30.5 |  |  |  |  | 61 |  | 24.6 |  | 10 | 0.167 |  | 3.3 | 80.68 | 1.24 |  |  |  |  | 20.458 | 14.51 | [6 empty] | 12.3 | 14.88 | 9.05
2009-03-20 | 7.2 | 6.54 |  |  |  |  | 7.11 | 1.99 |  |  |  |  | 37 |  |  |  | 0 | 0.135 |  |  | 0.098 | 0.21 | [5 empty] | 34.2 |  |  |  |  | 68.5 |  | 24.3 |  | 10 | 0.109 |  | 3.2 | 99.73 | 1.01 |  |  |  |  | 14.966 | 15.069 | [6 empty] | 12.3 | 14.88 | 9.05
2009-03-21 | 6.73 | 6.73 |  |  |  |  | 7.06 | 1.95 |  |  |  |  | 54 |  |  |  | 0 | 0.135 |  |  | 0.108 | 0.231 | [5 empty] | 34.4 |  |  |  |  | 68.8 |  | 20.9 |  | 10 | 0.124 |  | 3.2 | 85.07 | 0.69 |  |  |  |  | 14.59 | 14.62 | [6 empty] | 12.3 | 14.88 | 9.05
2009-03-22 | 6.455 | 6.645 |  |  |  |  | 6.61 | 1.925 |  |  |  |  | 46.5 |  |  |  | 0 | 0.1315 |  |  | 0.1205 | 0.2155 | [5 empty] | 30.15 |  |  |  |  | 60.25 |  | 19.4 |  | 10 | 0.1185 |  | 3.3 | 87.275 | 0.855 |  |  |  |  | 14.677 | 14.2725 | [6 empty] | 11.905 | 14.88 | 9.05
2009-03-23 | 6.18 | 6.56 |  |  |  |  | 6.16 | 1.9 |  |  |  |  | 39 |  |  |  | 0 | 0.128 |  |  | 0.133 | 0.2 | [5 empty] | 25.9 |  |  |  |  | 51.7 |  | 17.9 |  | 10 | 0.113 |  | 3.4 | 89.48 | 1.02 |  |  |  |  | 14.764 | 13.925 | [6 empty] | 11.51 | 14.88 | 9.05
2009-03-24 | 6.72 | 6.71 |  |  |  |  | 7.3 | 1.91 |  |  |  |  | 40 |  |  |  | 0 | 0.129 |  |  | 0.09 | 0.201 | [5 empty] | 33.2 |  |  |  |  | 66.4 |  | 21.8 |  | 10 | 0.101 |  | 3.4 | 90.38 | 1 |  |  |  |  | 14.154 | 14.122 | [6 empty] | 11.51 | 14.88 | 9.05
2009-03-25 | 6.8 | 6.72 |  |  |  |  | 7.26 | 1.83 |  |  |  |  | 60 |  |  |  | 0 | 0.131 |  |  | 0.074 | 0.206 | [5 empty] | 33.2 |  |  |  |  | 66.4 |  | 20.3 |  | 10 | 0.065 |  | 3.6 | 90.87 | 0.81 |  |  |  |  | 15.939 | 15.635 | [6 empty] | 11.51 | 14.88 | 9.05
2009-03-26 | 6.28 | 6.72 |  |  |  |  | 7.19 | 1.86 |  |  |  |  | 67 |  |  |  | 0 | 0.129 |  |  | 0.065 | 0.238 | [5 empty] | 35.1 |  |  |  |  | 70.2 |  | 21.3 |  | 10 | 0.092 |  | 3.7 | 100.17 | 0.87 |  |  |  |  | 16.845 | 16.652 | [6 empty] | 11.51 | 14.88 | 9.05
2009-03-27 | 6.55 | 6.19 |  |  |  |  | 6.81 | 1.91 |  |  |  |  | 61 |  |  |  | 0 | 0.183 |  |  | 0.073 | 0.142 | [5 empty] | 31.6 |  |  |  |  | 63.2 |  | 21.6 |  | 10 | 0.084 |  | 3.7 | 100.24 | 0.94 |  |  |  |  | 16.296 | 15.969 | [6 empty] | 10.72 | 14.88 | 9.05
2009-03-28 | 6.06 | 5.92 |  |  |  |  | 6.32 | 1.6 |  |  |  |  | 58 |  |  |  | 0 | 0.196 |  |  | 0.084 | 0.086 | [5 empty] | 26 |  |  |  |  | 52 |  | 22.5 |  | 10 | 0.063 |  | 3.4 | 80.17 | 0.58 |  |  |  |  | 16.86 | 16.67 | [6 empty] | 10.72 | 14.88 | 9.05
2009-03-29 | 6.15 | 5.95 |  |  |  |  | 7.02 | 1.56 |  |  |  |  | 49.5 |  |  |  | 0 | 0.1605 |  |  | 0.0815 | 0.1395 | [5 empty] | 27.65 |  |  |  |  | 55.3 |  | 22 |  | 10 | 0.077 |  | 3.3 | 77.825 | 0.63 |  |  |  |  | 16.734 | 16.133 | [6 empty] | 10.72 | 14.78 | 10.37
2009-03-30 | 6.24 | 5.98 |  |  |  |  | 7.72 | 1.52 |  |  |  |  | 41 |  |  |  | 0 | 0.125 |  |  | 0.079 | 0.193 | [5 empty] | 29.3 |  |  |  |  | 58.6 |  | 21.5 |  | 10 | 0.091 |  | 3.2 | 75.48 | 0.68 |  |  |  |  | 16.608 | 15.596 | [6 empty] | 10.72 | 14.68 | 11.69
2009-03-31 | 6.85 | 6.13 |  |  |  |  | 7.5 | 1.56 |  |  |  |  | 18 |  |  |  | 0 | 0.128 |  |  | 0.063 | 0.063 | [5 empty] | 34.1 |  |  |  |  | 68.3 |  | 22 |  | 10 | 0.099 |  | 3.7 | 79.71 | 0.93 |  |  |  |  | 14.804 | 14.533 | [6 empty] | 10.72 | 14.88 | 10.81
2009-04-01 | 6.92 | 6.35 |  |  |  |  | 7.51 | 1.5 |  |  |  |  | 26 |  |  |  | 0 | 0.186 |  |  | 0.072 | 0.072 | [5 empty] | 34.3 |  |  |  |  | 68.6 |  | 23.5 |  | 10 | 0.087 |  | 3.7 | 75.21 | 0.81 |  |  |  |  | 15.078 | 14.782 | [6 empty] | 9.92 | 14.88 | 10.81
2009-04-02 | 6.01 | 6.17 |  |  |  |  | 7.18 | 1.51 |  |  |  |  | 30 |  |  |  | 0 | 0.13 |  |  | 0.073 | 0.184 | [5 empty] | 33.7 |  |  |  |  | 67.4 |  | 23.6 |  | 10 | 0.072 |  | 4.6 | 80.2 | 0.87 |  |  |  |  | 15.597 | 15.304 | [6 empty] | 9.92 | 14.88 | 10.81
2009-04-03 | 6.25 | 6.75 |  |  |  |  | 7.2 | 1.46 |  |  |  |  | 28 |  |  |  | 0 | 0.129 |  |  | 0.067 | 0.216 | [5 empty] | 32.5 |  |  |  |  | 65.1 |  | 22.8 |  | 10 | 0.086 |  | 4.2 | 75.79 | 0.89 |  |  |  |  | 14.966 | 14.649 | [6 empty] | 9.92 | 14.88 | 10.81
2009-04-04 | 6.26 | 6.33 |  |  |  |  | 7.25 | 1.43 |  |  |  |  | 46 |  |  |  | 0 | 0.142 |  |  | 0.06 | 0.191 | [5 empty] | 31.5 |  |  |  |  | 63 |  | 24.1 |  | 10 | 0.072 |  | 3.8 | 84.67 | 1.23 |  |  |  |  | 14.76 | 14.44 | [6 empty] | 9.13 | 14.88 | 9.93
2009-04-05 | 6.57 | 5.935 |  |  |  |  | 7.2 | 1.535 |  |  |  |  | 47 |  |  |  | 0 | 0.1625 |  |  | 0.0655 | 0.1845 | [5 empty] | 31.4 |  |  |  |  | 62.8 |  | 24.25 |  | 10 | 0.0765 |  | 3.7 | 87.075 | 1.155 |  |  |  |  | 15.4245 | 14.68 | [6 empty] | 9.13 | 14.88 | 9.93
2009-04-06 | 6.88 | 5.54 |  |  |  |  | 7.15 | 1.64 |  |  |  |  | 48 |  |  |  | 0 | 0.183 |  |  | 0.071 | 0.178 | [5 empty] | 31.3 |  |  |  |  | 62.6 |  | 24.4 |  | 10 | 0.081 |  | 3.6 | 89.48 | 1.08 |  |  |  |  | 16.089 | 14.92 | [6 empty] | 9.13 | 14.88 | 9.93
2009-04-07 | 5.97 | 6.33 |  |  |  |  | 7.23 | [5 empty] | 14 |  |  |  | 0 | 0.13 |  |  | 0.04 | 0.176 | [5 empty] | 31.7 |  |  |  |  | 63.4 |  | 23.4 |  | 10 | 0.081 |  | 3.4 | 82.135 | 1.08 |  |  |  |  | 15.745 | 15.536 | [6 empty] | 9.13 | 14.88 | 9.93
2009-04-08 | 6.88 | 6.5 |  |  |  |  | 6.97 | 1.31 |  |  |  |  | 14 |  |  |  | 0 | 0.123 |  |  | 0.16 | 0.129 | [5 empty] | 31.4 |  |  |  |  | 62.9 |  | 23.9 |  | 10 | 0.034 |  | 3.4 | 74.79 | 1.08 |  |  |  |  | 14.525 | 14.214 | [6 empty] | 9.13 | 14.88 | 9.93
2009-04-09 | 6.84 | 6.34 |  |  |  |  | 7.47 | 1.34 |  |  |  |  | 48 |  |  |  | 0 | 0.132 |  |  | 0.043 | 0.117 | [5 empty] | 31.1 |  |  |  |  | 62.3 |  | 21.4 |  | 10 | 0.041 |  | 3.1 | 75.3 | 0.95 |  |  |  |  | 15.092 | 14.882 | [6 empty] | 9.13 | 14.88 | 9.93
2009-04-10 | 6.75 | 6.64 |  |  |  |  | 7.11 | 1.52 |  |  |  |  | 63 |  |  |  | 0 | 0.134 |  |  | 0.071 | 0.222 | [5 empty] | 28.4 |  |  |  |  | 56.7 |  | 20.3 |  | 10 | 0.054 |  | 3.3 | 83.26 | 1.1 |  |  |  |  | 14.6 | 14.428 | [6 empty] | 9.13 | 14.88 | 8.52
2009-04-11 | 6.81 | 6.63 |  |  |  |  | 7.36 | 1.46 |  |  |  |  | 53 |  |  |  | 0 | 0.137 |  |  | 0.068 | 0.161 | [5 empty] | 26.3 |  |  |  |  | 52.6 |  | 20 |  | 10 | 0.121 |  | 3 | 80.53 | 1.08 |  |  |  |  | 13.87 | 14.37 | [6 empty] | 9.13 | 14.88 | 8.52
2009-04-12 | 6.64 | 6.805 |  |  |  |  | 7.005 | 1.41 |  |  |  |  | 51.5 |  |  |  | 0 | 0.136 |  |  | 0.301 | 0.1495 | [5 empty] | 24.2 |  |  |  |  | 48.4 |  | 16.95 |  | 10 | 0.1335 |  | 3.1 | 85.245 | 1.315 |  |  |  |  | 14.431 | 14.1935 | [6 empty] | 9.13 | 14.88 | 9.225
2009-04-13 | 6.47 | 6.98 |  |  |  |  | 6.65 | 1.36 |  |  |  |  | 50 |  |  |  | 0 | 0.135 |  |  | 0.534 | 0.138 | [5 empty] | 22.1 |  |  |  |  | 44.2 |  | 13.9 |  | 10 | 0.146 |  | 3.2 | 89.96 | 1.55 |  |  |  |  | 14.992 | 14.017 | [6 empty] | 9.13 | 14.88 | 9.93
2009-04-14 | 6.69 | 6.9 |  |  |  |  | 6.35 | 1.49 |  |  |  |  | 51 |  |  |  | 0 | 0.131 |  |  | 0.074 | 0.425 | [5 empty] | 24.2 |  |  |  |  | 48.4 |  | 14.2 |  | 10 | 0.134 |  | 3.4 | 90.93 | 1.41 |  |  |  |  | 14.805 | 14.22 | [6 empty] | 10.72 | 14.88 | 9.93
2009-04-15 | 6.64 | 6.74 |  |  |  |  | 5.34 | 1.69 |  |  |  |  | 79 |  |  |  | 0 | 0.13 |  |  | 0.056 | 0.056 | [5 empty] | 19.9 |  |  |  |  | 39.9 |  | 14.5 |  | 10 | 0.192 |  | 3.5 | 79.71 | 0.79 |  |  |  |  | 15.393 | 14.6 | [6 empty] | 9.13 | 14.88 | 9.93
2009-04-16 | 6.29 | 5.61 |  |  |  |  | 5.44 | 1.7 |  |  |  |  | 79 |  |  |  | 0 | 0.133 |  |  | 0.098 | 0.051 | [5 empty] | 19.7 |  |  |  |  | 39.4 |  | 19.4 |  | 10 | 0.124 |  | 3.8 | 80.46 | 0.78 |  |  |  |  | 15.514 | 14.744 | [6 empty] | 9.13 | 14.88 | 9.93
2009-04-17 | 5.64 | 5.41 |  |  |  |  | 5.32 | 1.89 |  |  |  |  | 66 |  |  |  | 0 | 0.188 |  |  | 0.087 | 0.087 | [5 empty] | 16.6 |  |  |  |  | 33.2 |  | 19.9 |  | 10 | 0.116 |  | 3.8 | 100.22 | 0.98 |  |  |  |  | 16.621 | 15.834 | [6 empty] | 8.66 | 13.82 | 9.93
2009-04-18 | 5.76 | 6.29 |  |  |  |  | 5.8 | 1.69 |  |  |  |  | 78 |  |  |  | 0 | 0.213 |  |  | 0.097 | 0.048 | [5 empty] | 18.3 |  |  |  |  | 36.6 |  | 21.7 |  | 10 | 0.098 |  | 4.2 | 80.84 | 0.83 |  |  |  |  | 15.34 | 14.58 | [6 empty] | 8.66 | 13.82 | 9.93
2009-04-19 | 6.02 | 6.235 |  |  |  |  | 5.765 | 1.675 |  |  |  |  | 68.5 |  |  |  | 0 | 0.173 |  |  | 0.1035 | 0.1505 | [5 empty] | 17.3 |  |  |  |  | 34.55 |  | 21.35 |  | 10 | 0.086 |  | 4.2 | 85.37 | 0.95 |  |  |  |  | 15.9725 | 14.771 | [6 empty] | 8.66 | 14.35 | 9.93
2009-04-20 | 6.28 | 6.18 |  |  |  |  | 5.73 | 1.66 |  |  |  |  | 59 |  |  |  | 0 | 0.133 |  |  | 0.11 | 0.253 | [5 empty] | 16.3 |  |  |  |  | 32.5 |  | 21 |  | 10 | 0.074 |  | 4.2 | 89.9 | 1.07 |  |  |  |  | 16.605 | 14.962 | [6 empty] | 8.66 | 14.88 | 9.93
2009-04-21 | 5.93 | 6.34 |  |  |  |  | 5.67 | 1.47 |  |  |  |  | 40 |  |  |  | 0 | 0.12 |  |  | 0.056 | 0.036 | [5 empty] | 17.2 |  |  |  |  | 34.5 |  | 17.8 |  | 10 | 0.178 |  | 4.4 | 75.72 | 0.84 |  |  |  |  | 15.625 | 14.902 | [6 empty] | 8.66 | 14.88 | 9.93
2009-04-22 | 7.48 | 6.12 |  |  |  |  | 7.25 | 1.41 |  |  |  |  | 43 |  |  |  | 0 | 0.122 |  |  | 0.179 | 0.2189 | [5 empty] | 22 |  |  |  |  | 44 |  | 18.9 |  | 10 | 0.084 |  | 4.6 | 79.69 | 1.14 |  |  |  |  | 14.926 | 14.178 | [6 empty] | 8.66 | 14.88 | 9.08
2009-04-23 | 6.41 | 5.87 |  |  |  |  | 7.77 | 1.44 |  |  |  |  | 41 |  |  |  | 0 | 0.186 |  |  | 0.099 | 0.173 | [5 empty] | 25 |  |  |  |  | 50 |  | 21.1 |  | 10 | 0.073 |  | 4.7 | 75.3 | 0.85 |  |  |  |  | 15.609 | 14.933 | [6 empty] | 8.66 | 14.88 | 8.17
2009-04-24 | 6.38 | 6.3 |  |  |  |  | 7.57 | 1.49 |  |  |  |  | 28 |  |  |  | 0 | 0.121 |  |  | 0.08 | 0.199 | [5 empty] | 24.3 |  |  |  |  | 48.6 |  | 19.4 |  | 10 | 0.077 |  | 4.6 | 75.52 | 0.85 |  |  |  |  | 15.389 | 14.655 | [6 empty] | 9.45 | 14.88 | 8.17
2009-04-25 | 6.68 | 6.81 |  |  |  |  | 7.34 | 1.66 |  |  |  |  | 26 |  |  |  | 0 | 0.121 |  |  | 0.077 | 0.129 | [5 empty] | 24.6 |  |  |  |  | 49.3 |  | 20.9 |  | 10 | 0.081 |  | 4.7 | 80.88 | 0.78 |  |  |  |  | 15.69 | 15.03 | [6 empty] | 9.45 | 14.88 | 8.12
2009-04-26 | 7.265 | 6.67 |  |  |  |  | 7.53 | 1.74 |  |  |  |  | 34 |  |  |  | 0 | 0.1485 |  |  | 0.108 | 0.17 | [5 empty] | 24.25 |  |  |  |  | 48.55 |  | 20.35 |  | 10 | 0.073 |  | 4.4 | 90.8 | 0.985 |  |  |  |  | 16.1705 | 15.1115 | [6 empty] | 9.29 | 14.88 | 9.025
2009-04-27 | 7.85 | 6.53 |  |  |  |  | 7.72 | 1.82 |  |  |  |  | 42 |  |  |  | 0 | 0.176 |  |  | 0.139 | 0.211 | [5 empty] | 23.9 |  |  |  |  | 47.8 |  | 19.8 |  | 10 | 0.065 |  | 4.1 | 100.72 | 1.19 |  |  |  |  | 16.651 | 15.193 | [6 empty] | 9.13 | 14.88 | 9.93
2009-04-28 | 7.31 | 6.54 |  |  |  |  | 7.24 | 1.75 |  |  |  |  | 16 |  |  |  | 0 | 0.174 |  |  | 0.078 | 0.169 | [5 empty] | 23.5 |  |  |  |  | 47 |  | 21.5 |  | 10 | 0.096 |  | 4.5 | 95.08 | 0.74 |  |  |  |  | 17.972 | 17.308 | [6 empty] | 9.45 | 14.88 | 8.17
2009-04-29 | 6.46 | 6.83 |  |  |  |  | 7.53 | 1.54 |  |  |  |  | 42 |  |  |  | 0 | 0.181 |  |  | 0.154 | 0.095 | [5 empty] | 24.6 |  |  |  |  | 49.3 |  | 21.3 |  | 10 | 0.087 |  | 4.9 | 70.67 | 0.56 |  |  |  |  | 15.96 | 15.248 | [6 empty] | 9.45 | 14.88 | 8.17
2009-04-30 | 6.49 | 6.49 |  |  |  |  | 7.89 | 1.5 |  |  |  |  | 36 |  |  |  | 0 | 0.169 |  |  | 0.434 | 0.122 | [5 empty] | 24.6 |  |  |  |  | 49.3 |  | 21.1 |  | 10 | 0.081 |  | 4.9 | 64.76 | 0.52 |  |  |  |  | 15.269 | 14.532 | [6 empty] | 9.45 | 14.88 | 8.17
2009-05-01 | 6.45 | 6.23 |  |  |  |  | 7.86 | 1.48 |  |  |  |  | 37 |  |  |  | 0 | 0.169 |  |  | 0.067 | 0.079 | [5 empty] | 24 |  |  |  |  | 48 |  | 22.3 |  | 10 | 0.074 |  | 5.3 | 74.04 | 0.83 |  |  |  |  | 15.302 | 14.603 | [6 empty] | 9.45 | 13.29 | 8.17
2009-05-02 | 6.8 | 6.69 |  |  |  |  | 7.41 | 1.63 |  |  |  |  | 40 |  |  |  | 0 | 0.61 |  |  | 0.091 | 0.083 | [5 empty] | 26 |  |  |  |  | 53.4 |  | 20.6 |  | 10 | 0.092 |  | 5.6 | 74.82 | 0.69 |  |  |  |  | 15.27 | 14.65 | [6 empty] | 9.13 | 13.29 | 7.64
2009-05-03 | 6.95 | 6.78 |  |  |  |  | 7.54 | 1.585 |  |  |  |  | 33 |  |  |  | 0 | 0.4785 |  |  | 0.1075 | 0.115 | [5 empty] | 24.95 |  |  |  |  | 50.6 |  | 22.2 |  | 10 | 0.089 |  | 6.35 | 79.945 | 0.805 |  |  |  |  | 16.261 | 15.169 | [6 empty] | 9.13 | 13.29 | 7.375
2009-05-04 | 7.1 | 6.87 |  |  |  |  | 7.67 | 1.54 |  |  |  |  | 26 |  |  |  | 0 | 0.347 |  |  | 0.124 | 0.147 | [5 empty] | 23.9 |  |  |  |  | 47.8 |  | 23.8 |  | 10 | 0.086 |  | 7.1 | 85.07 | 0.92 |  |  |  |  | 17.252 | 15.688 | [6 empty] | 9.13 | 13.29 | 7.11
2009-05-05 | 6.97 | 6.99 |  |  |  |  | 7.55 | 1.53 |  |  |  |  | 24 |  |  |  | 0 | 0.31 |  |  | 0.054 | 0.091 | [5 empty] | 23.3 |  |  |  |  | 46.6 |  | 20.8 |  | 10 | 0.111 |  | 7.7 | 90.14 | 1.06 |  |  |  |  | 16.436 | 15.784 | [6 empty] | 9.13 | 13.29 | 7.11
2009-05-06 | 6.85 | 6.27 |  |  |  |  | 7.47 | 1.49 |  |  |  |  | 22 |  |  |  | 0 | 0.269 |  |  | 0.061 | 0.061 | [5 empty] | 24.6 |  |  |  |  | 49.3 |  | 20.1 |  | 10 | 0.101 |  | 7.5 | 89.48 | 1.02 |  |  |  |  | 16.883 | 16.173 | [6 empty] | 8.02 | 13.29 | 7.11
2009-05-07 | 7.89 | 6.37 |  |  |  |  | 7.84 | 1.46 |  |  |  |  | 64 |  |  |  | 0 | 0.285 |  |  | 0.063 | 0.237 | [5 empty] | 22.6 |  |  |  |  | 45.2 |  | 7.7 |  | 10 | 0.114 |  | 8.9 | 70.89 | 0.58 |  |  |  |  | 16.446 | 15.768 | [6 empty] | 7.55 | 12.22 | 7.11
2009-05-08 | 6.29 | 6.91 |  |  |  |  | 7.39 | 1.42 |  |  |  |  | 61 |  |  |  | 0 | 0.403 |  |  | 0.056 | 0.083 | [5 empty] | 20.1 |  |  |  |  | 40.2 |  | 8.6 |  | 10 | 0.103 |  | 9.6 | 84.67 | 1.07 |  |  |  |  | 16.127 | 15.413 | [6 empty] | 7.55 | 12.22 | 6.58
2009-05-09 | 6.34 | 6.97 |  |  |  |  | 7.88 | 1.4 |  |  |  |  | 60 |  |  |  | 0 | 0.424 |  |  | 0.069 | 0.081 | [5 empty] | 21.5 |  |  |  |  | 43 |  | 13 |  | 10 | 0.098 |  | 8.9 | 64.61 | 0.52 |  |  |  |  | 16.008 | 15.242 | [6 empty] | 7.55 | 12.22 | 6.58
2009-05-10 | 6.58 | 6.945 |  |  |  |  | 7.61 | 1.51 |  |  |  |  | 72 |  |  |  | 0 | 0.3855 |  |  | 0.0905 | 0.118 | [5 empty] | 21.85 |  |  |  |  | 43.8 |  | 15.9 |  | 10 | 0.1035 |  | 8.2 | 70.7 | 0.56 |  |  |  |  | 16.656 | 15.4595 | [6 empty] | 7.39 | 12.22 | 6.58
2009-05-11 | 6.82 | 6.92 |  |  |  |  | 7.34 | 1.62 |  |  |  |  | 84 |  |  |  | 0 | 0.347 |  |  | 0.112 | 0.155 | [5 empty] | 22.2 |  |  |  |  | 44.6 |  | 18.8 |  | 10 | 0.109 |  | 7.5 | 76.79 | 0.6 |  |  |  |  | 17.304 | 15.677 | [6 empty] | 7.23 | 12.22 | 6.58
2009-05-12 | 8.13 | 6.76 |  |  |  |  | 7.16 | 1.8 |  |  |  |  | 24 |  |  |  | 0 | 0.266 |  |  | 0.053 | 0.053 | [5 empty] | 21.8 |  |  |  |  | 43.7 |  | 15.7 |  | 10 | 0.062 |  | 7 | 99.72 | 0.99 |  |  |  |  | 16.939 | 16.22 | [6 empty] | 7.23 | 12.22 | 6.58
2009-05-13 | 7.17 | 6.9 |  |  |  |  | 7.44 | 1.86 |  |  |  |  | 31 |  |  |  | 0 | 0.421 |  |  | 0.068 | 0.083 | [5 empty] | 21.4 |  |  |  |  | 42.8 |  | 18.2 |  | 10 | 0.074 |  | 6.8 | 105.47 | 1.17 |  |  |  |  | 16.483 | 15.808 | [6 empty] | 7.23 | 12.22 | 6.58
2009-05-14 | 5.42 | 6.74 |  |  |  |  | 7.25 | 1.83 |  |  |  |  | 37 |  |  |  | 0 | 0.251 |  |  | 0.182 | 0.179 | [5 empty] | 18.3 |  |  |  |  | 36.6 |  | 19 |  | 10 | 0.129 |  | 8 | 104.63 | 1.08 |  |  |  |  | 17.01 | 16.33 | [6 empty] | 7.23 | 12.22 | 6.58
2009-05-15 | 6.28 | 5.83 |  |  |  |  | 7.39 | 1.8 |  |  |  |  | 44 |  |  |  | 0 | 0.267 |  |  | 0.134 | 0.134 | [5 empty] | 22.1 |  |  |  |  | 44.3 |  | 18.9 |  | 10 | 0.087 |  | 8.9 | 90.71 | 0.92 |  |  |  |  | 15.825 | 15.117 | [6 empty] | 7.23 | 12.22 | 6.58
2009-05-16 | 6.65 | 6.57 |  |  |  |  | 7.42 | 1.77 |  |  |  |  | 45 |  |  |  | 0 | 0.301 |  |  | 0.136 | 0.127 | [5 empty] | 22.3 |  |  |  |  | 44.6 |  | 21.7 |  | 10 | 0.091 |  | 8.9 | 89.46 | 0.86 |  |  |  |  | 16.15 | 15.47 | [6 empty] | 7.55 | 13.82 | 6.58
2009-05-17 | 6.8 | 6.545 |  |  |  |  | 7.29 | 1.725 |  |  |  |  | 59 |  |  |  | 0 | 0.301 |  |  | 0.1385 | 0.125 | [5 empty] | 21.45 |  |  |  |  | 42.9 |  | 20.45 |  | 10 | 0.089 |  | 9.5 | 94.85 | 1.015 |  |  |  |  | 16.842 | 15.73 | [6 empty] | 7.55 | 13.82 | 6.58
2009-05-18 | 6.95 | 6.52 |  |  |  |  | 7.16 | 1.68 |  |  |  |  | 73 |  |  |  | 0 | 0.301 |  |  | 0.141 | 0.123 | [5 empty] | 20.6 |  |  |  |  | 41.2 |  | 19.2 |  | 10 | 0.087 |  | 10.1 | 100.24 | 1.17 |  |  |  |  | 17.534 | 15.99 | [6 empty] | 7.55 | 13.82 | 6.58
2009-05-19 | 7.03 | 6.27 |  |  |  |  | 7.47 | 1.57 |  |  |  |  | 65 |  |  |  | 0 | 0.481 |  |  | 0.086 | 0.132 | [5 empty] | 21.2 |  |  |  |  | 42.4 |  | 18.4 |  | 10 | 0.084 |  | 11 | 103.64 | 1.39 |  |  |  |  | 16.542 | 15.896 | [6 empty] | 8.34 | 13.82 | 6.58
2009-05-20 | 6.7525 | 6.7875 |  |  |  |  | 6.9375 | 1.5525 |  |  |  |  | 60.5 |  |  |  | 0 | 0.30275 |  |  | 0.12875 | 0.22025 | [5 empty] | 22.175 |  |  |  |  | 44.375 |  | 19.625 |  | 10 | 0.10425 |  | 8.475 | 77.3825 | 0.855 |  |  |  |  | 15.302 | 14.5995 | [6 empty] | 10.515 | 13.82 | 6.79
2009-05-21 | 6.715 | 6.865 |  |  |  |  | 6.805 | 1.555 |  |  |  |  | 60 |  |  |  | 0 | 0.3015 |  |  | 0.1185 | 0.1745 | [5 empty] | 22.25 |  |  |  |  | 44.55 |  | 20.15 |  | 10 | 0.1075 |  | 9.35 | 79.945 | 0.95 |  |  |  |  | 15.198 | 14.493 | [6 empty] | 11.11 | 13.82 | 6.79
2009-05-22 | 6.79 | 6.71 |  |  |  |  | 7.07 | 1.55 |  |  |  |  | 61 |  |  |  | 0 | 0.304 |  |  | 0.139 | 0.266 | [5 empty] | 22.1 |  |  |  |  | 44.2 |  | 19.1 |  | 10 | 0.101 |  | 7.6 | 74.82 | 0.76 |  |  |  |  | 15.406 | 14.706 | [6 empty] | 9.92 | 13.82 | 6.79
2009-05-23 | 6.64 | 7.02 |  |  |  |  | 6.54 | 1.56 |  |  |  |  | 59 |  |  |  | 0 | 0.299 |  |  | 0.098 | 0.083 | [5 empty] | 22.4 |  |  |  |  | 44.9 |  | 21.2 |  | 10 | 0.114 |  | 11.1 | 85.07 | 1.14 |  |  |  |  | 14.99 | 14.28 | [6 empty] | 12.3 | 13.82 | 6.79
2009-05-24 | 6.885 | 6.93 |  |  |  |  | 7.265 | 1.46 |  |  |  |  | 45 |  |  |  | 0 | 0.271 |  |  | 0.1905 | 0.3345 | [5 empty] | 22.9 |  |  |  |  | 45.85 |  | 21.65 |  | 10 | 0.1175 |  | 11 | 92.645 | 1.335 |  |  |  |  | 16.2925 | 15.007 | [6 empty] | 9.765 | 13.02 | 6.16
2009-05-25 | 7.13 | 6.84 |  |  |  |  | 7.99 | 1.36 |  |  |  |  | 31 |  |  |  | 0 | 0.243 |  |  | 0.283 | 0.586 | [5 empty] | 23.4 |  |  |  |  | 46.8 |  | 22.1 |  | 10 | 0.121 |  | 10.9 | 100.22 | 1.53 |  |  |  |  | 17.595 | 15.734 | [6 empty] | 7.23 | 12.22 | 5.53
2009-05-26 | 7.13 | 7.01 |  |  |  |  | 7.45 | 1.34 |  |  |  |  | 22 |  |  |  | 0 | 0.262 |  |  | 0.214 | 0.214 | [5 empty] | 20.7 |  |  |  |  | 41.4 |  | 23.2 |  | 10 | 0.044 |  | 10.9 | 85.51 | 1.38 |  |  |  |  | 15.118 | 14.253 | [6 empty] | 6.78 | 12.25 | 5.49
2009-05-27 | 7.45 | 6.93 |  |  |  |  | 7.03 | 1.48 |  |  |  |  | 27 |  |  |  | 0 | 0.26 |  |  | 0.098 | 0.162 | [5 empty] | 20.7 |  |  |  |  | 41.5 |  | 22.2 |  | 10 | 0.069 |  | 10.4 | 94.33 | 1.44 |  |  |  |  | 15.396 | 14.673 | [6 empty] | 6.78 | 12.23 | 5.49
2009-05-28 | 6.93 | 6.94 |  |  |  |  | 7.48 | 1.43 |  |  |  |  | 11 |  |  |  | 0 | 0.209 |  |  | 0.233 | 0.162 | [5 empty] | 21 |  |  |  |  | 42 |  | 22.7 |  | 10 | 0.119 |  | 10.1 | 90.43 | 1.43 |  |  |  |  | 15.175 | 14.381 | [6 empty] | 6.44 | 12.23 | 5.49
2009-05-29 | 6.87 | 6.64 |  |  |  |  | 7.41 | 1.45 |  |  |  |  | 16 |  |  |  | 0 | 0.328 |  |  | 0.184 | 0.156 | [5 empty] | 20.9 |  |  |  |  | 41.8 |  | 21.4 |  | 10 | 0.107 |  | 11.1 | 94.83 | 1.42 |  |  |  |  | 15.713 | 14.986 | [6 empty] | 6.44 | 12.23 | 5.49
2009-05-30 | 6.82 | 6.63 |  |  |  |  | 7.3 | 1.69 |  |  |  |  | 27 |  |  |  | 0 | 0.342 |  |  | 0.124 | 0.158 | [5 empty] | 21.2 |  |  |  |  | 42.4 |  | 19 |  | 10 | 0.093 |  | 11.4 | 85.09 | 1.39 |  |  |  |  | 14.68 | 13.91 | [6 empty] | 6.44 | 12.23 | 5.49
2009-05-31 | 6.76 | 6.675 |  |  |  |  | 7.29 | 1.485 |  |  |  |  | 34.5 |  |  |  | 0 | 0.277 |  |  | 0.217 | 0.294 | [5 empty] | 21.2 |  |  |  |  | 42.45 |  | 19.6 |  | 10 | 0.0775 |  | 11.6 | 87.615 | 1.395 |  |  |  |  | 15.35 | 14.6005 | [6 empty] | 6.44 | 12.23 | 5.49
2009-06-01 | 6.7 | 6.72 |  |  |  |  | 7.28 | 1.28 |  |  |  |  | 42 |  |  |  | 0 | 0.212 |  |  | 0.31 | 0.43 | [5 empty] | 21.2 |  |  |  |  | 42.5 |  | 20.2 |  | 10 | 0.062 |  | 11.8 | 90.14 | 1.4 |  |  |  |  | 16.02 | 15.291 | [6 empty] | 6.44 | 12.23 | 5.49
2009-06-02 | 6.98 | 6.58 |  |  |  |  | 7.32 | 1.4 |  |  |  |  | 25 |  |  |  | 0 | 0.208 |  |  | 0.321 | 0.234 | [5 empty] | 18.4 |  |  |  |  | 36.9 |  | 21.2 |  | 10 | 0.077 |  | 12.7 | 90.45 | 1.57 |  |  |  |  | 14.594 | 13.822 | [6 empty] | 6.44 | 12.23 | 5.49
2009-06-03 | 7.05 | 6.85 |  |  |  |  | 7.45 | 1.62 |  |  |  |  | 56 |  |  |  | 0 | 0.253 |  |  | 0.363 | 0.246 | [5 empty] | 21.2 |  |  |  |  | 42.5 |  | 18.6 |  | 10 | 0.234 |  | 12.3 | 105.18 | 1.56 |  |  |  |  | 15.761 | 15.017 | [6 empty] | 6.44 | 12.23 | 5.49
2009-06-04 | 6.99 | 6.98 |  |  |  |  | 7.59 | 1.65 |  |  |  |  | 34 |  |  |  | 0 | 0.236 |  |  | 0.331 | 0.27 | [5 empty] | 23.7 |  |  |  |  | 47.3 |  | 19.3 |  | 10 | 0.226 |  | 12.1 | 105.2 | 1.51 |  |  |  |  | 15.869 | 15.118 | [6 empty] | 6.44 | 12.23 | 5.49
2009-06-05 | 6.98 | 6.87 |  |  |  |  | 7.31 | 1.69 |  |  |  |  | 21 |  |  |  | 0 | 0.266 |  |  | 0.375 | 0.322 | [5 empty] | 22.2 |  |  |  |  | 44.5 |  | 20.3 |  | 10 | 0.246 |  | 12.6 | 104.63 | 1.57 |  |  |  |  | 15.39 | 14.56 | [6 empty] | 6.44 | 12.23 | 5.49
2009-06-06 | 6.7125 | 7.1412 |  |  |  |  | 7.0388 | 1.5525 |  |  |  |  | 18.75 |  |  |  | 0 | 0.36813 |  |  | 0.45212 | 0.36675 | [5 empty] | 20.5625 |  |  |  |  | 41.2125 |  | 20.275 |  | 10 | 0.17338 |  | 12.9375 | 122.9281 | 1.7731 |  |  |  |  | 15.08 | 14.2553 | [6 empty] | 6.6869 | 11.16 | 5.49
2009-06-07 | 6.705 | 7.1525 |  |  |  |  | 7.0675 | 1.605 |  |  |  |  | 23.5 |  |  |  | 0 | 0.40325 |  |  | 0.43525 | 0.3615 | [5 empty] | 20.725 |  |  |  |  | 41.525 |  | 20.35 |  | 10 | 0.17375 |  | 12.775 | 122.7938 | 1.7638 |  |  |  |  | 15.178 | 14.3605 | [6 empty] | 6.7363 | 11.16 | 5.49
2009-06-08 | 6.72 | 7.13 |  |  |  |  | 7.01 | 1.5 |  |  |  |  | 14 |  |  |  | 0 | 0.333 |  |  | 0.469 | 0.372 | [5 empty] | 20.4 |  |  |  |  | 40.9 |  | 20.2 |  | 10 | 0.173 |  | 13.1 | 123.0625 | 1.7825 |  |  |  |  | 14.982 | 14.15 | [6 empty] | 6.6375 | 11.16 | 5.49
2009-06-09 | 6.69 | 7.175 |  |  |  |  | 7.125 | 1.71 |  |  |  |  | 33 |  |  |  | 0 | 0.4735 |  |  | 0.4015 | 0.351 | [5 empty] | 21.05 |  |  |  |  | 42.15 |  | 20.5 |  | 10 | 0.1745 |  | 12.45 | 122.525 | 1.745 |  |  |  |  | 15.374 | 14.571 | [6 empty] | 6.835 | 11.16 | 5.49
2009-06-10 | 6.66 | 7.22 |  |  |  |  | 7.24 | 1.92 |  |  |  |  | 52 |  |  |  | 0 | 0.614 |  |  | 0.334 | 0.33 | [5 empty] | 21.7 |  |  |  |  | 43.4 |  | 20.8 |  | 10 | 0.176 |  | 11.8 | 123.6 | 1.82 |  |  |  |  | 15.766 | 14.992 | [6 empty] | 6.44 | 11.16 | 5.49
2009-06-11 | 6.63 | 6.65 |  |  |  |  | 7.19 | 2.02 |  |  |  |  | 5 |  |  |  | 0 | 0.456 |  |  | 0.269 | 0.281 | [5 empty] | 21.7 |  |  |  |  | 43.4 |  | 19.2 |  | 10 | 0.188 |  | 11.5 | 121.45 | 1.67 |  |  |  |  | 15.668 | 14.917 | [6 empty] | 7.23 | 11.16 | 5.49
2009-06-12 | 6.935 | 6.62 |  |  |  |  | 7.05 | 1.875 |  |  |  |  | 34.5 |  |  |  | 0 | 0.3505 |  |  | 0.189 | 0.2385 | [5 empty] | 20.25 |  |  |  |  | 40.5 |  | 20.1 |  | 10 | 0.1165 |  | 11.35 | 90.67 | 1.67 |  |  |  |  | 15.174 | 14.4135 | [6 empty] | 9.92 | 13.29 | 5.49
2009-06-13 | 7.24 | 6.59 |  |  |  |  | 6.91 | 1.73 |  |  |  |  | 64 |  |  |  | 0 | 0.245 |  |  | 0.109 | 0.196 | [5 empty] | 18.8 |  |  |  |  | 37.6 |  | 21 |  | 10 | 0.045 |  | 11.2 | 99.84 | 1.53 |  |  |  |  | 14.68 | 13.91 | [6 empty] | 6.44 | 11.16 | 5.49
2009-06-14 | 7.135 | 6.255 |  |  |  |  | 6.725 | 1.685 |  |  |  |  | 35 |  |  |  | 0 | 0.222 |  |  | 0.1755 | 0.278 | [5 empty] | 19.5 |  |  |  |  | 39.05 |  | 19.25 |  | 10 | 0.1475 |  | 11.7 | 102.485 | 1.67 |  |  |  |  | 15.2715 | 13.853 | [6 empty] | 10.955 | 12.225 | 5.49
2009-06-15 | 7.03 | 5.92 |  |  |  |  | 6.54 | 1.64 |  |  |  |  | 6 |  |  |  | 0 | 0.199 |  |  | 0.242 | 0.36 | [5 empty] | 20.2 |  |  |  |  | 40.5 |  | 17.5 |  | 10 | 0.25 |  | 12.2 | 105.13 | 1.81 |  |  |  |  | 15.863 | 13.796 | [6 empty] | 15.47 | 13.29 | 5.49
2009-06-16 | 6.85 | 6.4 |  |  |  |  | 6.96 | 1.82 |  |  |  |  | 50 |  |  |  | 0 | 0.192 |  |  | 1.04 | 0.504 | [5 empty] | 24 |  |  |  |  | 48 |  | 18.4 |  | 10 | 0.097 |  | 12.6 | 105.71 | 1.6 |  |  |  |  | 16.603 | 14.027 | [6 empty] | 12.3 | 13.29 | 6.37
2009-06-17 | 7.02 | 6.72 |  |  |  |  | 7.2 | 2 |  |  |  |  | 31 |  |  |  | 0 | 0.197 |  |  | 0.109 | 0.204 | [5 empty] | 21.7 |  |  |  |  | 43.4 |  | 10.5 |  | 10 | 0.01 |  | 13.5 | 141.12 | 1.78 |  |  |  |  | 17.622 | 16.97 | [6 empty] | 7.55 | 12.22 | 5.49
2009-06-18 | 7.4 | 6.83 |  |  |  |  | 7.67 | 1.8 |  |  |  |  | 40 |  |  |  | 0 | 0.197 |  |  | 0.095 | 0.131 | [5 empty] | 21.3 |  |  |  |  | 42.7 |  | 15.8 |  | 10 | 0.21 |  | 14.4 | 125.18 | 1.68 |  |  |  |  | 17.017 | 16.318 | [6 empty] | 6.91 | 12.22 | 5.49
2009-06-19 | 7.28 | 7 |  |  |  |  | 7.34 | 1.47 |  |  |  |  | 33 |  |  |  | 0 | 0.281 |  |  | 0.096 | 0.148 | [5 empty] | 20.9 |  |  |  |  | 41.8 |  | 11.9 |  | 10 | 0.031 |  | 15.1 | 110.49 | 1.54 |  |  |  |  | 17.365 | 16.68 | [6 empty] | 6.91 | 12.22 | 5.49
2009-06-20 | 7.2 | 6.88 |  |  |  |  | 7.4 | 1.29 |  |  |  |  | 43 |  |  |  | 0 | 0.286 |  |  | 0.112 | 0.184 | [5 empty] | 20.7 |  |  |  |  | 41.4 |  | 13.9 |  | 10 | 0.073 |  | 15.7 | 99.75 | 1.55 |  |  |  |  | 16.67 | 15.97 | [6 empty] | 6.91 | 12.22 | 5.49
2009-06-21 | 7.25 | 6.96 |  |  |  |  | 7.54 | 1.41 |  |  |  |  | 50.5 |  |  |  | 0 | 0.233 |  |  | 0.107 | 0.189 | [5 empty] | 21.3 |  |  |  |  | 42.65 |  | 14.35 |  | 10 | 0.0835 |  | 16.15 | 95.34 | 1.19 |  |  |  |  | 17.417 | 16.2665 | [6 empty] | 6.91 | 12.22 | 5.49
2009-06-22 | 7.3 | 7.04 |  |  |  |  | 7.68 | 1.53 |  |  |  |  | 58 |  |  |  | 0 | 0.18 |  |  | 0.102 | 0.194 | [5 empty] | 21.9 |  |  |  |  | 43.9 |  | 14.8 |  | 10 | 0.094 |  | 16.6 | 120.28 | 1.77 |  |  |  |  | 18.164 | 16.563 | [6 empty] | 6.91 | 12.22 | 5.49
2009-06-23 | 7.19 | 7.04 |  |  |  |  | 7.19 | 1.63 |  |  |  |  | 11 |  |  |  | 0 | 0.181 |  |  | 0.118 | 0.141 | [5 empty] | 20.7 |  |  |  |  | 41.3 |  | 14.8 |  | 10 | 0.035 |  | 17 | 99.7 | 1.39 |  |  |  |  | 15.765 | 14.97 | [6 empty] | 6.91 | 12.22 | 5.49
2009-06-24 | 7.16 | 6.99 |  |  |  |  | 6.97 | 1.64 |  |  |  |  | 28 |  |  |  | 0 | 0.251 |  |  | 0.107 | 0.109 | [5 empty] | 18.2 |  |  |  |  | 36.4 |  | 15.6 |  | 10 | 0.047 |  | 16.9 | 100.24 | 1.53 |  |  |  |  | 15.11 | 14.337 | [6 empty] | 6.91 | 12.22 | 5.49
2009-06-25 | 7.22 | 6.93 |  |  |  |  | 7.21 | 1.79 |  |  |  |  | 17 |  |  |  | 0 | 0.284 |  |  | 0.038 | 0.065 | [5 empty] | 18.8 |  |  |  |  | 37.6 |  | 17.2 |  | 10 | 0.028 |  | 16.6 | 100.24 | 1.26 |  |  |  |  | 15.698 | 14.918 | [6 empty] | 6.91 | 12.22 | 5.49
2009-06-26 | 7.18 | 6.44 |  |  |  |  | 7.1 | 1.85 |  |  |  |  | 18 |  |  |  | 0 | 0.174 |  |  | 0.059 | 0.059 | [5 empty] | 19.2 |  |  |  |  | 38.4 |  | 19 |  | 10 | 0.044 |  | 16.8 | 96.65 | 1.14 |  |  |  |  | 15.406 | 14.677 | [6 empty] | 6.91 | 7.97 | 5.49
2009-06-27 | 6.98 | 6.81 |  |  |  |  | 7.02 | 1.81 |  |  |  |  | 21 |  |  |  | 0 | 0.187 |  |  | 0.037 | 0.056 | [5 empty] | 19.2 |  |  |  |  | 38.4 |  | 18.6 |  | 10 | 0.044 |  | 17.6 | 100.77 | 1.43 |  |  |  |  | 14.9 | 14.1 | [6 empty] | 6.91 | 7.97 | 5.49
2009-06-28 | 7.075 | 6.8 |  |  |  |  | 7.225 | 1.8 |  |  |  |  | 25.5 |  |  |  | 0 | 0.2035 |  |  | 0.0565 | 0.0805 | [5 empty] | 18.45 |  |  |  |  | 36.9 |  | 18.7 |  | 10 | 0.046 |  | 17.05 | 89.94 | 0.9 |  |  |  |  | 16.3735 | 15.165 | [6 empty] | 6.91 | 7.97 | 5.49
2009-06-29 | 7.17 | 6.79 |  |  |  |  | 7.43 | 1.79 |  |  |  |  | 30 |  |  |  | 0 | 0.22 |  |  | 0.076 | 0.105 | [5 empty] | 17.7 |  |  |  |  | 35.4 |  | 18.8 |  | 10 | 0.048 |  | 16.5 | 124.65 | 1.7 |  |  |  |  | 17.847 | 16.23 | [6 empty] | 6.91 | 7.97 | 5.49
2009-06-30 | 7.16 | 6.7 |  |  |  |  | 7.36 | 1.77 |  |  |  |  | 43 |  |  |  | 0 | 0.194 |  |  | 0.049 | 0.067 | [5 empty] | 19.5 |  |  |  |  | 39 |  | 0.58 |  | 10 | 0.042 |  | 17.9 | 119.38 | 1.42 |  |  |  |  | 17.772 | 17.013 | [6 empty] | 6.91 | 7.97 | 5.49
2009-07-01 | 7.22 | 6.82 |  |  |  |  | 7.29 | 1.5 |  |  |  |  | 42 |  |  |  | 0 | 0.192 |  |  | 0.056 | 0.062 | [5 empty] | 17.6 |  |  |  |  | 35.2 |  | 14.2 |  | 10 | 0.046 |  | 17.9 | 100.6 | 1.26 |  |  |  |  | 17.968 | 17.216 | [6 empty] | 6.91 | 7.97 | 5.49
2009-07-02 | 7.115 | 6.81 |  |  |  |  | 7.4 | 1.415 |  |  |  |  | 46.5 |  |  |  | 0 | 0.1965 |  |  | 0.0615 | 0.078 | [5 empty] | 18.85 |  |  |  |  | 37.65 |  | 15.05 |  | 10 | 0.0525 |  | 18.4 | 100.04 | 1.27 |  |  |  |  | 17.3955 | 16.6165 | [6 empty] | 6.91 | 7.97 | 5.49
2009-07-03 | 7.01 | 6.8 |  |  |  |  | 7.51 | 1.33 |  |  |  |  | 51 |  |  |  | 0 | 0.201 |  |  | 0.067 | 0.094 | [5 empty] | 20.1 |  |  |  |  | 40.1 |  | 15.9 |  | 10 | 0.059 |  | 18.9 | 93.93 | 1.33 |  |  |  |  | 16.823 | 16.017 | [6 empty] | 6.91 | 7.97 | 5.49
2009-07-04 | 7.09 | 6.35 |  |  |  |  | 7.4 | 1.38 |  |  |  |  | 30 |  |  |  | 0 | 0.192 |  |  | 0.059 | 0.063 | [5 empty] | 19 |  |  |  |  | 37.9 |  | 14.5 |  | 10 | 0.074 |  | 19.3 | 92.24 | 1.3 |  |  |  |  | 16.37 | 15.6 | [6 empty] | 6.91 | 7.97 | 5.49
2009-07-05 | 6.89 | 6.28 |  |  |  |  | 7.285 | 1.31 |  |  |  |  | 52 |  |  |  | 0 | 0.206 |  |  | 0.0855 | 0.1175 | [5 empty] | 18.65 |  |  |  |  | 37.2 |  | 15.35 |  | 10 | 0.084 |  | 18.6 | 75.3 | 1.06 |  |  |  |  | 16.276 | 15.041 | [6 empty] | 6.91 | 7.97 | 5.49
2009-07-06 | 6.69 | 6.21 |  |  |  |  | 7.17 | 1.24 |  |  |  |  | 74 |  |  |  | 0 | 0.22 |  |  | 0.112 | 0.172 | [5 empty] | 18.3 |  |  |  |  | 36.5 |  | 16.2 |  | 10 | 0.094 |  | 17.9 | 94.93 | 1.74 |  |  |  |  | 16.182 | 14.482 | [6 empty] | 6.91 | 7.97 | 5.49
2009-07-07 | 6.935 | 6.65 |  |  |  |  | 7.01 | 1.515 |  |  |  |  | 72 |  |  |  | 0 | 0.21 |  |  | 0.0795 | 0.121 | [5 empty] | 17.85 |  |  |  |  | 35.65 |  | 17.55 |  | 10 | 0.0865 |  | 17.05 | 100.04 | 1.44 |  |  |  |  | 16.395 | 15.142 | [6 empty] | 6.91 | 7.97 | 5.49
2009-07-08 | 7.18 | 7.09 |  |  |  |  | 6.85 | 1.79 |  |  |  |  | 70 |  |  |  | 0 | 0.2 |  |  | 0.047 | 0.07 | [5 empty] | 17.4 |  |  |  |  | 34.8 |  | 18.9 |  | 10 | 0.079 |  | 16.2 | 120.55 | 1.67 |  |  |  |  | 16.608 | 15.802 | [6 empty] | 6.91 | 7.97 | 5.49
2009-07-09 | 6.51 | 7 |  |  |  |  | 6.88 | 1.97 |  |  |  |  | 30 |  |  |  | 0 | 0.198 |  |  | 0.086 | 0.127 | [5 empty] | 22 |  |  |  |  | 44 |  | 18.1 |  | 10 | 0.137 |  | 16.6 | 125.14 | 1.49 |  |  |  |  | 17.19 | 16.4 | [6 empty] | 9.92 | 7.97 | 5.49
2009-07-10 | 6.71 | 6.845 |  |  |  |  | 7.165 | 1.8 |  |  |  |  | 31 |  |  |  | 0 | 0.246 |  |  | 0.092 | 0.1305 | [5 empty] | 20.45 |  |  |  |  | 40.9 |  | 18.7 |  | 10 | 0.112 |  | 17 | 120.285 | 1.473 |  |  |  |  | 16.75 | 16.86 | [6 empty] | 6.75 | 7.97 | 5.49
2009-07-11 | 6.91 | 6.69 |  |  |  |  | 7.45 | 1.6 |  |  |  |  | 32 |  |  |  | 0 | 0.294 |  |  | 0.098 | 0.134 | [5 empty] | 18.9 |  |  |  |  | 37.8 |  | 19.3 |  | 10 | 0.087 |  | 17.4 | 115.43 | 1.456 |  |  |  |  | 17.4 | 16.6 | [6 empty] | 6.75 | 7.97 | 5.49
2009-07-12 | 7.02 | 6.51 |  |  |  |  | 7.455 | 1.27 |  |  |  |  | 39 |  |  |  | 0 | 0.237 |  |  | 0.088 | 0.144 | [5 empty] | 20.15 |  |  |  |  | 40.35 |  | 16.45 |  | 10 | 0.0835 |  | 17.7 | 115.83 | 1.73 |  |  |  |  | 17.42 | 17.56 | [6 empty] | 6.75 | 7.97 | 5.49
2009-07-13 | 7.13 | 6.33 |  |  |  |  | 7.46 | 1.37 |  |  |  |  | 46 |  |  |  | 0 | 0.18 |  |  | 0.078 | 0.154 | [5 empty] | 21.4 |  |  |  |  | 42.9 |  | 13.6 |  | 10 | 0.08 |  | 18 | 110.54 | 1.94 |  |  |  |  | 16.91 | 15.141 | [6 empty] | 6.75 | 7.97 | 5.49
2009-07-14 | 7.28 | 6.48 |  |  |  |  | 7.42 | 1.54 |  |  |  |  | 19 |  |  |  | 0 | 0.245 |  |  | 0.091 | 0.109 | [5 empty] | 21.3 |  |  |  |  | 42.7 |  | 19.5 |  | 10 | 0.056 |  | 17.9 | 110.23 | 1.3 |  |  |  |  | 16.844 | 16.016 | [6 empty] | 6.75 | 7.97 | 5.49
2009-07-15 | 7.31 | 6.49 |  |  |  |  | 7.4 | 1.64 |  |  |  |  | 56 |  |  |  | 0 | 0.173 |  |  | 0.09 | 0.143 | [5 empty] | 22 |  |  |  |  | 44 |  | 19 |  | 10 | 0.077 |  | 18 | 114.9 | 1.64 |  |  |  |  | 16.699 | 15.884 | [6 empty] | 6.75 | 7.97 | 5.49
2009-07-16 | 7.28 | 6.94 |  |  |  |  | 7.17 | 1.63 |  |  |  |  | 44 |  |  |  | 0 | 0.168 |  |  | 0.135 | 0.138 | [5 empty] | 20.6 |  |  |  |  | 41.2 |  | 20.7 |  | 10 | 0.064 |  | 18.1 | 100.28 | 1.3 |  |  |  |  | 16.386 | 15.539 | [6 empty] | 6.75 | 7.97 | 5.49
2009-07-17 | 7.24 | 6.85 |  |  |  |  | 7.01 | 1.79 |  |  |  |  | 71 |  |  |  | 0 | 0.18 |  |  | 0.179 | 0.123 | [5 empty] | 21.5 |  |  |  |  | 43 |  | 19.6 |  | 10 | 0.071 |  | 18.1 | 121.09 | 1.81 |  |  |  |  | 16.117 | 15.28 | [6 empty] | 7.55 | 7.97 | 5.49
2009-07-18 | 7.24 | 6.77 |  |  |  |  | 7.02 | 1.75 |  |  |  |  | 48 |  |  |  | 0 | 0.169 |  |  | 0.297 | 0.192 | [5 empty] | 22 |  |  |  |  | 44.1 |  | 19.9 |  | 10 | 0.068 |  | 17.8 | 100.72 | 1.37 |  |  |  |  | 15.48 | 14.65 | [6 empty] | 7.55 | 9.57 | 5.49
2009-07-19 | 7.245 | 6.65 |  |  |  |  | 7.18 | 1.775 |  |  |  |  | 47.5 |  |  |  | 0 | 0.1665 |  |  | 0.292 | 0.2045 | [5 empty] | 21.8 |  |  |  |  | 43.65 |  | 17.7 |  | 10 | 0.1035 |  | 17.4 | 94.42 | 1.23 |  |  |  |  | 14.72 | 14.69 | [6 empty] | 7.55 | 9.57 | 5.49
2009-07-20 | 7.25 | 6.53 |  |  |  |  | 7.34 | 1.8 |  |  |  |  | 47 |  |  |  | 0 | 0.164 |  |  | 0.287 | 0.217 | [5 empty] | 21.6 |  |  |  |  | 43.2 |  | 15.5 |  | 10 | 0.139 |  | 17 | 125.24 | 1.81 |  |  |  |  | 17.331 | 15.768 | [6 empty] | 7.55 | 7.97 | 5.49
2009-07-21 | 6.71 | 7.03 |  |  |  |  | 7.56 | 1.84 |  |  |  |  | 48 |  |  |  | 0 | 0.176 |  |  | 0.118 | 0.174 | [5 empty] | 21.2 |  |  |  |  | 42.4 |  | 16.3 |  | 10 | 0.087 |  | 18.1 | 119.78 | 1.32 |  |  |  |  | 17.975 | 17.191 | [6 empty] | 7.55 | 7.97 | 5.49
2009-07-22 | 6.73 | 6.51 |  |  |  |  | 7.22 | 1.53 |  |  |  |  | 74 |  |  |  | 0 | 0.15 |  |  | 0.172 | 0.133 | [5 empty] | 25.9 |  |  |  |  | 51.8 |  | 16.8 |  | 10 | 0.06 |  | 19 | 110.58 | 1.55 |  |  |  |  | 17.048 | 16.283 | [6 empty] | 11.99 | 14.88 | 5.49
2009-07-23 | 6.7 | 6.4 |  |  |  |  | 7.22 | 1.5 |  |  |  |  | 31 |  |  |  | 0 | 0.154 |  |  | 0.296 | 0.245 | [5 empty] | 24.8 |  |  |  |  | 49.7 |  | 19.1 |  | 10 | 0.059 |  | 18 | 94.79 | 1.49 |  |  |  |  | 15.267 | 14.411 | [6 empty] | 11.99 | 13.29 | 5.49
2009-07-24 | 6.7 | 5.95 |  |  |  |  | 7.32 | 1.51 |  |  |  |  | 30 |  |  |  | 0 | 0.151 |  |  | 0.258 | 0.227 | [5 empty] | 25 |  |  |  |  | 50 |  | 18.6 |  | 10 | 0.074 |  | 17.5 | 105.86 | 1.53 |  |  |  |  | 16.54 | 15.808 | [6 empty] | 9.92 | 13.29 | 5.49
2009-07-25 | 6.67 | 6.63 |  |  |  |  | 7.14 | 1.54 |  |  |  |  | 28 |  |  |  | 0 | 0.162 |  |  | 0.101 | 0.23 | [5 empty] | 24.1 |  |  |  |  | 48.3 |  | 16.7 |  | 10 | 0.079 |  | 17.8 | 124.05 | 2.33 |  |  |  |  | 15.87 | 14.56 | [6 empty] | 10.72 | 10.63 | 5.49
2009-07-26 | 6.63 | 6.65 |  |  |  |  | 7.18 | 1.35 |  |  |  |  | 24.5 |  |  |  | 0 | 0.1555 |  |  | 0.1935 | 0.225 | [5 empty] | 24.05 |  |  |  |  | 48.15 |  | 18.35 |  | 10 | 0.0755 |  | 17.65 | 107.25 | 1.9 |  |  |  |  | 14.91 | 14.55 | [6 empty] | 10.72 | 10.63 | 5.49
2009-07-27 | 6.59 | 6.67 |  |  |  |  | 7.22 | 1.35 |  |  |  |  | 21 |  |  |  | 0 | 0.149 |  |  | 0.286 | 0.22 | [5 empty] | 24 |  |  |  |  | 48 |  | 20 |  | 10 | 0.072 |  | 17.5 | 90.45 | 1.47 |  |  |  |  | 16.268 | 14.546 | [6 empty] | 8.34 | 9.57 | 5.49
2009-07-28 | 6.69 | 6.545 |  |  |  |  | 3.61 | 1.28 |  |  |  |  | 35.5 |  |  |  | 0 | 0.148 |  |  | 0.23975 | 0.2245 | [5 empty] | 24.3 |  |  |  |  | 48.6 |  | 20.25 |  | 10 | 0.0825 |  | 17.85 | 86.1125 | 1.0175 |  |  |  |  | 15.706 | 15.639 | [6 empty] | 8.34 | 9.57 | 5.49
2009-07-29 | 6.79 | 6.42 | [5 empty] | 1.35 |  |  |  |  | 50 |  |  |  | 0 | 0.147 |  |  | 0.26287 | 0.229 | [5 empty] | 24.6 |  |  |  |  | 49.2 |  | 20.5 |  | 10 | 0.093 |  | 18.2 | 92.445 | 1.295 |  |  |  |  | 15.487 | 14.262 | [6 empty] | 5.08 | 9.57 | 6.37
2009-07-30 | 7.3 | 6.37 |  |  |  |  | 7.59 | 1.58 |  |  |  |  | 28 |  |  |  | 0 | 0.207 |  |  | 0.25131 | 0.156 | [5 empty] | 24.3 |  |  |  |  | 48.6 |  | 20.1 |  | 10 | 0.087 |  | 18.3 | 79.78 | 0.74 |  |  |  |  | 16.812 | 15.611 | [6 empty] | 5.08 | 9.57 | 6.37
2009-07-31 | 6.77 | 6.17 |  |  |  |  | 7.67 | 1.26 |  |  |  |  | 101 |  |  |  | 0 | 0.185 |  |  | 0.25709 | 0.178 | [5 empty] | 24.4 |  |  |  |  | 44.8 |  | 20.8 |  | 10 | 0.176 |  | 18.6 | 105.11 | 1.85 |  |  |  |  | 16.135 | 15.33 | [6 empty] | 5.08 | 9.57 | 6.37
2009-08-01 | 6.76 | 6.68 |  |  |  |  | 7.7 | 1.11 |  |  |  |  | 63 |  |  |  | 0 | 0.174 |  |  | 0.2542 | 0.153 | [5 empty] | 24.8 |  |  |  |  | 49.6 |  | 21.1 |  | 10 | 0.073 |  | 19.3 | 105.3 | 2.525 |  |  |  |  | 15.02 | 14.15 | [6 empty] | 5.08 | 9.57 | 6.37
2009-08-02 | 6.78 | 6.695 |  |  |  |  | 7.37 | 1.17 |  |  |  |  | 60 |  |  |  | 0 | 0.179 |  |  | 0.25565 | 0.2265 | [5 empty] | 24.95 |  |  |  |  | 49.9 |  | 20.6 |  | 10 | 0.098 |  | 19.25 | 105.6 | 2.58 |  |  |  |  | 14.609 | 14.652 | [6 empty] | 5.08 | 9.57 | 6.37
2009-08-03 | 6.8 | 6.71 |  |  |  |  | 7.04 | 1.05 |  |  |  |  | 57 |  |  |  | 0 | 0.184 |  |  | 0.25493 | 0.3 | [5 empty] | 25.1 |  |  |  |  | 50.2 |  | 20.1 |  | 10 | 0.123 |  | 19.2 | 113.98 | 2.47 |  |  |  |  | 16.408 | 14.68 | [6 empty] | 5.08 | 9.57 | 6.37
2009-08-04 | 6.52 | 6.7 |  |  |  |  | 7.01 | 1.29 |  |  |  |  | 70 |  |  |  | 0 | 0.185 |  |  | 0.25529 | 0.283 | [5 empty] | 24.8 |  |  |  |  | 49.6 |  | 18.8 |  | 10 | 0.146 |  | 19 | 135.43 | 2.69 |  |  |  |  | 16.274 | 15.449 | [6 empty] | 5.08 | 9.57 | 6.37
2009-08-05 | 7.21 | 6.42 |  |  |  |  | 7.25 | 1.5129 |  |  |  |  | 71 |  |  |  | 0 | 0.253 |  |  | 0.25511 | 0.274 | [5 empty] | 26.7 |  |  |  |  | 53.4 |  | 20.3 |  | 10 | 0.963 |  | 19.7 | 129.61 | 2.58 |  |  |  |  | 17.338 | 14.479 | [6 empty] | 5.08 | 9.57 | 7.08
2009-08-06 | 6.71 | 6.49 |  |  |  |  | 6.85 | 1.5142 |  |  |  |  | 33 |  |  |  | 0 | 0.178 |  |  | 0.2552 | 0.241 | [5 empty] | 25.2 |  |  |  |  | 50.4 |  | 21.5 |  | 10 | 0.083 |  | 20.1 | 129.63 | 2.635 |  |  |  |  | 16.866 | 10.71 | [6 empty] | 8.34 | 9.57 | 7.78
2009-08-07 | 6.48 | 6.51 |  |  |  |  | 6.86 | 1.5116 |  |  |  |  | 41 |  |  |  | 0 | 0.178 |  |  | 0.25515 | 0.274 | [5 empty] | 24.7 |  |  |  |  | 49.4 |  | 19.9 |  | 10 | 0.102 |  | 20 | 154.99 | 2.6075 |  |  |  |  | 17.325 | 11.507 | [6 empty] | 8.34 | 9.57 | 7.78
2009-08-08 | 6.67 | 6.49 |  |  |  |  | 6.91 | 1.5169 |  |  |  |  | 40 |  |  |  | 0 | 0.197 |  |  | 0.25517 | 0.335 | [5 empty] | 25 |  |  |  |  | 50.1 |  | 18.6 |  | 10 | 0.11 |  | 20.2 | 160.85 | 2.6212 |  |  |  |  | 15.54 | 15.994 | [6 empty] | 8.34 | 9.57 | 8.49
2009-08-09 | 6.47 | 6.545 |  |  |  |  | 6.39 | 1.5062 |  |  |  |  | 50.5 |  |  |  | 0 | 0.242 |  |  | 0.25516 | 0.2435 | [5 empty] | 25.3 |  |  |  |  | 50.65 |  | 18.25 |  | 10 | 0.132 |  | 19.9 | 185.31 | 2.6144 |  |  |  |  | 14.206 | 15.994 | [6 empty] | 8.34 | 9.57 | 8.49
2009-08-10 | 6.27 | 6.6 |  |  |  |  | 5.87 | 1.5275 |  |  |  |  | 61 |  |  |  | 0 | 0.287 |  |  | 0.25517 | 0.152 | [5 empty] | 25.6 |  |  |  |  | 51.2 |  | 17.9 |  | 10 | 0.154 |  | 19.6 | 190.67 | 2.6178 |  |  |  |  | 18.832 | 12.484 | [6 empty] | 8.34 | 9.57 | 8.34
2009-08-11 | 6.97 | 7.39 |  |  |  |  | 7.73 | 1.485 |  |  |  |  | 73 |  |  |  | 0 | 0.257 |  |  | 0.25517 | 0.463 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 23.6 |  | 10 | 0.098 |  | 19.3 | 145.22 | 2.6161 |  |  |  |  | 18.503 | 12.36 | [6 empty] | 8.34 | 9.52 | 8.31
2009-08-12 | 6.83 | 6.67 |  |  |  |  | 6.96 | 1.57 |  |  |  |  | 71 |  |  |  | 0 | 0.258 |  |  | 0.25517 | 0.234 | [5 empty] | 23.8 |  |  |  |  | 47.6 |  | 21.5 |  | 10 | 0.083 |  | 19 | 125.22 | 3.95 |  |  |  |  | 16.052 | 15.994 | [6 empty] | 8.34 | 9.57 | 8.31
2009-08-13 | 6.825 | 6.765 |  |  |  |  | 7.095 | 1.4 |  |  |  |  | 78.5 |  |  |  | 0 | 0.217 |  |  | 0.25517 | 0.268 | [5 empty] | 24.55 |  |  |  |  | 49.1 |  | 20.35 |  | 10 | 0.069 |  | 19.15 | 109.92 | 3.74 |  |  |  |  | 15.26 | 15.994 | [6 empty] | 8.34 | 9.57 | 8.31
2009-08-14 | 6.82 | 6.86 |  |  |  |  | 7.23 | 1.59 |  |  |  |  | 86 |  |  |  | 0 | 0.176 |  |  | 0.25517 | 0.302 | [5 empty] | 25.3 |  |  |  |  | 50.6 |  | 19.2 |  | 10 | 0.055 |  | 19.3 | 107.16 | 2.38 |  |  |  |  | 17.483 | 11.373 | [6 empty] | 8.34 | 9.57 | 8.31
2009-08-15 | 6.67 | 6.67 |  |  |  |  | 7.03 | 1.82 |  |  |  |  | 76 |  |  |  | 0 | 0.175 |  |  | 0.28667 | 0.293 | [5 empty] | 24.2 |  |  |  |  | 48.5 |  | 21.6 |  | 10 | 0.064 |  | 19.6 | 159.97 | 5.14 |  |  |  |  | 16.86 | 15.994 | [6 empty] | 8.34 | 9.57 | 8.31
2009-08-16 | 6.33 | 6.41 |  |  |  |  | 6.95 | 1.73 |  |  |  |  | 52.5 |  |  |  | 0 | 0.177 |  |  | 0.28667 | 0.303 | [5 empty] | 23.05 |  |  |  |  | 46.2 |  | 20.8 |  | 10 | 0.157 |  | 19.65 | 140.68 | 4.36 |  |  |  |  | 15.51 | 15.994 | [6 empty] | 8.34 | 9.57 | 8.31
2009-08-17 | 5.99 | 6.15 |  |  |  |  | 6.87 | 1.7 |  |  |  |  | 29 |  |  |  | 0 | 0.179 |  |  | 0.28667 | 0.313 | [5 empty] | 21.9 |  |  |  |  | 43.9 |  | 20 |  | 10 | 0.25 |  | 19.7 | 150.71 | 5.05 |  |  |  |  | 16.1 | 15.994 | [6 empty] | 8.34 | 9.57 | 8.31
2009-08-18 | 6.44 | 5.74 |  |  |  |  | 6.2 | 2.01 |  |  |  |  | 38 |  |  |  | 0 | 0.175 |  |  | 0.28667 | 0.274 | [5 empty] | 21.6 |  |  |  |  | 42.6 |  | 20.6 |  | 10 | 0.23 |  | 19.6 | 175.58 | 5.18 |  |  |  |  | 15.083 | 11.094 | [6 empty] | 8.34 | 9.57 | 9.02
2009-08-19 | 8.06 | 6.45 |  |  |  |  | 8.11 | 2.85 |  |  |  |  | 22 |  |  |  | 0 | 0.655 |  |  | 0.28667 | 0.274 | [5 empty] | 26.1 |  |  |  |  | 52.1 |  | 21.5 |  | 10 | 0.152 |  | 18.8 | 190.18 | 3.13 |  |  |  |  | 15.421 | 14.428 | [6 empty] | 8.34 | 9.57 | 6.37
2009-08-20 | 8.44 | 7.1 |  |  |  |  | 8.28 | 2.67 |  |  |  |  | 30 |  |  |  | 0 | 0.619 |  |  | 0.28667 | 0.732 | [5 empty] | 24 |  |  |  |  | 48 |  | 22 |  | 10 | 0.143 |  | 18.3 | 199.2 | 3.38 |  |  |  |  | 15.963 | 14.949 | [6 empty] | 6.28 | 7.97 | 6.37
2009-08-21 | 8.28 | 7.18 |  |  |  |  | 7.88 | 2.14 |  |  |  |  | 47 |  |  |  | 0 | 0.611 |  |  | 0.28667 | 0.948 | [5 empty] | 21.4 |  |  |  |  | 42.8 |  | 20.7 |  | 10 | 0.168 |  | 18.9 | 165.37 | 2.89 |  |  |  |  | 15.79 | 14.92 | [6 empty] | 5.96 | 7.97 | 5.49
2009-08-22 | 6.55 | 7.42 |  |  |  |  | 7.27 | 1.71 |  |  |  |  | 61 |  |  |  | 0 | 0.626 |  |  | 0.28667 | 0.447 | [5 empty] | 19.1 |  |  |  |  | 38.2 |  | 21.4 |  | 10 | 0.223 |  | 19.3 | 125.84 | 2.31 |  |  |  |  | 15.23 | 14.2 | [6 empty] | 5.33 | 5.31 | 3.73
2009-08-23 | 6.535 | 6.945 |  |  |  |  | 7.255 | 1.58 |  |  |  |  | 60 |  |  |  | 0 | 0.79133 |  |  | 0.28667 | 0.5145 | [5 empty] | 18.05 |  |  |  |  | 36.1 |  | 20.2 |  | 10 | 0.176 |  | 19 | 115.32 | 2 |  |  |  |  | 14.667 | 14.623 | [6 empty] | 5.33 | 6.91 | 3.38
2009-08-24 | 6.52 | 6.47 |  |  |  |  | 7.24 | 1.72 |  |  |  |  | 59 |  |  |  | 0 | 0.79133 |  |  | 0.28667 | 0.582 | [5 empty] | 17 |  |  |  |  | 34 |  | 19 |  | 10 | 0.129 |  | 18.7 | 155.47 | 2.82 |  |  |  |  | 17.485 | 15.557 | [6 empty] | 5.33 | 6.91 | 3.38
2009-08-25 | 6.74 | 6.52 |  |  |  |  | 7.18 | 1.78 |  |  |  |  | 75 |  |  |  | 0 | 0.79134 |  |  | 0.28667 | 0.396 | [5 empty] | 17 |  |  |  |  | 34 |  | 19.2 |  | 10 | 0.139 |  | 18.8 | 154.4 | 2.93 |  |  |  |  | 15.805 | 14.868 | [6 empty] | 5.33 | 6.91 | 3.38
2009-08-26 | 5.84 | 6.55 |  |  |  |  | 7.41 | 1.72 |  |  |  |  | 74 |  |  |  | 0 | 0.79132 |  |  | 0.28667 | 0.638 | [5 empty] | 18 |  |  |  |  | 36 |  | 20.5 |  | 10 | 0.112 |  | 18.5 | 155.67 | 3.22 |  |  |  |  | 15.355 | 14.322 | [6 empty] | 5.33 | 6.91 | 3.38
2009-08-27 | 6.09 | 6.58 |  |  |  |  | 6.97 | 1.98 |  |  |  |  | 43 |  |  |  | 0 | 0.79135 |  |  | 0.28666 | 0.467 | [5 empty] | 18 |  |  |  |  | 36 |  | 8.9 |  | 10 | 0.25 |  | 17.7 | 164.76 | 3.09 |  |  |  |  | 15.674 | 14.761 | [6 empty] | 5.33 | 6.91 | 3.38
2009-08-28 | 6.59 | 6.29 |  |  |  |  | 7.385 | 2.17 |  |  |  |  | 34 |  |  |  | 0 | 0.79129 |  |  | 0.28668 | 1.13 | [5 empty] | 17.1 |  |  |  |  | 34.3 |  | 14 |  | 10 | 0.204 |  | 17 | 168.18 | 3.08 |  |  |  |  | 15.538 | 14.541 | [6 empty] | 5.33 | 13.29 | 3.38
2009-08-29 | 6.38 | 6.38 |  |  |  |  | 7.8 | 2.36 |  |  |  |  | 31 |  |  |  | 0 | 0.79141 |  |  | 0.28664 | 1.907 | [5 empty] | 21.2 |  |  |  |  | 42.4 |  | 20.9 |  | 10 | 0.248 |  | 15.9 | 164.4 | 2.91 |  |  |  |  | 15.1 | 14.15 | [6 empty] | 5.33 | 15.94 | 3.38
2009-08-30 | 6.675 | 6.355 |  |  |  |  | 7.38 | 2.29 |  |  |  |  | 31 |  |  |  | 0 | 0.79118 |  |  | 0.28672 | 2.2635 | [5 empty] | 22.7 |  |  |  |  | 45.4 |  | 21.3 |  | 10 | 0.22 |  | 15.55 | 167.6 | 3.61 |  |  |  |  | 13.913 | 12.893 | [6 empty] | 5.33 | 17.54 | 5.49
2009-08-31 | 6.97 | 6.33 |  |  |  |  | 6.96 | 2.45 |  |  |  |  | 31 |  |  |  | 0 | 0.79164 |  |  | 0.28656 | 2.62 | [5 empty] | 24.2 |  |  |  |  | 48.4 |  | 21.7 |  | 10 | 0.192 |  | 15.2 | 200.22 | 3.58 |  |  |  |  | 17.004 | 15.088 | [6 empty] | 5.33 | 17.54 | 5.49
2009-09-01 | 7.08 | 6.35 |  |  |  |  | 7.04 | 2.15 |  |  |  |  | 27 |  |  |  | 0 | 0.79072 |  |  | 0.28687 | 2.7055 | [5 empty] | 26.7 |  |  |  |  | 53.4 |  | 23.2 |  | 10 | 0.249 |  | 15.2 | 180.61 | 3.76 |  |  |  |  | 15.636 | 13.881 | [6 empty] | 5.33 | 19.66 | 6.37
2009-09-02 | 7.28 | 7.05 |  |  |  |  | 6.93 | 2.34 |  |  |  |  | 32 |  |  |  | 0 | 0.79256 |  |  | 0.28625 | 2.791 | [5 empty] | 26.1 |  |  |  |  | 51.8 |  | 23.4 |  | 9.547 | 0.173 |  | 15.1 | 199.94 | 4.01 |  |  |  |  | 16.32 | 14.301 | [6 empty] | 5.48 | 18.07 | 6.9
2009-09-03 | 6.5975 | 7.12 |  |  |  |  | 5.71 | 2.64 |  |  |  |  | 37 |  |  |  | 0 | 0.78887 |  |  | 0.2875 | 1.52 | [5 empty] | 20.4 |  |  |  |  | 40.9 |  | 18.9 |  | 9.094 | 0.25 |  | 15.5 | 210.67 | 3.58 |  |  |  |  | 17.218 | 15.385 | [6 empty] | 6.75 | 18.07 | 4.61
2009-09-04 | 6.595 | 6.31 |  |  |  |  | 6.71 | 2.7 |  |  |  |  | 60 |  |  |  | 0 | 0.79625 |  |  | 0.285 | 0.287 | [5 empty] | 24.7 |  |  |  |  | 49.5 |  | 21.4 |  | 10 | 0.06 |  | 16 | 175.32 | 2.66 |  |  |  |  | 15.737 | 14.844 | [6 empty] | 9.61 | 21.26 | 4.61
2009-09-05 | 6.6 | 6.52 |  |  |  |  | 6.72 | 2.42 |  |  |  |  | 47 |  |  |  | 0 | 0.7815 |  |  | 0.29 | 0.172 | [5 empty] | 23.9 |  |  |  |  | 47.8 |  | 19.5 |  | 8.1879 | 0.029 |  | 16.2 | 152.03 | 2.43 |  |  |  |  | 15.24 | 14.23 | [6 empty] | 9.61 | 21.26 | 6.37
2009-09-06 | 6.59 | 6.35 |  |  |  |  | 6.775 | 2.39 |  |  |  |  | 48 |  |  |  | 0 | 0.811 |  |  | 0.28 | 0.1705 | [5 empty] | 25.4 |  |  |  |  | 50.8 |  | 21 |  | 8.1898 | 0.017 |  | 15.85 | 125.69 | 1.94 |  |  |  |  | 13.22 | 13.18 | [6 empty] | 9.61 | 21.26 | 6.37
2009-09-07 | 6.58 | 6.18 |  |  |  |  | 6.83 | 2.45 |  |  |  |  | 49 |  |  |  | 0 | 0.752 |  |  | 0.3 | 0.169 | [5 empty] | 26.9 |  |  |  |  | 53.8 |  | 22.5 |  | 8.1861 | 0.005 |  | 15.5 | 145.715 | 2.395 |  |  |  |  | 16.565 | 14.66 | [6 empty] | 9.13 | 21.26 | 6.37
2009-09-08 | 6.67 | 6.32 |  |  |  |  | 7.1 | 2.19 |  |  |  |  | 35 |  |  |  | 0 | 0.87 |  |  | 0.26 | 0.132 | [5 empty] | 22.8 |  |  |  |  | 45.6 |  | 20.7 |  | 8.1934 | 0.18 |  | 15.3 | 165.74 | 2.85 |  |  |  |  | 15.787 | 14.933 | [6 empty] | 9.13 | 21.26 | 6.37
2009-09-09 | 6.52 | 6.05 |  |  |  |  | 7.11 | 2.5 |  |  |  |  | 67 |  |  |  | 0 | 0.777 |  |  | 0.34 | 0.209 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 16.9 |  | 8.1788 | 0.109 |  | 15.4 | 157.68 | 2.28 |  |  |  |  | 16.344 | 14.965 | [6 empty] | 9.13 | 21.26 | 6.37
2009-09-10 | 6.67 | 6.47 |  |  |  |  | 4.63 | 2.87 |  |  |  |  | 38 |  |  |  | 0 | 0.79153 |  |  | 0.18 | 0.213 | [5 empty] | 17.8 |  |  |  |  | 35.6 |  | 19.7 |  | 8.208 | 0.138 |  | 14.9 | 145.09 | 1.08 |  |  |  |  | 15.146 | 14.109 | [6 empty] | 9.13 | 21.26 | 4.61
2009-09-11 | 6.64 | 6.57 |  |  |  |  | 7.47 | 2.43 |  |  |  |  | 27 |  |  |  | 0 | 0.78994 |  |  | 0.5 | 0.517 | [5 empty] | 26.5 |  |  |  |  | 53 |  | 19.1 |  | 8.1496 | 0.089 |  | 14.6 | 158.94 | 2.32 |  |  |  |  | 16.17 | 15.201 | [6 empty] | 9.61 | 23.92 | 6.37
2009-09-12 | 7 | 6.61 |  |  |  |  | 6.96 | 2.32 |  |  |  |  | 28 |  |  |  | 0 | 0.79313 |  |  | 0.1 | 0.278 | [5 empty] | 22.2 |  |  |  |  | 44.4 |  | 21.4 |  | 8.2664 | 0.175 |  | 14.9 | 125.18 | 1.74 |  |  |  |  | 14.88 | 14 | [6 empty] | 9.13 | 21.26 | 6.37
2009-09-13 | 6.92 | 6.605 |  |  |  |  | 6.995 | 2.3 |  |  |  |  | 29 |  |  |  | 0 | 0.78675 |  |  | 0.107 | 0.2425 | [5 empty] | 21.85 |  |  |  |  | 43.65 |  | 20.95 |  | 8.0328 | 0.1105 |  | 14.9 | 115.39 | 1.65 |  |  |  |  | 14.241 | 13.266 | [6 empty] | 9.13 | 21.26 | 6.37
2009-09-14 | 6.84 | 6.6 |  |  |  |  | 7.03 | 2.3 |  |  |  |  | 30 |  |  |  | 0 | 0.7995 |  |  | 0.114 | 0.207 | [5 empty] | 21.5 |  |  |  |  | 42.9 |  | 20.5 |  | 8.5 | 0.046 |  | 14.9 | 115.39 | 1.16 |  |  |  |  | 16.54 | 15.148 | [6 empty] | 9.61 | 23.92 | 6.37
2009-09-15 | 6.9 | 6.73 |  |  |  |  | 7.3 | 1.92 |  |  |  |  | 35 |  |  |  | 0 | 0.774 |  |  | 0.442 | 0.453 | [5 empty] | 27 |  |  |  |  | 54 |  | 29.1 |  | 7.5656 | 0.081 |  | 15 | 150.18 | 2.78 |  |  |  |  | 14.988 | 14.514 | [6 empty] | 9.61 | 23.92 | 6.37
2009-09-16 | 7.32 | 6.8087 |  |  |  |  | 6.96 | 2.09 |  |  |  |  | 30 |  |  |  | 0 | 0.825 |  |  | 0.535 | 0.45 | [5 empty] | 27.7 |  |  |  |  | 55.4 |  | 23.4 |  | 7.6438 | 0.052 |  | 14.8 | 145.02 | 2.49 |  |  |  |  | 15.269 | 14.36 | [6 empty] | 9.61 | 21.26 | 6.37
2009-09-17 | 7.135 | 6.8375 |  |  |  |  | 7.02 | 2.065 |  |  |  |  | 30.5 |  |  |  | 0 | 0.723 |  |  | 0.4315 | 0.412 | [5 empty] | 26.85 |  |  |  |  | 53.7 |  | 24.15 |  | 7.4875 | 0.04 |  | 14.45 | 140.3 | 2.44 |  |  |  |  | 15.3095 | 14.135 | [6 empty] | 9.61 | 21.26 | 6.37
2009-09-18 | 6.95 | 6.78 |  |  |  |  | 7.08 | 2.04 |  |  |  |  | 31 |  |  |  | 0 | 0.621 |  |  | 0.328 | 0.374 | [5 empty] | 26 |  |  |  |  | 52 |  | 24.9 |  | 7.8 | 0.028 |  | 14.1 | 135.58 | 2.39 |  |  |  |  | 15.35 | 13.91 | [6 empty] | 9.61 | 21.26 | 6.37
2009-09-19 | 6.815 | 6.895 |  |  |  |  | 7.285 | 2.015 |  |  |  |  | 35.25 |  |  |  | 0 | 0.5805 |  |  | 0.3965 | 0.40375 | [5 empty] | 26.75 |  |  |  |  | 53.5 |  | 20.8 |  | 7.175 | 0.076 |  | 13.15 | 105.13 | 1.54 |  |  |  |  | 13.98 | 13.08 | [6 empty] | 9.61 | 21.26 | 6.37
2009-09-20 | 6.84 | 6.9 |  |  |  |  | 7.35 | 1.99 |  |  |  |  | 36.5 |  |  |  | 0 | 0.578 |  |  | 0.403 | 0.4145 | [5 empty] | 26.7 |  |  |  |  | 53.4 |  | 23.2 |  | 7.15 | 0.082 |  | 13.2 | 136.55 | 2.59 |  |  |  |  | 14.045 | 13.138 | [6 empty] | 9.61 | 21.26 | 6.37
2009-09-21 | 6.79 | 6.89 |  |  |  |  | 7.22 | 2.04 |  |  |  |  | 34 |  |  |  | 0 | 0.583 |  |  | 0.39 | 0.393 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 18.4 |  | 7.2 | 0.07 |  | 13.1 | 138.84 | 2.15 |  |  |  |  | 16.908 | 15.018 | [6 empty] | 9.61 | 21.26 | 6.32
2009-09-22 | 6.89 | 6.91 |  |  |  |  | 7.48 | 1.94 |  |  |  |  | 39 |  |  |  | 0 | 0.573 |  |  | 0.416 | 0.436 | [5 empty] | 26.6 |  |  |  |  | 53.2 |  | 28 |  | 7.1 | 0.094 |  | 13.3 | 129.63 | 2.19 |  |  |  |  | 15.272 | 14.249 | [6 empty] | 9.61 | 21.26 | 6.37
2009-09-23 | 6.87 | 6.81 |  |  |  |  | 7.1 | 1.79 |  |  |  |  | 45 |  |  |  | 0 | 0.594 |  |  | 0.438 | 0.449 | [5 empty] | 21.9 |  |  |  |  | 43.8 |  | 19.2 |  | 7.2 | 0.031 |  | 13.7 | 116.14 | 1.95 |  |  |  |  | 15.032 | 14.115 | [6 empty] | 9.61 | 21.26 | 6.37
2009-09-24 | 6.69 | 5.92 |  |  |  |  | 5.32 | 1.8 |  |  |  |  | 39 |  |  |  | 0 | 0.766 |  |  | 0.444 | 0.323 | [5 empty] | 20 |  |  |  |  | 40 |  | 25.4 |  | 4.3 | 0.076 |  | 14.1 | 111.1 | 1.6 |  |  |  |  | 15.806 | 14.837 | [6 empty] | 9.61 | 21.26 | 6.37
2009-09-25 | 6.82 | 6 |  |  |  |  | 7.2 | 2.12 |  |  |  |  | 56 |  |  |  | 0 | 0.693 |  |  | 0.753 | 0.592 | [5 empty] | 26.5 |  |  |  |  | 51.2 |  | 23.8 |  | 6.7 | 0.098 |  | 13.9 | 135.01 | 2.16 |  |  |  |  | 15.279 | 14.335 | [6 empty] | 9.61 | 26.57 | 5.49
2009-09-26 | 6.8 | 6.81 |  |  |  |  | 7.01 | 2.19 |  |  |  |  | 42 |  |  |  | 0 | 0.679 |  |  | 0.346 | 0.402 | [5 empty] | 27.6 |  |  |  |  | 55.3 |  | 20 |  | 5.4 | 0.095 |  | 12.7 | 130.45 | 2.25 |  |  |  |  | 14.324 | 13.332 | [6 empty] | 10.72 | 31.89 | 5.49
2009-09-27 | 6.66 | 6.72 |  |  |  |  | 6.945 | 2.19 |  |  |  |  | 34 |  |  |  | 0 | 0.6185 |  |  | 0.4335 | 0.3735 | [5 empty] | 24.85 |  |  |  |  | 49.75 |  | 24.05 |  | 6 | 0.083 |  | 12.55 | 137.595 | 2.22 |  |  |  |  | 15.5915 | 14.159 | [6 empty] | 10.72 | 31.89 | 5.49
2009-09-28 | 6.52 | 6.63 |  |  |  |  | 6.88 | 2.19 |  |  |  |  | 26 |  |  |  | 0 | 0.558 |  |  | 0.521 | 0.345 | [5 empty] | 22.1 |  |  |  |  | 44.2 |  | 28.1 |  | 6.6 | 0.071 |  | 12.4 | 144.74 | 2.19 |  |  |  |  | 16.859 | 14.986 | [6 empty] | 10.72 | 31.89 | 5.49
2009-09-29 | 6.78 | 6.7 |  |  |  |  | 6.93 | 1.97 |  |  |  |  | 28 |  |  |  | 0 | 0.574 |  |  | 0.308 | 0.323 | [5 empty] | 27.4 |  |  |  |  | 54.9 |  | 26.2 |  | 7.4 | 0.068 |  | 12.6 | 120.92 | 1.72 |  |  |  |  | 15.786 | 14.843 | [6 empty] | 10.72 | 31.889 | 5.49
2009-09-30 | 6.72 | 6.74 |  |  |  |  | 7.03 | 1.94 |  |  |  |  | 51 |  |  |  | 0 | 0.564 |  |  | 0.622 | 0.319 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 27.7 |  | 8.3 | 0.036 |  | 12.8 | 124.49 | 1.89 |  |  |  |  | 15.783 | 14.751 | [6 empty] | 10.72 | 31.89 | 5.49
2009-10-01 | 6.7 | 6.6 |  |  |  |  | 7.2 | 1.97 |  |  |  |  | 62 |  |  |  | 0 | 0.56 |  |  | 0.314 | 0.294 | [5 empty] | 29.4 |  |  |  |  | 58.7 |  | 26.3 |  | 7.9 | 0.043 |  | 13.8 | 130.05 | 1.82 |  |  |  |  | 16.477 | 15.572 | [6 empty] | 10.72 | 31.89 | 5.49
2009-10-02 | 6.82 | 6.8 |  |  |  |  | 7.63 | 1.91 |  |  |  |  | 35 |  |  |  | 0 | 0.541 |  |  | 0.295 | 0.285 | [5 empty] | 27.9 |  |  |  |  | 55.8 |  | 26.9 |  | 7.8 | 0.087 |  | 13.8 | 130.24 | 1.77 |  |  |  |  | 16.579 | 15.558 | [6 empty] | 11.03 | 34.54 | 5.49
2009-10-03 | 6.7 | 6.94 |  |  |  |  | 6.97 | 2.23 |  |  |  |  | 36 |  |  |  | 0 | 0.553 |  |  | 0.11 | 0.2 | [5 empty] | 30.6 |  |  |  |  | 61.2 |  | 24.4 |  | 8.3 | 0.061 |  | 13.2 | 129.63 | 1.71 |  |  |  |  | 15.87 | 14.92 | [6 empty] | 11.03 | 34.54 | 5.49
2009-10-04 | 6.715 | 6.6 |  |  |  |  | 7.1 | 2.215 |  |  |  |  | 37.5 |  |  |  | 0 | 0.53 |  |  | 0.1485 | 0.1615 | [5 empty] | 30.7 |  |  |  |  | 61.4 |  | 23.55 |  | 7.85 | 0.0675 |  | 12.75 | 114.97 | 1.3 |  |  |  |  | 15.281 | 15.215 | [6 empty] | 11.03 | 34.54 | 5.49
2009-10-05 | 6.73 | 6.26 |  |  |  |  | 7.23 | 2.2 |  |  |  |  | 39 |  |  |  | 0 | 0.507 |  |  | 0.187 | 0.123 | [5 empty] | 30.8 |  |  |  |  | 61.6 |  | 22.7 |  | 7.4 | 0.074 |  | 12.3 | 150.09 | 2.15 |  |  |  |  | 17.618 | 15.676 | [6 empty] | 11.03 | 34.54 | 5.49
2009-10-06 | 6.73 | 6.13 |  |  |  |  | 7.13 | 1.87 |  |  |  |  | 44 |  |  |  | 0 | 0.504 |  |  | 0.169 | 0.118 | [5 empty] | 30.8 |  |  |  |  | 61.7 |  | 19.3 |  | 8.7 | 0.005 |  | 12.3 | 121.3 | 1.69 |  |  |  |  | 16.606 | 15.49 | [6 empty] | 11.03 | 34.54 | 5.49
2009-10-07 | 6.67 | 6.57 |  |  |  |  | 7.32 | 2.02 |  |  |  |  | 38 |  |  |  | 0 | 0.558 |  |  | 0.134 | 0.198 | [5 empty] | 30.7 |  |  |  |  | 61.5 |  | 20.1 |  | 10.6 | 0.045 |  | 11.9 | 134.95 | 1.9 |  |  |  |  | 16.593 | 15.622 | [6 empty] | 10.4 | 36.14 | 6.37
2009-10-08 | 6.67 | 6.21 |  |  |  |  | 7.26 | 1.99 |  |  |  |  | 37 |  |  |  | 0 | 0.509 |  |  | 0.159 | 0.2 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 19.3 |  | 8.9 | 0.038 |  | 12 | 135.92 | 1.86 |  |  |  |  | 17.114 | 16.035 | [6 empty] | 9.92 | 36.14 | 6.2
2009-10-09 | 6.67 | 6.39 |  |  |  |  | 7.29 | 2.06 |  |  |  |  | 37.5 |  |  |  | 0 | 0.5335 |  |  | 0.1465 | 0.199 | [5 empty] | 30.55 |  |  |  |  | 61.15 |  | 19.7 |  | 9.75 | 0.0415 |  | 11.95 | 125.82 | 1.71 |  |  |  |  | 16.8535 | 15.8285 | [6 empty] | 9.92 | 36.14 | 6.2
2009-10-10 | 6.86 | 6.61 |  |  |  |  | 5.45 | 1.85 |  |  |  |  | 52 |  |  |  | 0 | 0.671 |  |  | 0.239 | 0.136 | [5 empty] | 23.2 |  |  |  |  | 45.8 |  | 25.7 |  | 8.8 | 0.024 |  | 10.6 | 120.28 | 1.81 |  |  |  |  | 15.96 | 14.91 | [6 empty] | 9.92 | 36.14 | 6.2
2009-10-11 | 6.8 | 6.36 |  |  |  |  | 6.245 | 1.85 |  |  |  |  | 47 |  |  |  | 0 | 0.6695 |  |  | 0.2605 | 0.1735 | [5 empty] | 25.95 |  |  |  |  | 51.6 |  | 23.05 |  | 8.2 | 0.0145 |  | 10.3 | 110.49 | 1.75 |  |  |  |  | 16.933 | 15.4405 | [6 empty] | 9.92 | 36.14 | 6.2
2009-10-12 | 6.74 | 6.11 |  |  |  |  | 7.04 | 2.08 |  |  |  |  | 42 |  |  |  | 0 | 0.668 |  |  | 0.282 | 0.211 | [5 empty] | 28.7 |  |  |  |  | 57.4 |  | 20.4 |  | 7.6 | 0.005 |  | 10 | 150.09 | 2.19 |  |  |  |  | 17.906 | 15.971 | [6 empty] | 9.92 | 36.14 | 6.2
2009-10-13 | 6.85 | 6.19 |  |  |  |  | 6.89 | 2.08 |  |  |  |  | 41 |  |  |  | 0 | 0.65 |  |  | 0.209 | 0.23 | [5 empty] | 24.7 |  |  |  |  | 49.4 |  | 19.7 |  | 7.2 | 0.036 |  | 9.6 | 135.45 | 1.74 |  |  |  |  | 17.1 | 16.1 | [6 empty] | 10.72 | 36.14 | 6.2
2009-10-14 | 6.64 | 6.26 |  |  |  |  | 7.27 | 2.03 |  |  |  |  | 43 |  |  |  | 0 | 0.621 |  |  | 0.271 | 0.251 | [5 empty] | 29 |  |  |  |  | 58 |  | 21 |  | 7.3 | 0.021 |  | 9.3 | 130.05 | 1.09 |  |  |  |  | 16.958 | 15.876 | [6 empty] | 10.72 | 36.14 | 6.2
2009-10-15 | 6.745 | 6.225 |  |  |  |  | 7.08 | 2.055 |  |  |  |  | 42 |  |  |  | 0 | 0.6355 |  |  | 0.24 | 0.2405 | [5 empty] | 26.85 |  |  |  |  | 53.7 |  | 20.35 |  | 7.25 | 0.0285 |  | 9.45 | 132.75 | 1.415 |  |  |  |  | 17.029 | 15.988 | [6 empty] | 10.72 | 36.14 | 6.2
2009-10-16 | 6.86 | 6.28 |  |  |  |  | 7.15 | 1.77 |  |  |  |  | 51 |  |  |  | 0 | 0.663 |  |  | 0.874 | 0.624 | [5 empty] | 27.5 |  |  |  |  | 54.9 |  | 19.8 |  | 6.9 | 0.095 |  | 9.3 | 120.2 | 2.07 |  |  |  |  | 15.307 | 14.206 | [6 empty] | 12.3 | 36.14 | 6.2
2009-10-17 | 6.76 | 6.61 |  |  |  |  | 6.93 | 1.84 |  |  |  |  | 60 |  |  |  | 0 | 0.595 |  |  | 0.124 | 0.192 | [5 empty] | 25.3 |  |  |  |  | 50.6 |  | 17 |  | 8.4 | 0.025 |  | 8.8 | 115.34 | 1.71 |  |  |  |  | 15.76 | 14.76 | [6 empty] | 12.78 | 36.14 | 6.2
2009-10-18 | 6.83 | 6.74 |  |  |  |  | 7.03 | 1.75 |  |  |  |  | 47 |  |  |  | 0 | 0.622 |  |  | 0.2175 | 0.2595 | [5 empty] | 27.15 |  |  |  |  | 54.3 |  | 18.75 |  | 8.35 | 0.029 |  | 8.15 | 115.155 | 1.835 |  |  |  |  | 16.0595 | 14.5815 | [6 empty] | 12.78 | 36.14 | 6.2
2009-10-19 | 6.9 | 6.87 |  |  |  |  | 7.13 | 1.66 |  |  |  |  | 34 |  |  |  | 0 | 0.649 |  |  | 0.311 | 0.327 | [5 empty] | 29 |  |  |  |  | 58 |  | 20.5 |  | 8.3 | 0.033 |  | 7.5 | 114.97 | 1.96 |  |  |  |  | 16.359 | 14.403 | [6 empty] | 12.78 | 36.14 | 6.2
2009-10-20 | 6.63 | 6.81 |  |  |  |  | 6.98 | 1.32 |  |  |  |  | 41 |  |  |  | 0 | 0.637 |  |  | 0.207 | 0.339 | [5 empty] | 30.3 |  |  |  |  | 60.5 |  | 19.9 |  | 8.6 | 0.036 |  | 7.4 | 115.37 | 2.05 |  |  |  |  | 16.607 | 15.529 | [6 empty] | 12.78 | 36.14 | 6.2
2009-10-21 | 6.69 | 6.3 |  |  |  |  | 7.02 | 2.08 |  |  |  |  | 43 |  |  |  | 0 | 0.601 |  |  | 0.109 | 0.289 | [5 empty] | 28.3 |  |  |  |  | 56.7 |  | 19.3 |  | 7.4 | 0.029 |  | 7.6 | 110.01 | 1.26 |  |  |  |  | 15.927 | 14.97 | [6 empty] | 13.89 | 36.14 | 6.2
2009-10-22 | 6.73 | 6.35 |  |  |  |  | 7.09 | 1.86 |  |  |  |  | 32 |  |  |  | 0 | 0.646 |  |  | 0.28 | 0.36 | [5 empty] | 30.3 |  |  |  |  | 60.6 |  | 19.8 |  | 9.6 | 0.013 |  | 7.6 | 100.24 | 1.13 |  |  |  |  | 16.321 | 15.234 | [6 empty] | 13.16 | 36.14 | 6.2
2009-10-23 | 6.67 | 6.64 |  |  |  |  | 7.22 | 1.77 |  |  |  |  | 53 |  |  |  | 0 | 0.619 |  |  | 0.254 | 0.284 | [5 empty] | 29.8 |  |  |  |  | 59.6 |  | 18.4 |  | 8.9 | 0.056 |  | 7.3 | 105.18 | 1.33 |  |  |  |  | 16.381 | 15.39 | [6 empty] | 12.3 | 34.54 | 6.2
2009-10-24 | 6.6 | 5.06 |  |  |  |  | 7.23 | 2.1 |  |  |  |  | 52 |  |  |  | 0 | 0.546 |  |  | 0.219 | 0.258 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 19.2 |  | 7.9 | 0.061 |  | 7.9 | 104.69 | 1.16 |  |  |  |  | 15.56 | 14.57 | [6 empty] | 13.1 | 36.14 | 6.2
2009-10-25 | 6.85 | 5.845 |  |  |  |  | 7.27 | 1.86 |  |  |  |  | 47 |  |  |  | 0 | 0.6375 |  |  | 0.4415 | 0.5 | [5 empty] | 29.4 |  |  |  |  | 58.85 |  | 18.3 |  | 8.15 | 0.064 |  | 7.55 | 89.55 | 0.86 |  |  |  |  | 16.292 | 14.8375 | [6 empty] | 13.1 | 36.14 | 6.2
2009-10-26 | 7.1 | 6.63 |  |  |  |  | 7.31 | 1.75 |  |  |  |  | 42 |  |  |  | 0 | 0.729 |  |  | 0.664 | 0.742 | [5 empty] | 30.6 |  |  |  |  | 61.3 |  | 17.4 |  | 8.4 | 0.067 |  | 7.2 | 115.39 | 1.72 |  |  |  |  | 17.024 | 15.105 | [6 empty] | 13.1 | 36.14 | 6.2
2009-10-27 | 6.5 | 7.43 |  |  |  |  | 7.22 | 1.88 |  |  |  |  | 46 |  |  |  | 0 | 0.781 |  |  | 0.267 | 0.285 | [5 empty] | 28.8 |  |  |  |  | 57.5 |  | 19.9 |  | 7.7 | 0.094 |  | 6.7 | 105.53 | 1.3 |  |  |  |  | 16.07 | 15.075 | [6 empty] | 12.3 | 34.54 | 6.37
2009-10-28 | 6.89 | 6.72 |  |  |  |  | 6.94 | 1.66 |  |  |  |  | 41 |  |  |  | 0 | 0.75 |  |  | 0.634 | 0.365 | [5 empty] | 30 |  |  |  |  | 60.1 |  | 19.1 |  | 7.5 | 0.063 |  | 5.9 | 99.69 | 1.46 |  |  |  |  | 15.623 | 14.513 | [6 empty] | 12.3 | 34.54 | 6.37
2009-10-29 | 6.68 | 6.19 |  |  |  |  | 7.49 | 1.8 |  |  |  |  | 59 |  |  |  | 0 | 0.633 |  |  | 0.286 | 0.28 | [5 empty] | 27.9 |  |  |  |  | 55.8 |  | 19.2 |  | 8.4 | 0.078 |  | 5.9 | 105.11 | 1.49 |  |  |  |  | 15.53 | 14.5 | [6 empty] | 9.92 | 29.23 | 6.37
2009-10-30 | 6.11 | 5.95 |  |  |  |  | 7.15 | 1.76 |  |  |  |  | 36 |  |  |  | 0 | 0.577 |  |  | 0.388 | 0.281 | [5 empty] | 29.3 |  |  |  |  | 58.6 |  | 20.2 |  | 8.1 | 0.009 |  | 5.6 | 95.83 | 1.33 |  |  |  |  | 15.113 | 14.035 | [6 empty] | 11.51 | 29.23 | 6.77
2009-10-31 | 6.7 | 5.95 |  |  |  |  | 7.05 | 1.71 |  |  |  |  | 43 |  |  |  | 0 | 0.617 |  |  | 0.254 | 0.332 | [5 empty] | 24.8 |  |  |  |  | 49.7 |  | 21.3 |  | 7.2 | 0.031 |  | 5.4 | 84.58 | 1.1 |  |  |  |  | 14.7 | 13.65 | [6 empty] | 11.51 | 29.33 | 5.49
2009-11-01 | 6.66 | 6.005 |  |  |  |  | 6.895 | 1.78 |  |  |  |  | 42 |  |  |  | 0 | 1.262 |  |  | 0.401 | 0.389 | [5 empty] | 25.4 |  |  |  |  | 50.85 |  | 20.8 |  | 7.4 | 0.055 |  | 6.05 | 89.96 | 1.1 |  |  |  |  | 15.692 | 14.2205 | [6 empty] | 11.51 | 29.33 | 5.49
2009-11-02 | 6.62 | 6.06 |  |  |  |  | 6.74 | 1.82 |  |  |  |  | 41 |  |  |  | 0 | 1.907 |  |  | 0.548 | 0.446 | [5 empty] | 26 |  |  |  |  | 52 |  | 20.3 |  | 7.6 | 0.079 |  | 6.7 | 109.59 | 1.54 |  |  |  |  | 16.684 | 14.791 | [6 empty] | 11.51 | 29.33 | 5.49
2009-11-03 | 6.34 | 6 |  |  |  |  | 6.98 | 1.81 |  |  |  |  | 43 |  |  |  | 0 | 1.37 |  |  | 0.206 | 0.231 | [5 empty] | 25.9 |  |  |  |  | 51.8 |  | 20.4 |  | 7.7 | 0.063 |  | 6.4 | 100.7 | 1.61 |  |  |  |  | 14.451 | 13.381 | [6 empty] | 11.51 | 29.33 | 5.49
2009-11-04 | 6.65 | 5.99 |  |  |  |  | 7.23 | 1.71 |  |  |  |  | 31 |  |  |  | 0 | 1.214 |  |  | 0.306 | 0.269 | [5 empty] | 26 |  |  |  |  | 52 |  | 20.7 |  | 8.6 | 0.042 |  | 6.5 | 89.96 | 1.18 |  |  |  |  | 15.075 | 14.125 | [6 empty] | 11.51 | 29.33 | 5.49
2009-11-05 | 6.65 | 5.74 |  |  |  |  | 7.35 | 1.67 |  |  |  |  | 45 |  |  |  | 0 | 0.955 |  |  | 0.304 | 0.319 | [5 empty] | 27.2 |  |  |  |  | 54.2 |  | 20.6 |  | 8.4 | 0.006 |  | 6.5 | 85.79 | 1.27 |  |  |  |  | 13.828 | 13.231 | [6 empty] | 11.51 | 29.33 | 5.49
2009-11-06 | 6.72 | 6.455 |  |  |  |  | 7.53 | 1.75 |  |  |  |  | 56.5 |  |  |  | 0 | 1.209 |  |  | 0.423 | 0.3435 | [5 empty] | 26.15 |  |  |  |  | 52.1 |  | 21.65 |  | 9.35 | 0.042 |  | 6.2 | 89.96 | 1.45 |  |  |  |  | 14.174 | 13.3005 | [6 empty] | 3.58 | 29.33 | 6.37
2009-11-07 | 6.79 | 7.17 |  |  |  |  | 7.71 | 1.86 |  |  |  |  | 68 |  |  |  | 0 | 1.463 |  |  | 0.542 | 0.368 | [5 empty] | 25.1 |  |  |  |  | 50 |  | 22.7 |  | 10.3 | 0.078 |  | 5.9 | 100.24 | 1.54 |  |  |  |  | 14.52 | 13.37 | [6 empty] | 3.58 | 29.33 | 6.37
2009-11-08 | 6.77 | 7.05 |  |  |  |  | 7.485 | 1.785 |  |  |  |  | 49.5 |  |  |  | 0 | 1.348 |  |  | 0.663 | 0.4465 | [5 empty] | 26.9 |  |  |  |  | 53.7 |  | 25.5 |  | 11.9 | 0.141 |  | 5.6 | 95.42 | 1.505 |  |  |  |  | 14.6905 | 13.1475 | [6 empty] | 3.58 | 27.95 | 6.81
2009-11-09 | 6.75 | 6.93 |  |  |  |  | 7.26 | 1.71 |  |  |  |  | 31 |  |  |  | 0 | 1.233 |  |  | 0.784 | 0.525 | [5 empty] | 28.7 |  |  |  |  | 57.4 |  | 28.3 |  | 13.5 | 0.204 |  | 5.3 | 90.6 | 1.47 |  |  |  |  | 14.861 | 12.925 | [6 empty] | 3.58 | 26.57 | 7.25
2009-11-10 | 7.11 | 6.77 |  |  |  |  | 7.42 | 1.92 |  |  |  |  | 46 |  |  |  | 0 | 0.959 |  |  | 0.274 | 0.273 | [5 empty] | 25 |  |  |  |  | 50.1 |  | 24.3 |  | 9.9 | 0.061 |  | 5.1 | 105.79 | 1.31 |  |  |  |  | 15.836 | 14.893 | [6 empty] | 3.58 | 29.33 | 6.37
2009-11-11 | 6.9 | 6.89 |  |  |  |  | 6.95 | 1.82 |  |  |  |  | 51 |  |  |  | 0 | 0.865 |  |  | 0.21 | 0.467 | [5 empty] | 30.7 |  |  |  |  | 61.5 |  | 21.6 |  | 9.1 | 0.071 |  | 5.7 | 100.22 | 1.47 |  |  |  |  | 14.938 | 13.878 | [6 empty] | 2 | 29.23 | 6.37
2009-11-12 | 6.48 | 6.94 |  |  |  |  | 7.02 | 1.83 |  |  |  |  | 51 |  |  |  | 0 | 1.002 |  |  | 0.437 | 0.452 | [5 empty] | 25.5 |  |  |  |  | 51 |  | 22.4 |  | 8.9 | 0.049 |  | 4.9 | 87.19 | 1.22 |  |  |  |  | 14.105 | 12.986 | [6 empty] | 11.51 | 29.23 | 6.02
2009-11-13 | 6.72 | 6.59 |  |  |  |  | 6.71 | 1.75 |  |  |  |  | 49 |  |  |  | 0 | 0.83 |  |  | 0.258 | 0.274 | [5 empty] | 27.1 |  |  |  |  | 54.2 |  | 23.1 |  | 8.7 | 0.051 |  | 4.5 | 90.45 | 1.17 |  |  |  |  | 15.101 | 14.078 | [6 empty] | 12.3 | 29.23 | 6.37
2009-11-14 | 6.81 | 6.67 |  |  |  |  | 8.5 | 1.8 |  |  |  |  | 47 |  |  |  | 0 | 0.783 |  |  | 0.216 | 0.341 | [5 empty] | 29.9 |  |  |  |  | 59.8 |  | 22.2 |  | 8.2 | 0.061 |  | 4.7 | 94.86 | 1.5 |  |  |  |  | 14.28 | 13.04 | [6 empty] | 10.72 | 29.23 | 6.02
2009-11-15 | 6.795 | 6.685 |  |  |  |  | 7.565 | 1.64 |  |  |  |  | 44 |  |  |  | 0 | 0.8125 |  |  | 0.4715 | 0.7245 | [5 empty] | 29.55 |  |  |  |  | 59.05 |  | 21.9 |  | 8.9 | 0.0695 |  | 4.9 | 90.45 | 1.25 |  |  |  |  | 14.583 | 12.7605 | [6 empty] | 10.72 | 29.23 | 6.195
2009-11-16 | 6.78 | 6.7 |  |  |  |  | 6.63 | 1.75 |  |  |  |  | 41 |  |  |  | 0 | 0.842 |  |  | 0.727 | 1.108 | [5 empty] | 29.2 |  |  |  |  | 58.3 |  | 21.6 |  | 9.6 | 0.078 |  | 5.1 | 89.88 | 1.52 |  |  |  |  | 14.886 | 12.481 | [6 empty] | 10.72 | 29.23 | 6.37
2009-11-17 | 6.89 | 6.81 |  |  |  |  | 7.71 | 1.78 |  |  |  |  | 54 |  |  |  | 0 | 0.831 |  |  | 0.336 | 0.238 | [5 empty] | 32.5 |  |  |  |  | 65 |  | 19.1 |  | 8.6 | 0.06 |  |  | 100.72 | 1.58 |  |  |  |  | 15.315 | 13.621 | [6 empty] | 9.13 | 29.23 | 6.37
2009-11-18 | 6.87 | 5.91 |  |  |  |  | 7.04 | 1.91 |  |  |  |  | 47 |  |  |  | 0 | 0.64 |  |  | 0.387 | 0.302 | [5 empty] | 30.3 |  |  |  |  | 60.6 |  | 19.4 |  | 8.7 | 0.051 |  | 4.9 | 106.26 | 1.28 |  |  |  |  | 16.055 | 15.141 | [6 empty] | 9.92 | 29.23 | 6.37
2009-11-19 | 6.88 | 6.54 |  |  |  |  | 6.64 | 1.84 |  |  |  |  | 49 |  |  |  | 0 | 0.721 |  |  | 0.283 | 0.498 | [5 empty] | 29.8 |  |  |  |  | 59.6 |  | 20 |  | 7.7 | 0.073 |  | 4.5 | 95.16 | 1.21 |  |  |  |  | 15.173 | 14.15 | [6 empty] | 12.3 | 29.23 | 6.37
2009-11-20 | 6.81 | 7.24 |  |  |  |  | 7.25 | 1.69 |  |  |  |  | 42 |  |  |  | 0 | 0.708 |  |  | 0.527 | 0.581 | [5 empty] | 28.9 |  |  |  |  | 57.8 |  | 20.8 |  | 8.2 | 0.039 |  | 4.5 | 85.07 | 1.07 |  |  |  |  | 14.961 | 14.006 | [6 empty] | 9.13 | 26.57 | 6.37
2009-11-21 | 6.93 | 7.11 |  |  |  |  | 7.82 | 1.82 |  |  |  |  | 41 |  |  |  | 0 | 0.745 |  |  | 0.328 | 0.352 | [5 empty] | 28.7 |  |  |  |  | 57.5 |  | 19.9 |  | 8.3 | 0.022 |  | 4.5 | 90.14 | 1.16 |  |  |  |  | 14.72 | 13.73 | [6 empty] | 9.13 | 25.51 | 6.9
2009-11-22 | 6.875 | 6.82 |  |  |  |  | 7.445 | 1.78 |  |  |  |  | 42 |  |  |  | 0 | 0.715 |  |  | 0.5795 | 0.502 | [5 empty] | 28.4 |  |  |  |  | 56.85 |  | 20.5 |  | 8.2 | 0.0265 |  | 4.55 | 81.34 | 1.05 |  |  |  |  | 14.9245 | 13.4965 | [6 empty] | 9.13 | 25.51 | 6.9
2009-11-23 | 6.82 | 6.53 |  |  |  |  | 7.07 | 1.9 |  |  |  |  | 43 |  |  |  | 0 | 0.685 |  |  | 0.831 | 0.652 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 21.1 |  | 8.1 | 0.031 |  | 4.6 | 96.62 | 1.41 |  |  |  |  | 15.129 | 13.263 | [6 empty] | 9.61 | 26.57 | 6.37
2009-11-24 | 7.01 | 7.01 |  |  |  |  | 6.98 | 1.77 |  |  |  |  | 42 |  |  |  | 0 | 0.698 |  |  | 0.325 | 0.297 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 19.7 |  | 7.9 | 0.038 |  | 4.7 | 89.96 | 1.22 |  |  |  |  | 14.651 | 13.662 | [6 empty] | 9.61 | 26.57 | 6.37
2009-11-25 | 6.76 | 6.64 |  |  |  |  | 7.07 | 1.69 |  |  |  |  | 41 |  |  |  | 0 | 0.649 |  |  | 0.525 | 0.552 | [5 empty] | 26.5 |  |  |  |  | 53.1 |  | 20.5 |  | 8 | 0.091 |  | 4.3 | 95.34 | 1.34 |  |  |  |  | 16.414 | 14.278 | [6 empty] | 9.13 | 21.26 | 6.37
2009-11-26 | 7.04 | 6.58 |  |  |  |  | 6.92 | 1.87 |  |  |  |  | 40 |  |  |  | 0 | 0.683 |  |  | 0.321 | 0.442 | [5 empty] | 26.4 |  |  |  |  | 52.9 |  | 20.2 |  | 7.4 | 0.048 |  | 4.1 | 85.07 | 1.01 |  |  |  |  | 16.267 | 13.408 | [6 empty] | 9.13 | 21.26 | 6.37
2009-11-27 | 6.83 | 6.37 |  |  |  |  | 7.32 | 1.95 |  |  |  |  | 53 |  |  |  | 0 | 0.674 |  |  | 0.298 | 0.487 | [5 empty] | 24.7 |  |  |  |  | 49.2 |  | 19.3 |  | 8.6 | 0.054 |  | 5.2 | 105.13 | 1.18 |  |  |  |  | 18.256 | 15.242 | [6 empty] | 9.92 | 21.26 | 6.37
2009-11-28 | 6.7 | 6.6 |  |  |  |  | 5.14 | 1.86 |  |  |  |  | 57 |  |  |  | 0 | 0.726 |  |  | 0.114 | 0.143 | [5 empty] | 24.6 |  |  |  |  | 49.3 |  | 18.5 |  | 7.2 | 0.074 |  | 5.4 | 94.62 | 1.19 |  |  |  |  | 17.01 | 14.07 | [6 empty] | 9.92 | 21.26 | 6.37
2009-11-29 | 6.78 | 6.425 |  |  |  |  | 6.38 | 1.85 |  |  |  |  | 51 |  |  |  | 0 | 0.9465 |  |  | 0.2135 | 0.3445 | [5 empty] | 24.9 |  |  |  |  | 49.85 |  | 21.3 |  | 6.8 | 0.0975 |  | 5.25 | 97.42 | 1.35 |  |  |  |  | 17.2055 | 13.816 | [6 empty] | 10.16 | 21.26 | 6.37
2009-11-30 | 6.86 | 6.25 |  |  |  |  | 7.62 | 1.84 |  |  |  |  | 45 |  |  |  | 0 | 1.167 |  |  | 0.313 | 0.546 | [5 empty] | 25.2 |  |  |  |  | 50.4 |  | 24.1 |  | 6.4 | 0.121 |  | 5.1 | 100.22 | 1.51 |  |  |  |  | 17.401 | 13.562 | [6 empty] | 10.4 | 21.26 | 6.37
2009-12-01 | 6.77 | 7.23 |  |  |  |  | 7.24 | 1.69 |  |  |  |  | 42 |  |  |  | 0 | 0.843 |  |  | 0.145 | 0.449 | [5 empty] | 26.3 |  |  |  |  | 52.7 |  | 22.7 |  | 8.2 | 0.11 |  | 5 | 89.96 | 1.26 |  |  |  |  | 16.776 | 13.832 | [6 empty] | 10.4 | 21.26 | 7.25
2009-12-02 | 6.85 | 6.06 |  |  |  |  | 7.43 | 1.78 |  |  |  |  | 54 |  |  |  | 0 | 1.49 |  |  | 0.235 | 0.292 | [5 empty] | 27.8 |  |  |  |  | 55.6 |  | 23.5 |  | 11.7 | 0.054 |  | 5.2 | 106.66 | 1.62 |  |  |  |  | 17.165 | 14.259 | [6 empty] | 10.4 | 21.26 | 7.78
2009-12-03 | 6.78 | 7.12 |  |  |  |  | 7.22 | 1.76 |  |  |  |  | 72 |  |  |  | 0 | 3.612 |  |  | 0.194 | 0.272 | [5 empty] | 27.5 |  |  |  |  | 55.1 |  | 20 |  | 9.8 | 0.091 |  | 4.5 | 94.35 | 1.27 |  |  |  |  | 17.072 | 14.136 | [6 empty] | 10.4 | 21.26 | 8.13
2009-12-04 | 6.695 | 6.935 |  |  |  |  | 7.355 | 1.73 |  |  |  |  | 66 |  |  |  | 0 | 2.6415 |  |  | 0.1755 | 0.288 | [5 empty] | 27.85 |  |  |  |  | 55.75 |  | 21.65 |  | 9.35 | 0.0775 |  | 4.05 | 92.4 | 1.295 |  |  |  |  | 16.81 | 13.8695 | [6 empty] | 10.4 | 21.26 | 8.395
2009-12-05 | 6.61 | 6.75 |  |  |  |  | 7.49 | 1.7 |  |  |  |  | 60 |  |  |  | 0 | 1.671 |  |  | 0.157 | 0.304 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 23.3 |  | 8.9 | 0.064 |  | 3.6 | 90.45 | 1.32 |  |  |  |  | 16.548 | 13.603 | [6 empty] | 10.4 | 21.26 | 8.66
2009-12-06 | 6.73 | 6.79 |  |  |  |  | 7.575 | 1.71 |  |  |  |  | 61 |  |  |  | 0 | 1.625 |  |  | 0.179 | 0.3745 | [5 empty] | 28.5 |  |  |  |  | 57 |  | 20.65 |  | 9.25 | 0.069 |  | 4 | 100.64 | 1.77 |  |  |  |  | 17.3255 | 13.652 | [6 empty] | 10.4 | 21.26 | 8.66
2009-12-07 | 6.85 | 6.83 |  |  |  |  | 7.66 | 1.8 |  |  |  |  | 62 |  |  |  | 0 | 1.579 |  |  | 0.201 | 0.445 | [5 empty] | 28.8 |  |  |  |  | 57.6 |  | 18 |  | 9.6 | 0.074 |  | 4.4 | 105.13 | 1.67 |  |  |  |  | 18.103 | 13.701 | [6 empty] | 10.4 | 21.26 | 8.66
2009-12-08 | 6.835 | 6.695 |  |  |  |  | 7.36 | 1.75 |  |  |  |  | 57 |  |  |  | 0 | 1.4445 |  |  | 0.18 | 0.385 | [5 empty] | 27.85 |  |  |  |  | 55.7 |  | 18.55 |  | 9.7 | 0.1355 |  | 4.4 | 100.43 | 1.45 |  |  |  |  | 18.337 | 14.2625 | [6 empty] | 10.4 | 21.26 | 8.66
2009-12-09 | 6.82 | 6.56 |  |  |  |  | 7.06 | 1.74 |  |  |  |  | 52 |  |  |  | 0 | 1.31 |  |  | 0.159 | 0.325 | [5 empty] | 26.9 |  |  |  |  | 53.8 |  | 19.1 |  | 9.8 | 0.197 |  | 4.4 | 105.16 | 1.48 |  |  |  |  | 18.571 | 14.824 | [6 empty] | 10.4 | 21.26 | 8.66
2009-12-10 | 6.85 | 6.94 |  |  |  |  | 7.54 | 1.76 |  |  |  |  | 53 |  |  |  | 0 | 1.369 |  |  | 0.148 | 0.298 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 21.2 |  | 8.9 | 0.063 |  | 4.2 | 105.11 | 1.47 |  |  |  |  | 18.502 | 14.79 | [6 empty] | 10.4 | 21.26 | 8.66
2009-12-11 | 6.86 | 7.14 |  |  |  |  | 7.43 | 1.7 |  |  |  |  | 53 |  |  |  | 0 | 1.28 |  |  | 0.275 | 0.328 | [5 empty] | 29.2 |  |  |  |  | 58.6 |  | 20.1 |  | 9.1 | 0.096 |  | 4 | 105.11 | 1.5 |  |  |  |  | 18.718 | 14.928 | [6 empty] | 10.4 | 21.26 | 8.66
2009-12-12 | 6.84 | 6.89 |  |  |  |  | 7.5 | 1.86 |  |  |  |  | 50 |  |  |  | 0 | 1.167 |  |  | 0.256 | 0.286 | [5 empty] | 30.1 |  |  |  |  | 60 |  | 21.1 |  | 8.8 | 0.088 |  | 4 | 100.66 | 1.26 |  |  |  |  | 18.37 | 14.63 | [6 empty] | 10.4 | 21.26 | 9.02
2009-12-13 | 6.785 | 6.89 |  |  |  |  | 7.215 | 1.86 |  |  |  |  | 60 |  |  |  | 0 | 0.924 |  |  | 0.3345 | 0.3435 | [5 empty] | 29.6 |  |  |  |  | 59.1 |  | 21.1 |  | 9.5 | 0.0995 |  | 3.9 | 100.46 | 1.23 |  |  |  |  | 19.136 | 14.9275 | [6 empty] | 10.4 | 21.26 | 9.02
2009-12-14 | 6.73 | 6.89 |  |  |  |  | 6.93 | 1.8 |  |  |  |  | 70 |  |  |  | 0 | 0.681 |  |  | 0.413 | 0.401 | [5 empty] | 29.1 |  |  |  |  | 58.2 |  | 21.1 |  | 10.2 | 0.111 |  | 3.8 | 110.01 | 1.48 |  |  |  |  | 19.902 | 15.225 | [6 empty] | 10.4 | 21.26 | 9.02
2009-12-15 | 6.73 | 6.95 |  |  |  |  | 7.44 | 1.93 |  |  |  |  | 62 |  |  |  | 0 | 1.024 |  |  | 0.242 | 0.327 | [5 empty] | 30.1 |  |  |  |  | 60.2 |  | 21.6 |  | 11.1 | 0.223 |  | 4.4 | 110.01 | 1.55 |  |  |  |  | 17.791 | 14.371 | [6 empty] | 10.4 | 21.26 | 9.54
2009-12-16 | 6.72 | 6.82 |  |  |  |  | 7.69 | 1.7 |  |  |  |  | 51 |  |  |  | 0 | 0.94 |  |  | 0.194 | 0.27 | [5 empty] | 31.2 |  |  |  |  | 62.4 |  | 20.8 |  | 9.6 | 0.118 |  | 3.8 | 100.24 | 1.38 |  |  |  |  | 18.999 | 14.795 | [6 empty] | 9.61 | 21.26 | 9.54
2009-12-17 | 6.85 | 6.2 |  |  |  |  | 7.15 | 1.85 |  |  |  |  | 50 |  |  |  | 0 | 0.878 |  |  | 0.316 | 0.319 | [5 empty] | 31.4 |  |  |  |  | 62.85 |  | 21.65 |  | 8.75 | 0.101 |  | 3.85 | 107.57 | 1.31 |  |  |  |  | 17.772 | 16.772 | [6 empty] | 10.005 | 21.26 | 9.805
2009-12-18 | 6.84 | 7.08 |  |  |  |  | 6.95 | 2.07 |  |  |  |  | 52 |  |  |  | 0 | 0.835 |  |  | 0.241 | 0.328 | [5 empty] | 31.6 |  |  |  |  | 63.3 |  | 22.5 |  | 7.9 | 0.084 |  | 3.9 | 114.9 | 1.24 |  |  |  |  | 16.738 | 15.774 | [6 empty] | 10.4 | 21.26 | 10.07
2009-12-19 | 6.77 | 7.13 |  |  |  |  | 7.08 | 2.15 |  |  |  |  | 41 |  |  |  | 0 | 0.779 |  |  | 0.146 | 0.345 | [5 empty] | 34.2 |  |  |  |  | 68.5 |  | 20.1 |  | 9.8 | 0.074 |  | 3.7 | 115.38 | 1.21 |  |  |  |  | 16.59 | 15.6 | [6 empty] | 10.4 | 21.26 | 10.78
2009-12-20 | 6.745 | 7.175 |  |  |  |  | 6.92 | 2 |  |  |  |  | 42 |  |  |  | 0 | 0.7665 |  |  | 0.211 | 0.38 | [5 empty] | 31.95 |  |  |  |  | 63.95 |  | 20.2 |  | 10.6 | 0.162 |  | 3.65 | 99.31 | 1.05 |  |  |  |  | 15.75 | 14.768 | [6 empty] | 10.4 | 21.26 | 10.78
2009-12-21 | 6.72 | 7.22 |  |  |  |  | 6.76 | 2.1 |  |  |  |  | 43 |  |  |  | 0 | 0.754 |  |  | 0.276 | 0.415 | [5 empty] | 29.7 |  |  |  |  | 59.4 |  | 20.3 |  | 11.4 | 0.25 |  | 3.6 | 115.39 | 1.24 |  |  |  |  | 17.12 | 15.23 | [6 empty] | 10.4 | 21.26 | 10.78
2009-12-22 | 6.86 | 6.84 |  |  |  |  | 6.92 | 2.06 |  |  |  |  | 59 |  |  |  | 0 | 0.7 |  |  | 0.153 | 0.291 | [5 empty] | 33.9 |  |  |  |  | 67.8 |  | 21.1 |  | 12.2 | 0.023 |  | 3.5 | 110.98 | 1.14 |  |  |  |  | 16.735 | 15.754 | [6 empty] | 10.4 | 21.26 | 10.78
2009-12-23 | 6.89 | 6.94 |  |  |  |  | 6.95 | 1.99 |  |  |  |  | 58 |  |  |  | 0 | 0.629 |  |  | 0.17 | 0.301 | [5 empty] | 29.6 |  |  |  |  | 59.3 |  | 23.5 |  | 11.4 | 0.044 |  | 3.8 | 116.07 | 1.24 |  |  |  |  | 17.603 | 16.211 | [6 empty] | 10.4 | 21.26 | 10.78
2009-12-24 | 6.8 | 6.92 |  |  |  |  | 7.34 | 1.9 |  |  |  |  | 69 |  |  |  | 0 | 0.66 |  |  | 0.159 | 0.294 | [5 empty] | 36.3 |  |  |  |  | 72.7 |  | 22.3 |  | 10.1 | 0.074 |  | 3.8 | 111 | 1.23 |  |  |  |  | 17.05 | 15.95 | [6 empty] | 10.4 | 21.26 | 12.54
2009-12-25 | 6.91 | 6.9 |  |  |  |  | 7.43 | 1.77 |  |  |  |  | 56 |  |  |  | 0 | 0.683 |  |  | 0.163 | 0.306 | [5 empty] | 31.3 |  |  |  |  | 62.6 |  | 20.7 |  | 11.2 | 0.037 |  | 3.8 | 89.96 | 1.05 |  |  |  |  | 15.431 | 14.474 | [6 empty] | 10.4 | 21.26 | 11.66
2009-12-26 | 6.74 | 6.89 |  |  |  |  | 7.09 | 1.95 |  |  |  |  | 45 |  |  |  | 0 | 0.642 |  |  | 0.21 | 0.267 | [5 empty] | 32.8 |  |  |  |  | 65.6 |  | 23.2 |  | 12.7 | 0.063 |  | 3.4 | 110.91 | 1.3 |  |  |  |  | 16.47 | 15.48 | [6 empty] | 10.4 | 21.26 | 11.66
2009-12-27 | 6.74 | 6.825 |  |  |  |  | 7.035 | 1.78 |  |  |  |  | 47 |  |  |  | 0 | 0.623 |  |  | 0.242 | 0.3365 | [5 empty] | 33.75 |  |  |  |  | 67.45 |  | 22.7 |  | 12.2 | 0.067 |  | 3.8 | 99.75 | 1.25 |  |  |  |  | 16.7045 | 15.4265 | [6 empty] | 10.4 | 21.26 | 11.66
2009-12-28 | 6.74 | 6.76 |  |  |  |  | 6.98 | 1.92 |  |  |  |  | 49 |  |  |  | 0 | 0.604 |  |  | 0.274 | 0.406 | [5 empty] | 34.7 |  |  |  |  | 69.3 |  | 22.2 |  | 11.7 | 0.071 |  | 4.2 | 115.39 | 1.49 |  |  |  |  | 16.939 | 15.373 | [6 empty] | 10.4 | 21.26 | 11.66
2009-12-29 | 6.75 | 6.8 |  |  |  |  | 6.88 | 1.79 |  |  |  |  | 64 |  |  |  | 0 | 0.576 |  |  | 0.183 | 0.353 | [5 empty] | 35.6 |  |  |  |  | 71.2 |  | 22.5 |  | 14.5 | 0.218 |  | 4.8 | 94.77 | 0.95 |  |  |  |  | 16.569 | 15.708 | [6 empty] | 10.4 | 21.26 | 11.66
2009-12-30 | 6.75 | 6.81 |  |  |  |  | 7.28 | 1.67 |  |  |  |  | 62 |  |  |  | 0 | 0.67 |  |  | 0.193 | 0.324 | [5 empty] | 36.5 |  |  |  |  | 73 |  | 24.9 |  | 14.8 | 0.192 |  | 3.9 | 94.86 | 0.94 |  |  |  |  | 17.537 | 16.529 | [6 empty] | 10.4 | 21.26 | 11.66
2009-12-31 | 6.79 | 6.69 |  |  |  |  | 7.59 | 1.77 |  |  |  |  | 51 |  |  |  | 0 | 0.483 |  |  | 0.126 | 0.259 | [5 empty] | 35.1 |  |  |  |  | 70.2 |  | 20.1 |  | 14.7 | 0.143 |  | 3.9 | 89.96 | 0.73 |  |  |  |  | 16.739 | 15.761 | [6 empty] | 10.4 | 21.26 | 10.78
| Finish Water (ML) | [11 empty] | Finish Water (ML)
|  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 |  |  |  |  | Max Value | Min Value
| January | 13.98 | 15 | 13.78 | 11.91 | 13.16 | 13.16 | 12.28 |  |  |  | 2009 | 17.56 | 10.71
| February | 14.03 | 14.82 | 14.11 | 12.49 | 13.48 | 13.95 | 12.24 |  |  |  | 2010 | 17.55 | 12.16
| March | 14.59 | 14.86 | 14.35 | 12.63 | 13.36 | 13.81 | 12.04 |  |  |  | 2011 | 15.942 | 9.683
| April | 14.84 | 14.67 | 13.68 | 12.89 | 12.99 | 13.01 | 12.24 |  |  |  | 2012 | 22.417 | 9.512
| May | 15.22 | 13.94 | 12.28 | 14.38 | 13.22 | 13.23 | 11.7 |  |  |  | 2013 | 18.668 | 1.811
| June | 15.04 | 15.03 | 12.54 | 16.74 | 12.98 | 12.86 | 12.22 |  |  |  | 2014 | 18.743 | 9.931
| July | 15.63 | 15.66 | 13.5 | 15.2 | 15.3 | 16.21 | 13.33 |  |  |  | 2015 | 16.475 | 10.208
| August | 14.33 | 15.29 | 12.94 | 13.85 | 14.5 | 13.16 | 13.45
| September | 14.33 | 14.1 | 12.17 | 13.08 | 12.43 | 12.03 | 14.15
| October | 15.15 | 13.72 | 11.68 | 12.7 | 13.1 | 12.65 | 15.17
| November | 13.74 | 13.76 | 11.63 | 12.4 | 12.64 | 11.57 | 14.96
| December | 14.99 | 13.56 | 11.75 | 12.75 | 13.13 | 11.78 | 14.27
| ANNUAL | 14.66 | 14.53 | 12.87 | 13.42 | 13.36 | 13.12 | 13.17
|  | 2009: Turbidity (Raw) |  |  |  |  | Turbidity (Raw)
|  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 |  |  |  |  | Max Value | Min Value
| January | 0.23 | 0.42 | 1.05 | 0.96 | 0.26 | 0.44 | 0.48 |  |  |  | 2009 | 3.612 | 0.041
| February | 0.14 | 0.35 | 0.47 | 0.75 | 0.25 | 0.36 | 0.39 |  |  |  | 2010 | 2.701 | 0.24
| March | 0.16 | 0.31 | 0.4 | 1.07 | 0.23 | 0.31 | 0.33 |  |  |  | 2011 | 3.812 | 0.029
| April | 0.15 | 0.33 | 0.3 | 0.62 | 0.27 | 0.48 | 0.38 |  |  |  | 2012 | 2.806 | 0.02
| May | 0.32 | 0.42 | 0.71 | 0.98 | 0.75 | 0.4 | 0.44 |  |  |  | 2013 | 4.671 | 0.164
| June | 0.27 | 0.41 | 1.54 | 0.69 | 0.89 | 0.77 | 0.55 |  |  |  | 2014 | 3.165 | 0.0972
| July | 0.19 | 0.59 | 1.55 | 0.6 | 2 | 0.49 | 0.54 |  |  |  | 2015 | 1.378 | 0.001
| August | 0.43 | 0.58 | 1.04 | 0.24 | 0.6 | 0.5 | 0.57
| September | 0.71 | 0.7 |  | 0.62 | 0.79 | 0.74 | 0.6
| October | 0.61 | 0.73 | 0.71 | 0.82 | 0.85 | 0.95 | 0.62
| November | 0.95 | 1.16 | 0.9 | 0.51 | 0.81 | 1.51 | 0.93
| December | 1.09 | 1.33 | 0.72 | 0.4 | 0.74 | 0.81 | 0.64
| ANNUAL | 0.44 | 0.61 | 0.85 | 0.69 | 0.7 | 0.65 | 0.54
|  | Turbidity (Raw) 2009: Turbidity (Finish) | [8 empty] | True Colour
|  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 |  |  |  |  | Turbidity (Finish) |  |  |  |  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015
| January | 0.16 | 0.31 | 0.28 | 0.27 | 0.24 | 0.31 | 0.75 |  |  |  |  | Max Value | Min Value |  |  | January | 52.32 | 47.44 | 41.81 | 44.52 | 36.37 | 43.76 | 37.63
62 | February | 0.71 | 0.42 | 0.14 | 0.3 | 0.34 | 0.2 | 0.96 |  |  |  | 2009 | 7.06 | 0.036 |  |  | February | 51.8 | 38.27 | 31.2 | 37.68 | 37.97 | 42.77 | 38.78
93 | March | 0.21 | 0.29 | 0.21 | 0.27 | 0.21 | 0.19 | 0.71 |  |  |  | 2010 | 1.126 | 0.058 |  |  | March | 47.06 | 35.15 | 35.48 | 40.93 | 38.05 | 40.15 | 37.34
123 | April | 0.16 | 0.29 | 0.16 | 0.39 | 0.12 | 0.19 | 0.65 |  |  |  | 2011 | 1.14 | 0.06 |  |  | April | 44.9 | 39.03 | 36.58 | 40.98 | 37.27 | 45.93 | 38.12
154 | May | 0.16 | 0.18 | 0.14 | 0.19 | 0.1 | 0.14 | 0.62 |  |  |  | 2012 | 0.956 | 0.054 |  |  | May | 43.71 | 40.25 | 36.15 | 39.23 | 40.08 | 37.74 | 38.44
184 | June | 0.23 | 0.2 | 0.15 | 0.14 | 0.11 | 0.12 | 0.32 |  |  |  | 2013 | 0.826 | 0.037 |  |  | June | 32.09 | 38.52 | 41.88 | 30.47 | 29.13 | 32.22 | 32.48
215 | July | 0.16 | 0.24 | 0.29 | 0.09 | 0.08 | 0.1 | 0.23 |  |  |  | 2014 | 1.134 | 0.026 |  |  | July | 45.77 | 37.19 | 41.93 | 26.26 | 26.56 | 30.44 | 28.69
246 | August | 0.58 | 0.27 | 0.29 | 0.11 | 0.08 | 0.18 | 0.21 |  |  |  | 2015 | 7.69 | 0.098 |  |  | August | 53.18 | 37.21 | 38.28 | 23.45 | 28.15 | 24.55 | 29.6
276 | September | 0.54 | 0.49 | 0.12 | 0.12 | 0.08 | 0.1 | 0.18 | [8 empty] | September | 38.21 | 41.41 | 35.47 | 36.77 | 40.92 | 31.17 | 25
307 | October | 0.28 | 0.4 | 0.21 | 0.11 | 0.1 | 0.24 | 0.43 | [8 empty] | October | 43.87 | 48.97 | 45.82 | 41.13 | 39.21 | 26.75 | 25.32
337 | November | 0.43 | 0.59 | 0.28 | 0.1 | 0.12 | 0.37 | 0.62 | [8 empty] | November | 46.1 | 47.58 | 50.66 | 39.87 | 37.12 | 46.78 | 28.87
368 | December | 0.33 | 0.54 | 0.2 | 0.31 | 0.15 | 0.54 | 0.42 | [8 empty] | December | 55.26 | 48.9 | 58.03 | 45.66 | 46.35 | 47.61 | 30.73
| ANNUAL | 0.33 | 0.35 | 0.21 | 0.2 | 0.14 | 0.22 | 0.51 | [8 empty] | ANNUAL | 46.19 | 41.66 | 41.11 | 37.25 | 36.43 | 37.49 | 32.58
|  | Turbidity (Finish) 2009: pH (Raw) |  |  |  |  | pH (Raw)
|  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 |  |  |  |  | Max Value | Min Value
| January | 6.76 | 6.81 | 6.37 | 6.4 | 5.93 | 6.05 | 6.05 |  |  |  | 2009 | 8.44 | 5.42
| February | 6.71 | 6.57 | 6.36 | 6.4 | 5.81 | 6.07 | 5.93 |  |  |  | 2010 | 7.71 | 4.71
| March | 6.61 | 6.55 | 6.36 | 6.39 | 5.86 | 6.01 | 5.96 |  |  |  | 2011 | 7.44 | 5.52
| April | 6.56 | 6.48 | 6.25 | 6.35 | 5.89 | 5.94 | 5.8 |  |  |  | 2012 | 7.7 | 5.15
| May | 6.85 | 6.3 | 6.37 | 6.4 | 6.06 | 6.12 | 5.86 |  |  |  | 2013 | 6.79 | 5.13
| June | 7.02 | 6.37 | 6.33 | 6.53 | 5.98 | 6.2 | 6.13 |  |  |  | 2014 | 7.09 | 5.4
| July | 6.95 | 6.23 | 6.53 | 6.64 | 6.19 | 6.26 | 6.06 |  |  |  | 2015 | 7.08 | 5.34
| August | 6.75 | 6.71 | 6.45 | 6.5 | 6.3 | 6.43 | 6.07
| September | 6.8 | 6.63 | 6.43 | 6.5 | 6.27 | 6.48 | 6.13
| October | 6.73 | 6.64 | 6.53 | 6.29 | 6.24 | 6.35 | 6.56
| November | 6.79 | 6.42 | 6.7 | 6.19 | 6.23 | 6.34 | 6.35
| December | 6.79 | 6.43 | 6.43 | 5.88 | 6.1 | 6.12 | 6.28
| ANNUAL | 6.78 | 6.51 | 6.43 | 6.37 | 6.07 | 6.2 | 6.1
|  | pH (Raw) 2009: pH (Finish) |  |  |  |  | pH (Finish)
|  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 |  |  |  |  | Max Value | Min Value
| January | 7.02 | 7.03 | 7.92 | 7.25 | 7.43 |  | 7.04 |  |  |  | 2009 | 8.62 | 1.73
| February | 7.33 | 7.18 | 7.78 | 7.39 | 7.36 |  | 6.99 |  |  |  | 2010 | 8.77 | 1.43
| March | 7.03 | 7.06 | 7.32 | 7.1 | 7.36 |  | 6.92 |  |  |  | 2011 | 9.16 | 5.06
| April | 6.88 | 7.24 | 7.43 | 7.08 | 7.44 |  | 6.91 |  |  |  | 2012 | 9.03 | 3.94
| May | 7.38 | 7.32 | 7.44 | 7.27 | 7.79 |  | 7.19 |  |  |  | 2013 | 9.11 | 4.42
| June | 7.2 | 7.18 | 7.36 | 7.72 | 7.42 |  | 7.47 |  |  |  | 2014
| July | 7.15 | 7.17 | 7.18 | 7.69 | 7.65 |  | 7.2 |  |  |  | 2015 | 8.47 | 4.83
| August | 7.18 | 7.26 | 7.15 | 7.48 | 7.39 |  | 7.43
| September | 6.87 | 7.26 | 7.27 | 7.34 | 7.36 |  | 7.09
| October | 7.07 | 7.14 | 7.22 | 8.04 | 7.1 |  | 6.84
| November | 7.15 | 7.27 | 7.3 | 8.3 | 7.54 |  | 6.76
| December | 7.24 | 7.17 | 7.51 | 7.34 | 6.96 |  | 6.7
| ANNUAL | 7.13 | 7.19 | 7.41 | 7.5 | 7.4 |  | 7.05
|  | pH (Finish) 2009: Free Chlorine (mg/L) |  |  |  |  | Free Chlorine (mg/L)
|  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 |  |  |  |  | Max Value | Min Value
| January | 2.06 | 1.57 | 1.49 | 1.83 | 1.86 | 1.74 | 1.72 |  |  |  | 2009 | 7.86 | 1.05
| February | 1.74 | 1.26 | 1.29 | 1.43 | 1.67 | 1.9 | 1.62 |  |  |  | 2010 | 2.98 | 0.91
| March | 1.77 | 1.21 | 1.05 | 1.35 | 1.78 | 1.87 | 1.81 |  |  |  | 2011 | 2.1 | 0.58
| April | 1.55 | 1.31 | 0.96 | 1.36 | 1.82 | 1.83 | 1.48 |  |  |  | 2012 | 2.52 | 0.41
| May | 1.57 | 1.22 | 0.96 | 1.49 | 1.98 | 2.04 | 1.76 |  |  |  | 2013 | 2.64 | 0.885
| June | 1.68 | 1.24 | 1.03 | 1.53 | 1.88 | 1.92 | 1.57 |  |  |  | 2014 | 2.98 | 0.341
| July | 1.53 | 1.4 | 1.11 | 1.78 | 1.89 | 2.11 | 1.62 |  |  |  | 2015 | 6.59 | 1.24
| August | 1.76 | 1.76 | 1.32 | 1.95 | 2.1 | 1.85 | 1.89
| September | 2.21 | 1.69 | 1.15 | 1.98 | 2.06 | 1.96 | 1.91
| October | 1.9 | 1.58 | 1.21 | 2.06 | 2.15 | 1.87 | 1.87
| November | 1.8 | 1.66 | 1.85 | 1.8 | 2.19 | 1.69 | 1.78
| December | 1.84 | 1.45 | 1.87 | 1.83 | 2.08 | 1.86 | 1.79
| ANNUAL | 1.78 | 1.45 | 1.27 | 1.7 | 1.96 | 1.89 | 1.74
|  | Free Chlorine (mg/L) 2009: Alum (mg/L) |  |  |  |  | Alum (mg/L)
|  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 |  |  |  |  | Max Value | Min Value
| January | 14.32 | 10.51 | 28.34 | 26.88 | 32.33 | 31.84 | 28.1 |  |  |  | 2009 | 15.47 | 2
| February | 6.63 | 10.02 | 30.69 | 27.1 | 32.07 | 32.81 | 29.86 |  |  |  | 2010 | 38.72 | 5.17
| March | 10.19 | 9.49 | 31.61 | 29 | 31 | 31.37 | 29.16 |  |  |  | 2011 | 48.81 | 15.03
| April | 9.21 | 10.66 | 37.95 | 26.35 | 27.72 | 31.06 | 30.1 |  |  |  | 2012 | 76.16 | 11.78
| May | 8.11 | 9.64 | 38 | 28.56 | 28.01 | 31.44 | 30.13 |  |  |  | 2013 | 39.33 | 3.014
| June | 7.51 | 8.95 | 36.29 | 31.05 | 28.12 | 30.84 | 29.61 |  |  |  | 2014 | 37.46 | 22.61
| July | 7.66 | 7.93 | 26.87 | 30.64 | 28.9 | 29.77 | 28.68 |  |  |  | 2015 | 35.59 | 14.085
| August | 6.7 | 8.11 | 31.55 | 29 | 27.84 | 31.77 | 29.39
| September | 9.32 | 10.28 | 33.76 | 30.67 | 29.04 | 31.19 | 30.43
| October | 11.54 | 10.81 | 30.85 | 33.33 | 29.65 | 30.68 | 30.01
| November | 9 | 17.19 | 29.52 | 34.59 | 30.79 | 31.24 | 29.3
| December | 10.36 | 24.67 | 29.26 | 34.4 | 30.75 | 30.99 | 30.63
| ANNUAL | 9.21 | 11.52 | 32.06 | 30.13 | 29.69 | 31.25 | 29.62
|  | Alum (mg/L) 2009: Alkalinity (Finish) |  |  |  |  | Alkalinity (Finish)
|  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 |  |  |  |  | Max Value | Min Value
| January | 10 | 9.79 | 10.3 | 7.71 | 8.71 | 7.99 | 7.11 |  |  |  | 2009 | 14.8 | 4.3
| February | 10 | 10.73 | 10.28 | 8.67 | 8.72 | 8.01 | 6.68 |  |  |  | 2010 | 19 | 3.3
| March | 10 | 11.83 | 10.12 | 8.63 | 7.67 | 7.7 | 6.84 |  |  |  | 2011 | 16.5 | 5
| April | 10 | 10.89 | 10.7 | 8.06 | 7.56 | 8.42 | 7.76 |  |  |  | 2012 | 13.6 | 1
| May | 10 | 7.69 | 8.93 | 7.74 | 6.4 | 6.38 | 7.1 |  |  |  | 2013 | 11.5 | 2
| June | 10 | 10.76 | 7.63 | 6.69 | 6.21 | 5.75 | 6.93 |  |  |  | 2014 | 11.6 | 1.7
| July | 10 | 10.8 | 7.88 | 7.93 | 6.07 | 6.14 | 6.81 |  |  |  | 2015 | 10 | 1.4
| August | 10 | 8.68 | 7.19 | 7.71 | 7.11 | 6.93 | 7.14
| September | 7.73 | 9.25 | 7.78 | 7.67 | 6.85 | 6.79 | 6.83
| October | 8.17 | 8.85 | 7.13 | 7.63 | 7.06 | 5.87 | 5.74
| November | 8.61 | 7.89 | 7.03 | 7.82 | 7.01 | 6 | 5.8
| December | 10.56 | 9.04 | 6.93 | 7.42 | 6.41 | 6.21 | 5.88
| ANNUAL | 9.59 | 9.68 | 8.49 | 7.81 | 7.15 | 6.85 | 6.72
|  | Alkalinity (Finish) 2009: Hardness (Finish) |  |  |  |  | Hardness (Finish)
|  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 |  |  |  |  | Max Value | Min Value
| January | 22.49 | 23.51 | 26.15 | 24.4 | 25.04 | 23.89 | 25.27 |  |  |  | 2009 | 35.2 | 0.58
| February | 22.93 | 22.2 | 26.54 | 26.12 | 24.83 | 24.65 | 23.73 |  |  |  | 2010 | 40.4 | 7.6
| March | 23.97 | 22.86 | 25.83 | 26.48 | 24.51 | 24.24 | 22.54 |  |  |  | 2011 | 58.6 | 14.7
| April | 20.56 | 23.4 | 24.03 | 25.63 | 25.06 | 23.51 | 23.23 |  |  |  | 2012 | 36.4 | 20.8
| May | 19.27 | 17.7 | 23.67 | 25.84 | 25.39 | 23.57 | 22.7 |  |  |  | 2013 | 44.2 | 12.4
| June | 17.39 | 20.59 | 23.74 | 27.4 | 24.28 | 23.42 | 22.66 |  |  |  | 2014 | 28.3 | 15.2
| July | 17.85 | 22.36 | 22.81 | 24.55 | 24.68 | 22.02 | 22.6 |  |  |  | 2015 | 27.9 | 21
| August | 19.87 | 21.86 | 24.02 | 25.24 | 24.32 | 23.81 | 23.35
| September | 22.52 | 24.38 | 24.28 | 25.54 | 24.29 | 24.02 | 23.83
| October | 20.66 | 23.12 | 25.25 | 24.6 | 24.99 | 23.61 | 24.16
| November | 21.42 | 25.02 | 23.9 | 25.41 | 23.95 | 24.03 | 23.78
| December | 21.37 | 25.68 | 24.69 | 24.75 | 22.97 | 23.2 | 24.14
| ANNUAL | 20.86 | 22.72 | 24.58 | 25.5 | 24.53 | 23.66 | 23.5
|  | Hardness (Finish) 2009: Temperature (Finish) |  |  |  |  | Temperature (Finish)
|  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 |  |  |  |  | Max Value | Min Value
| January | 3.35 | 3.46 | 4.19 | 3.15 | 4 | 2.73 | 3.68 |  |  |  | 2009 | 20.2 | 2.5
| February | 2.77 | 4.03 | 3.64 | 3.25 | 3.69 | 2.99 | 3.42 |  |  |  | 2010 | 20.6 | 1.02
| March | 3.13 | 3.75 | 3.74 | 3.53 | 3.6 | 3.28 | 3.09 |  |  |  | 2011 | 18.2 | 2.5
| April | 3.97 | 5.54 | 3.88 | 3.9 | 3.67 | 2.9 | 3.75 |  |  |  | 2012 | 43 | 2.7
| May | 8.93 | 8.19 | 7.74 | 8.9 | 8.54 | 6.8 | 6.15 |  |  |  | 2013 | 19.4 | 1.4
| June | 14.1 | 12.15 | 11.64 | 12.45 | 12.65 | 12.72 | 13.34 |  |  |  | 2014 | 21.6 | 1.9
| July | 17.86 | 17.4 | 15.07 | 17.34 | 17.24 | 19.7 | 15.89 |  |  |  | 2015 | 28 | 2.3
| August | 18.81 | 19.08 | 17.19 | 18.93 | 18.46 | 19.2 | 18.22
| September | 14.34 | 15.82 | 16.12 | 16.54 | 15.32 | 15.36 | 15.78
| October | 9.32 | 11.64 | 11.91 | 11.68 | 11.45 | 10.86 | 10.73
| November | 5.23 | 7.89 | 7.02 | 7.55 | 5.81 | 5.53 | 5.06
| December | 4.04 | 5.28 | 3.72 | 6.09 | 2.7 | 3.67 | 3.54
| ANNUAL | 8.82 | 9.52 | 8.82 | 9.44 | 8.93 | 8.81 | 8.55
|  | Temperature (Finish) 2009: Total Dissolved Solids (Finish) |  |  |  |  | TDS (Finish)
|  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 |  |  |  |  | Max Value | Min Value
| January | 28.04 | 28.28 | 37.16 | 34.5 | 36 | 33.41 | 30.72 |  |  |  | 2009 | 36.5 | 16.3
| February | 29.14 | 28.7 | 38.92 | 35.47 | 37.04 | 35.36 | 31.15 |  |  |  | 2010 | 36.6 | 17.6
| March | 30.46 | 30.37 | 40.92 | 33.73 | 34.13 | 37.19 | 33.03 |  |  |  | 2011 | 49.2 | 21.7
| April | 25.21 | 27.32 | 35.98 | 32.08 | 31.73 | 35.85 | 34.3 |  |  |  | 2012 | 41.4 | 22.1
| May | 22.1 | 24.1 | 30.09 | 28.21 | 27.55 | 29.8 | 27.73 |  |  |  | 2013 | 46.5 | 21.1
| June | 20.5 | 28.87 | 29.78 | 28.82 | 27.8 | 25.9 | 26.06 |  |  |  | 2014 | 46.7 | 16.8
| July | 21.55 | 28.9 | 29.95 | 28.88 | 27.45 | 27.01 | 25.54 |  |  |  | 2015 | 39.2 | 21
| August | 22.83 | 27.38 | 30.01 | 29.35 | 27.96 | 35.01 | 27.45
| September | 24.88 | 31.33 | 32.02 | 30.24 | 29.78 | 28.44 | 27.27
| October | 28.61 | 28.61 | 31 | 33.68 | 29.49 | 27.62 | 25.68
| November | 27.39 | 29.47 | 29.79 | 33.79 | 31.19 | 27.99 | 26.51
| December | 30.86 | 29.46 | 30.96 | 32.86 | 31.01 | 33.5 | 27.74
| ANNUAL | 25.96 | 28.57 | 33.05 | 31.8 | 30.93 | 31.42 | 28.6
|  | Total Dissolved Solids (Finish) 2009: Free Aluminum (mg/L) |  |  |  | Free Aluminum (mg/L)
|  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 |  |  |  |  | Max Value | Min Value
| January | 0.092 | 0.13 | 0.138 | 0.081 | 0.104 | 0.08 | 0.06 |  |  |  | 2009 | 0.963 | 0.005
| February | 0.129 | 0.09 | 0.061 | 0.087 | 0.088 | 0.065 | 0.047 |  |  |  | 2010 | 2.5 | 0.013
| March | 0.089 | 0.077 | 0.056 | 0.081 | 0.083 | 0.078 | 0.059 |  |  |  | 2011 | 0.22 | 0.001
| April | 0.093 | 0.106 | 0.045 | 0.05 | 0.072 | 0.073 | 0.038 |  |  |  | 2012 | 0.86 | 0.001
| May | 0.095 | 0.124 | 0.072 | 0.129 | 0.092 | 0.071 | 0.059 |  |  |  | 2013 | 2 | 0.008
| June | 0.113 | 0.215 | 0.07 | 0.082 | 0.066 | 0.076 | 0.075 |  |  |  | 2014 | 0.76 | 0.001
| July | 0.084 | 0.216 | 0.111 | 0.065 | 0.073 | 0.054 | 0.067 |  |  |  | 2015 | 0.36 | 0.0005
| August | 0.172 | 0.276 | 0.088 | 0.062 | 0.076 | 0.09 | 0.082
| September | 0.09 | 0.204 | 0.062 | 0.097 | 0.082 | 0.071 | 0.043
| October | 0.044 | 0.161 | 0.097 | 0.102 | 0.083 | 0.081 | 0.039
| November | 0.066 | 0.128 | 0.105 | 0.118 | 0.075 | 0.048 | 0.071
| December | 0.106 | 0.138 | 0.099 | 0.106 | 0.17 | 0.074 | 0.032
| ANNUAL | 0.098 | 0.155 | 0.084 | 0.088 | 0.089 | 0.072 | 0.056

## 2010
All of the data presented below was copied verbatim from spreadsheets transcribed by Debbie Rideout, Town PLO
| pH | [6 empty] | Chlorine |  |  |  | Colour | [5 empty] | Turbidity | [5 empty] | Total Dissolved Solids |  |  |  |  | Conductivity |  |  |  |  | Hardness |  | Alkalinity |  | Aluminum | Temperature |  | Cl Used | Cl Demand | UVT |  | UVA |  | Flows within plant |  |  |  | Flows from plant |  |  | Chemical Dosages
Date | Raw | PTC | PTC (OL) | SWC | Filter | Finish (OL) | Finish | Free | Total | Sample | Analyzer | Raw A | Raw T | SWC A | Filter A | Finish A | Finish T | Raw | Raw (OL) | SWC | Filter | Finish | Finish (OL) | Raw | PTC | SWC | Filter | Finish | Raw | PTC | SWC | Filter | Finish | Raw | Finish | Raw | Finish | Finish (Free) | Raw | Finish |  |  | Raw | Filter | Raw | Filter | Raw | Finish | Filter | Backwash | Bishop's | Botwood | GFW | Chlorine | Alum | Limestone | Lime
2010-01-01 | 6.75 | 6.7 |  |  |  |  | 6.49 | 1.28 |  |  |  |  | 51 |  |  |  | 0 | 0.484 |  |  | 0.092 | 0.16 | [5 empty] | 36.6 |  |  |  |  | 73.2 |  | 21.9 |  | 9.2 | 0.125 |  | 3.4 | 85.55 | 1.24 |  |  |  |  | 16.41 | 15.4 | [6 empty] | 10.4 | 21.26 | 10.78
2010-01-02 | 6.73 | 6.76 |  |  |  |  | 8.26 | 1.37 |  |  |  |  | 40 |  |  |  | 0 | 0.505 |  |  | 0.243 | 0.671 | [5 empty] | 27.5 |  |  |  |  | 54.7 |  | 21 |  | 8.9 | 0.116 |  | 3.4 | 79.69 | 0.97 |  |  |  |  | 16.32 | 15.43 | [6 empty] | 10.4 | 21.26 | 6.55
2010-01-03 | 6.74 | 6.73 |  |  |  |  | 7.375 | 1.325 |  |  |  |  | 45.5 |  |  |  | 0 | 0.4945 |  |  | 0.1675 | 0.4155 | [5 empty] | 32.05 |  |  |  |  | 63.95 |  | 21.45 |  | 9.05 | 0.1205 |  | 3.4 | 75.28 | 0.91 |  |  |  |  | 16.245 | 15.298 | [6 empty] | 10.4 | 21.26 | 7.25
2010-01-04 | 6.86 | 6.88 |  |  |  |  | 4.86 | 1.61 |  |  |  |  | 43 |  |  |  | 0 | 0.467 |  |  | 0.278 | 0.491 | [5 empty] | 21.1 |  |  |  |  | 42.2 |  | 20.5 |  | 3.4 | 0.172 |  | 4.3 | 105.11 | 1.44 |  |  |  |  | 17.542 | 15.645 | [6 empty] | 10.4 | 21.26 | 7.25
2010-01-05 | 6.86 | 6.7 |  |  |  |  | 7.12 | 1.55 |  |  |  |  | 65 |  |  |  | 0 | 0.493 |  |  | 0.205 | 0.401 | [5 empty] | 25.6 |  |  |  |  | 51.2 |  | 19.7 |  | 13.6 | 0.163 |  | 4.4 | 89.96 | 1.18 |  |  |  |  | 16.026 | 14.971 | [6 empty] | 10.4 | 21.26 | 7.25
2010-01-06 | 6.86 | 6.63 |  |  |  |  | 6.8 | 1.55 |  |  |  |  | 41 |  |  |  | 0 | 0.507 |  |  | 0.527 | 0.679 | [5 empty] | 27.5 |  |  |  |  | 55 |  | 21.3 |  | 9.2 | 0.131 |  | 3.4 | 80.68 | 0.98 |  |  |  |  | 15.435 | 14.484 | [6 empty] | 10.4 | 21.26 | 8.66
2010-01-07 | 6.74 | 6.67 |  |  |  |  | 7.78 | 1.55 |  |  |  |  | 39 |  |  |  | 0 | 0.478 |  |  | 0.311 | 0.252 | [5 empty] | 26.3 |  |  |  |  | 52.7 |  | 23.2 |  | 10 | 0.128 |  | 3.5 | 100.22 | 1.21 |  |  |  |  | 17.419 | 16.483 | [6 empty] | 10.4 | 21.26 | 8.66
2010-01-08 | 6.82 | 6.82 |  |  |  |  | 7.3 | 1.55 |  |  |  |  | 54 |  |  |  | 0 | 0.504 |  |  | 0.301 | 0.219 | [5 empty] | 30 |  |  |  |  | 60 |  | 23.6 |  | 11.3 | 0.13 |  | 3.7 | 100.17 | 1.25 |  |  |  |  | 17.091 | 16.244 | [6 empty] | 10.4 | 21.26 | 9.02
2010-01-09 | 6.89 | 6.95 |  |  |  |  | 6.85 | 1.56 |  |  |  |  | 51 |  |  |  | 0 | 0.491 |  |  | 0.153 | 0.223 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 25.7 |  | 14.4 | 0.099 |  | 3.6 | 100.22 | 1.3 |  |  |  |  | 17.02 | 15.9 | [6 empty] | 10.4 | 21.26 | 9.02
2010-01-10 | 6.855 | 6.885 |  |  |  |  | 7.075 | 1.555 |  |  |  |  | 52.5 |  |  |  | 0 | 0.4975 |  |  | 0.227 | 0.221 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 24.65 |  | 12.85 | 0.1145 |  | 3.65 | 100.195 | 1.275 |  |  |  |  | 17.0555 | 16.072 | [6 empty] | 10.4 | 21.26 | 9.02
2010-01-11 | 6.74 | 7.01 |  |  |  |  | 7.02 | 1.61 |  |  |  |  | 51.75 |  |  |  | 0 | 0.44 |  |  | 0.277 | 0.64 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 23 |  | 12 | 0.205 |  | 3.4 | 99.82 | 1.56 |  |  |  |  | 16.118 | 14.302 | [6 empty] | 10.4 | 21.26 | 9.02
2010-01-12 | 6.84 | 6.59 |  |  |  |  | 7.33 | 1.8 |  |  |  |  | 45 |  |  |  | 0 | 0.414 |  |  | 0.107 | 0.133 | [5 empty] | 27.1 |  |  |  |  | 54.3 |  | 29.2 |  | 11.2 | 0.182 |  | 3.4 | 85.14 | 0.84 |  |  |  |  | 15.542 | 14.646 | [6 empty] | 10.4 | 21.26 | 9.54
2010-01-13 | 6.73 | 6.6 |  |  |  |  | 3.44 | 1.6 |  |  |  |  | 41 |  |  |  | 0 | 0.406 |  |  | 0.165 | 0.104 | [5 empty] | 20.1 |  |  |  |  | 40.3 |  | 30.8 |  | 7.4 | 0.119 |  | 3.4 | 79.48 | 0.93 |  |  |  |  | 15.24 | 14.3 | [6 empty] | 10.4 | 21.26 | 9.54
2010-01-14 | 6.785 | 6.595 |  |  |  |  | 5.385 | 1.7 |  |  |  |  | 43 |  |  |  | 0 | 0.41 |  |  | 0.136 | 0.1185 | [5 empty] | 23.6 |  |  |  |  | 47.3 |  | 30 |  | 9.3 | 0.1505 |  | 3.4 | 84.43 | 1.05 |  |  |  |  | 15.399 | 14.531 | [6 empty] | 10.4 | 21.26 | 9.54
2010-01-15 | 6.76 | 6.68 |  |  |  |  | 8.43 | 1.62 |  |  |  |  | 43 |  |  |  | 0 | 0.403 |  |  | 0.141 | 0.463 | [5 empty] | 25.8 |  |  |  |  | 52 |  | 28.8 |  | 8.8 | 0.115 |  | 3.3 | 89.94 | 1.16 |  |  |  |  | 15.566 | 14.71 | [6 empty] | 10.4 | 21.26 | 6.73
2010-01-16 | 6.83 | 6.89 |  |  |  |  | 6.94 | 1.61 |  |  |  |  | 43 |  |  |  | 0 | 0.405 |  |  | 0.176 | 0.295 | [5 empty] | 27.5 |  |  |  |  | 55 |  | 26.3 |  | 8.9 | 0.07 |  | 3.1 | 94.84 | 1.32 |  |  |  |  | 15.48 | 14.68 | [6 empty] | 10.4 | 21.26 | 7.25
2010-01-17 | 6.795 | 6.785 |  |  |  |  | 7.685 | 1.5 |  |  |  |  | 43 |  |  |  | 0 | 0.404 |  |  | 0.1585 | 0.379 | [5 empty] | 26.65 |  |  |  |  | 53.5 |  | 27.55 |  | 8.85 | 0.0925 |  | 3.2 | 85.51 | 1.26 |  |  |  |  | 14.923 | 14.086 | [6 empty] | 10.4 | 21.26 | 7.25
2010-01-18 | 6.75 | 6.89 |  |  |  |  | 7.27 | 1.54 |  |  |  |  | 49 |  |  |  | 0 | 0.419 |  |  | 0.373 | 0.74 | [5 empty] | 28.2 |  |  |  |  | 56.5 |  | 22.5 |  | 9 | 0.143 |  | 3.4 | 100.15 | 1.56 |  |  |  |  | 16.41 | 14.636 | [6 empty] | 10.4 | 21.26 | 7.25
2010-01-19 | 6.75 | 6.85 |  |  |  |  | 7.03 | 1.67 |  |  |  |  | 50 |  |  |  | 0 | 0.409 |  |  | 0.223 | 0.249 | [5 empty] | 28 |  |  |  |  | 56 |  | 26.6 |  | 9 | 0.055 |  | 3.3 | 100.72 | 1.33 |  |  |  |  | 16.361 | 15.242 | [6 empty] | 10.4 | 21.26 | 7.25
2010-01-20 | 6.88 | 6.91 |  |  |  |  | 6.87 | 1.45 |  |  |  |  | 54 |  |  |  | 0 | 0.397 |  |  | 0.206 | 0.177 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 25.4 |  | 11.9 | 0.14 |  | 3.3 | 94.35 | 1.42 |  |  |  |  | 15.804 | 14.92 | [6 empty] | 10.4 | 21.26 | 9.02
2010-01-21 | 6.85 | 6.85 |  |  |  |  | 6.87 | 1.53 |  |  |  |  | 45 |  |  |  | 0 | 0.378 |  |  | 0.277 | 0.187 | [5 empty] | 29.8 |  |  |  |  | 59.6 |  | 24.4 |  | 11.3 | 0.073 |  | 3.2 | 99.6 | 1.48 |  |  |  |  | 16.721 | 15.024 | [6 empty] | 10.4 | 21.26 | 9.02
2010-01-22 | 6.86 | 6.94 |  |  |  |  | 7.2 | 1.55 |  |  |  |  | 51 |  |  |  | 0 | 0.371 |  |  | 0.208 | 0.123 | [5 empty] | 29.5 |  |  |  |  | 59.2 |  | 23.6 |  | 10.6 | 0.098 |  | 3.5 | 90.45 | 1.23 |  |  |  |  | 15.688 | 14.759 | [6 empty] | 10.4 | 21.26 | 9.02
2010-01-23 | 6.84 | 6.94 |  |  |  |  | 7.3 | 1.65 |  |  |  |  | 48 |  |  |  | 0 | 0.37 |  |  | 0.225 | 0.183 | [5 empty] | 28.2 |  |  |  |  | 56.5 |  | 22.9 |  | 10.6 | 0.081 |  | 3.2 | 90.45 | 1.11 |  |  |  |  | 15.82 | 14.87 | [6 empty] | 10.4 | 21.26 | 8.49
2010-01-24 | 6.85 | 6.94 |  |  |  |  | 7.25 | 1.6 |  |  |  |  | 49.5 |  |  |  | 0 | 0.3705 |  |  | 0.2165 | 0.153 | [5 empty] | 28.85 |  |  |  |  | 57.85 |  | 23.25 |  | 10.6 | 0.0895 |  | 3.35 | 85.07 | 1.12 |  |  |  |  | 15.388 | 14.422 | [6 empty] | 10.4 | 21.26 | 8.49
2010-01-25 | 6.86 | 6.87 |  |  |  |  | 7.11 | 1.67 |  |  |  |  | 54 |  |  |  | 0 | 0.378 |  |  | 0.292 | 0.51 | [5 empty] | 29.2 |  |  |  |  | 58.3 |  | 17.7 |  | 8.7 | 0.133 |  | 3.3 | 105.11 | 1.62 |  |  |  |  | 16.361 | 14.501 | [6 empty] | 10.4 | 21.26 | 8.49
2010-01-26 | 6.87 | 6.7 |  |  |  |  | 7.78 | 1.56 |  |  |  |  | 54 |  |  |  | 0 | 0.377 |  |  | 0.193 | 0.164 | [5 empty] | 30 |  |  |  |  | 60.1 |  | 18.6 |  | 8.9 | 0.114 |  | 3.5 | 94.57 | 1.26 |  |  |  |  | 16.187 | 15.247 | [6 empty] | 10.4 | 21.26 | 9.02
2010-01-27 | 6.92 | 6.77 |  |  |  |  | 7.86 | 1.49 |  |  |  |  | 57 |  |  |  | 0 | 0.386 |  |  | 0.249 | 0.233 | [5 empty] | 34.5 |  |  |  |  | 69 |  | 18 |  | 7.4 | 0.134 |  | 3.5 | 89.96 | 1.25 |  |  |  |  | 15.863 | 14.9 | [6 empty] | 10.4 | 21.26 | 9.02
2010-01-28 | 7.13 | 6.67 |  |  |  |  | 7.38 | 1.49 |  |  |  |  | 43 |  |  |  | 0 | 0.377 |  |  | 0.395 | 0.248 | [5 empty] | 30.1 |  |  |  |  | 60.1 |  | 19.1 |  | 8.6 | 0.142 |  | 3.5 | 90.38 | 1.27 |  |  |  |  | 15.814 | 14.877 | [6 empty] | 10.4 | 21.26 | 9.54
2010-01-29 | 6.61 | 7.04 |  |  |  |  | 6.84 | 1.67 |  |  |  |  | 42 |  |  |  | 0 | 0.376 |  |  | 0.158 | 0.261 | [5 empty] | 30.6 |  |  |  |  | 61.3 |  | 24.5 |  | 10.4 | 0.207 |  | 3.4 | 94.86 | 1.2 |  |  |  |  | 15.946 | 14.99 | [6 empty] | 11.51 | 15.94 | 9.54
2010-01-30 | 6.69 | 6.6 |  |  |  |  | 7.77 | 1.65 |  |  |  |  | 41 |  |  |  | 0 | 0.364 |  |  | 0.21 | 0.294 | [5 empty] | 29.4 |  |  |  |  | 58.9 |  | 21 |  | 8.6 | 0.199 |  | 3.5 | 90.45 | 1.17 |  |  |  |  | 15.47 | 14.56 | [6 empty] | 11.51 | 15.94 | 9.54
2010-01-31 | 6.65 | 6.82 |  |  |  |  | 7.305 | 1.66 |  |  |  |  | 41.5 |  |  |  | 0 | 0.37 |  |  | 0.184 | 0.2775 | [5 empty] | 30 |  |  |  |  | 60.1 |  | 22.75 |  | 9.5 | 0.203 |  | 3.45 | 92.655 | 1.185 |  |  |  |  | 15.708 | 14.775 | [6 empty] | 11.51 | 15.94 | 9.54
2010-02-01 | 6.52 | 6.49 |  |  |  |  | 7.98 | 1.58 |  |  |  |  | 42 |  |  |  | 0 | 0.352 |  |  | 0.222 | 0.407 | [5 empty] | 32.3 |  |  |  |  | 64.7 |  | 23.4 |  | 10.6 | 0.25 |  | 3.7 | 95.39 | 1.39 |  |  |  |  | 16.457 | 14.573 | [6 empty] | 10.72 | 15.94 | 10.78
2010-02-02 | 6.48 | 6.49 |  |  |  |  | 7.06 | 1.63 |  |  |  |  | 48 |  |  |  | 0 | 0.352 |  |  | 0.111 | 0.377 | [5 empty] | 26.5 |  |  |  |  | 53 |  | 21.2 |  | 10.4 | 0.153 |  | 3.5 | 90.58 | 1.13 |  |  |  |  | 15.876 | 14.898 | [6 empty] | 10.08 | 15.94 | 9.9
2010-02-03 | 7.43 | 6.42 |  |  |  |  | 8.31 | 1.59 |  |  |  |  | 33 |  |  |  | 0 | 0.354 |  |  | 0.247 | 0.144 | [5 empty] | 27.6 |  |  |  |  | 55.1 |  | 20.6 |  | 9.8 | 0.142 |  | 3.8 | 89.96 | 1.12 |  |  |  |  | 16.026 | 15.083 | [6 empty] | 10.08 | 15.94 | 9.37
2010-02-04 | 6.75 | 7.19 |  |  |  |  | 7.89 | 1.27 |  |  |  |  | 15 |  |  |  | 0 | 0.353 |  |  | 0.251 | 0.498 | [5 empty] | 29.8 |  |  |  |  | 59.6 |  | 20.8 |  | 10 | 0.038 |  | 4 | 107.12 | 2 |  |  |  |  | 15.857 | 14.885 | [6 empty] | 10.08 | 15.94 | 8.13
2010-02-05 | 6.17 | 6.3 |  |  |  |  | 6.82 | 1.3 |  |  |  |  | 16 |  |  |  | 0 | 0.371 |  |  | 0.161 | 0.423 | [5 empty] | 29.1 |  |  |  |  | 58.2 |  | 21.1 |  | 9.9 | 0.041 |  | 5.6 | 80.62 | 1.15 |  |  |  |  | 15.89 | 14.931 | [6 empty] | 10.08 | 15.94 | 8.13
2010-02-06 | 6.96 | 6.14 |  |  |  |  | 7.04 | 1.24 |  |  |  |  | 42 |  |  |  | 0 | 0.387 |  |  | 0.179 | 0.515 | [5 empty] | 30.5 |  |  |  |  | 61 |  | 20.1 |  | 10.1 | 0.046 |  | 3.6 | 75.28 | 1.08 |  |  |  |  | 15.69 | 14.74 | [6 empty] | 10.08 | 15.94 | 8.13
2010-02-07 | 6.565 | 6.22 |  |  |  |  | 6.93 | 1.33 |  |  |  |  | 29 |  |  |  | 0 | 0.379 |  |  | 0.17 | 0.469 | [5 empty] | 29.8 |  |  |  |  | 59.6 |  | 20.6 |  | 10 | 0.0435 |  | 4.6 | 69.44 | 0.93 |  |  |  |  | 14.956 | 13.957 | [6 empty] | 10.08 | 15.94 | 13.02
2010-02-08 | 6.19 | 6.48 |  |  |  |  | 5.08 | 1.23 |  |  |  |  | 30 |  |  |  | 0 | 0.395 |  |  | 0.319 | 0.219 | [5 empty] | 29.2 |  |  |  |  | 59.3 |  | 20 |  | 8.2 | 0.069 |  | 3.8 | 75.96 | 1.24 |  |  |  |  | 15.871 | 13.959 | [6 empty] | 10.08 | 15.94 | 13.02
2010-02-09 | 6.4 | 5.49 |  |  |  |  | 7.35 | 1.13 |  |  |  |  | 30 |  |  |  | 0 | 0.415 |  |  | 0.126 | 0.379 | [5 empty] | 30.5 |  |  |  |  | 61 |  | 21.6 |  | 8.9 | 0.087 |  | 3.7 | 69.57 | 1.11 |  |  |  |  | 15.054 | 14.111 | [6 empty] | 10.72 | 15.94 | 11.11
2010-02-10 | 6.69 | 6.31 |  |  |  |  | 7.18 | 1.31 |  |  |  |  | 49 |  |  |  | 0 | 0.378 |  |  | 0.157 | 0.527 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 23.7 |  | 11.8 | 0.06 |  | 3.6 | 80.19 | 1.15 |  |  |  |  | 15.795 | 14.804 | [6 empty] | 9.92 | 15.94 | 11.11
2010-02-11 | 6.71 | 6.49 |  |  |  |  | 7.51 | 1.14 |  |  |  |  | 46 |  |  |  | 0 | 0.386 |  |  | 0.137 | 0.289 | [5 empty] | 31 |  |  |  |  | 62 |  | 23.8 |  | 10.7 | 0.059 |  | 3.5 | 91.46 | 1.69 |  |  |  |  | 15.641 | 14.682 | [6 empty] | 9.92 | 15.94 | 11.83
2010-02-12 | 6.76 | 6.71 |  |  |  |  | 7.31 | 1.23 |  |  |  |  | 44 |  |  |  | 0 | 0.377 |  |  | 0.195 | 0.492 | [5 empty] | 30.9 |  |  |  |  | 61.7 |  | 24 |  | 10.9 | 0.128 |  | 3.8 | 69.96 | 0.91 |  |  |  |  | 15.855 | 14.835 | [6 empty] | 9.92 | 15.94 | 11.83
2010-02-13 | 6.16 | 6.18 |  |  |  |  | 6.68 | 1.25 |  |  |  |  | 42 |  |  |  | 0 | 0.372 |  |  | 0.188 | 0.343 | [5 empty] | 22.3 |  |  |  |  | 44.7 |  | 23.3 |  | 11.2 | 0.167 |  | 3.9 | 74.82 | 0.97 |  |  |  |  | 16.23 | 15.28 | [6 empty] | 9.92 | 15.94 | 11.11
2010-02-14 | 6.46 | 6.445 |  |  |  |  | 6.995 | 1.2 |  |  |  |  | 43 |  |  |  | 0 | 0.3745 |  |  | 0.1915 | 0.4175 | [5 empty] | 26.6 |  |  |  |  | 53.2 |  | 23.65 |  | 11.05 | 0.1475 |  | 3.85 | 72.39 | 0.94 |  |  |  |  | 15.039 | 14.042 | [6 empty] | 9.92 | 15.94 | 11.11
2010-02-15 | 6.15 | 6 |  |  |  |  | 7.12 | 1.23 |  |  |  |  | 73 |  |  |  | 0 | 0.346 |  |  | 0.215 | 0.65 | [5 empty] | 30.3 |  |  |  |  | 60.6 |  | 23.7 |  | 11.9 | 0.046 |  | 3.4 | 85.14 | 1.35 |  |  |  |  | 16.859 | 14.96 | [6 empty] | 9.92 | 15.94 | 11.11
2010-02-16 | 6.48 | 6 |  |  |  |  | 7.52 | 1.04 |  |  |  |  | 41 |  |  |  | 0 | 0.338 |  |  | 0.153 | 0.193 | [5 empty] | 29.1 |  |  |  |  | 58.2 |  | 23.4 |  | 12.3 | 0.064 |  | 3.7 | 65.03 | 1.09 |  |  |  |  | 14.919 | 13.875 | [6 empty] | 9.92 | 15.94 | 11.83
2010-02-17 | 6.55 | 6.62 |  |  |  |  | 7.24 | 1.28 |  |  |  |  | 43 |  |  |  | 0 | 0.326 |  |  | 0.094 | 0.503 | [5 empty] | 28.6 |  |  |  |  | 57.3 |  | 18.4 |  | 12.1 | 0.068 |  | 3.3 | 85.09 | 1.12 |  |  |  |  | 17.039 | 16.069 | [6 empty] | 9.92 | 15.94 | 11.83
2010-02-18 | 6.54 | 6.73 |  |  |  |  | 6.87 | 1.19 |  |  |  |  | 30 |  |  |  | 0 | 0.327 |  |  | 0.206 | 0.483 | [5 empty] | 30.7 |  |  |  |  | 61.2 |  | 20.4 |  | 11.8 | 0.084 |  | 4.2 | 69.5 | 0.87 |  |  |  |  | 16.384 | 15.33 | [6 empty] | 9.92 | 15.94 | 11.83
2010-02-19 | 6.49 | 6.41 |  |  |  |  | 6.55 | 1.12 |  |  |  |  | 34 |  |  |  | 0 | 0.334 |  |  | 0.193 | 0.344 | [5 empty] | 26.8 |  |  |  |  | 53.7 |  | 20 |  | 10.4 | 0.103 |  | 4.5 | 75.65 | 1.13 |  |  |  |  | 16.343 | 15.278 | [6 empty] | 9.92 | 15.94 | 11.83
2010-02-20 | 6.75 | 6.27 |  |  |  |  | 7.36 | 1.27 |  |  |  |  | 31 |  |  |  | 0 | 0.347 |  |  | 0.132 | 0.295 | [5 empty] | 29.2 |  |  |  |  | 58.3 |  | 19.9 |  | 10.4 | 0.084 |  | 4.2 | 79.51 | 1.16 |  |  |  |  | 15.93 | 14.87 | [6 empty] | 9.92 | 15.94 | 10.63
2010-02-21 | 6.62 | 6.34 |  |  |  |  | 6.955 | 1.195 |  |  |  |  | 32.5 |  |  |  | 0 | 0.3405 |  |  | 0.1625 | 0.3195 | [5 empty] | 28 |  |  |  |  | 56 |  | 19.95 |  | 10.4 | 0.0935 |  | 4.35 | 77.58 | 1.145 |  |  |  |  | 16.1365 | 15.074 | [6 empty] | 9.92 | 15.94 | 11.23
2010-02-22 | 6.39 | 6.46 |  |  |  |  | 7.2 | 1.21 |  |  |  |  | 40 |  |  |  | 0 | 0.33 |  |  | 0.237 | 0.701 | [5 empty] | 29.4 |  |  |  |  | 58.8 |  | 25.9 |  | 10.9 | 0.158 |  | 4.4 | 80.19 | 1.24 |  |  |  |  | 16.744 | 14.854 | [6 empty] | 9.92 | 15.94 | 10.63
2010-02-23 | 6.64 | 6.51 |  |  |  |  | 6.68 | 1.22 |  |  |  |  | 41 |  |  |  | 0 | 0.328 |  |  | 0.095 | 0.432 | [5 empty] | 30 |  |  |  |  | 60 |  | 24.1 |  | 11.2 | 0.097 |  | 4.1 | 74.79 | 1.04 |  |  |  |  | 15.991 | 15.044 | [6 empty] | 9.92 | 15.94 | 10.63
2010-02-24 | 6.515 | 6.485 |  |  |  |  | 6.94 | 1.215 |  |  |  |  | 40.5 |  |  |  | 0 | 0.329 |  |  | 0.166 | 0.5665 | [5 empty] | 29.7 |  |  |  |  | 59.4 |  | 25 |  | 11.05 | 0.1275 |  | 4.25 | 77.49 | 1.14 |  |  |  |  | 16.3675 | 14.949 | [6 empty] | 9.92 | 15.94 | 10.63
2010-02-25 | 7.2 | 6.81 |  |  |  |  | 7.29 | 1.35 |  |  |  |  | 41 |  |  |  | 0 | 0.326 |  |  | 0.135 | 0.415 | [5 empty] | 30 |  |  |  |  | 60.1 |  | 25.1 |  | 11.1 | 0.053 |  | 4.6 | 79.27 | 0.95 |  |  |  |  | 16.486 | 15.622 | [6 empty] | 9.92 | 15.94 | 10.63
2010-02-26 | 6.56 | 6.88 |  |  |  |  | 7.84 | 1.12 |  |  |  |  | 31 |  |  |  | 0 | 0.324 |  |  | 0.185 | 0.31 | [5 empty] | 29.1 |  |  |  |  | 58.2 |  | 24.1 |  | 11 | 0.058 |  | 4.5 | 75.37 | 1.18 |  |  |  |  | 15.886 | 14.863 | [6 empty] | 9.92 | 15.94 | 10.63
2010-02-27 | 6.33 | 6.84 |  |  |  |  | 7.68 | 1.25 |  |  |  |  | 46 |  |  |  | 0 | 0.331 |  |  | 0.16 | 0.504 | [5 empty] | 22.5 |  |  |  |  | 55 |  | 21.2 |  | 11.2 | 0.022 |  | 4 | 69.92 | 0.88 |  |  |  |  | 15.9 | 14.87 | [6 empty] | 9.92 | 15.94 | 10.63
2010-02-28 | 6.445 | 6.86 |  |  |  |  | 7.76 | 1.185 |  |  |  |  | 38.5 |  |  |  | 0 | 0.3275 |  |  | 0.1725 | 0.407 | [5 empty] | 25.8 |  |  |  |  | 56.6 |  | 22.65 |  | 11.1 | 0.04 |  | 4.25 | 72.645 | 1.03 |  |  |  |  | 15.511 | 14.484 | [6 empty] | 9.92 | 15.94 | 10.63
2010-03-01 | 6.44 | 6.95 |  |  |  |  | 7.43 | 1.25 |  |  |  |  | 44 |  |  |  | 1 | 0.325 |  |  | 0.333 | 0.617 | [5 empty] | 30.4 |  |  |  |  | 60.9 |  | 20.9 |  | 10.6 | 0.064 |  | 3.7 | 80.17 | 1.22 |  |  |  |  | 16.652 | 14.739 | [6 empty] | 9.92 | 15.94 | 9.91
2010-03-02 | 6.43 | 6.68 |  |  |  |  | 7.58 | 1.29 |  |  |  |  | 41 |  |  |  | 0 | 0.336 |  |  | 0.135 | 0.44 | [5 empty] | 29.6 |  |  |  |  | 59.3 |  | 19.9 |  | 10.2 | 0.029 |  | 3.6 | 74.84 | 0.97 |  |  |  |  | 16.049 | 15.032 | [6 empty] | 9.92 | 15.94 | 9.91
2010-03-03 | 6.03 | 6.38 |  |  |  |  | 7.56 | 1.22 |  |  |  |  | 43 |  |  |  | 0 | 0.334 |  |  | 0.145 | 0.43 | [5 empty] | 27.3 |  |  |  |  | 54.6 |  | 21.8 |  | 11.1 | 0.044 |  | 3.6 | 71 | 0.9 |  |  |  |  | 17.295 | 15.194 | [6 empty] | 9.92 | 15.94 | 9.91
2010-03-04 | 7.42 | 6.08 |  |  |  |  | 7.33 | 1.22 |  |  |  |  | 37 |  |  |  | 0 | 0.323 |  |  | 0.152 | 0.292 | [5 empty] | 28.3 |  |  |  |  | 56.6 |  | 18.4 |  | 10.2 | 0.019 |  | 3.9 | 78.76 | 1.19 |  |  |  |  | 18.22 | 14.82 | [6 empty] | 9.92 | 15.94 | 11.83
2010-03-05 | 6.47 | 6.61 |  |  |  |  | 6.28 | 1.21 |  |  |  |  | 0 |  |  |  | 0 | 0.31 |  |  | 0.147 | 0.274 | [5 empty] | 31 |  |  |  |  | 61.1 |  | 19.9 |  | 12.3 | 0.034 |  | 3.9 | 64.96 | 0.79 |  |  |  |  | 16.909 | 14.744 | [6 empty] | 9.92 | 15.94 | 10.63
2010-03-06 | 6.32 | 6.57 |  |  |  |  | 7.02 | 1.189 |  |  |  |  | 31 |  |  |  | 0 | 0.323 |  |  | 0.156 | 0.266 | [5 empty] | 31.1 |  |  |  |  | 62 |  | 22.9 |  | 11.6 | 0.048 |  | 3.8 | 64.96 | 0.92 |  |  |  |  | 17.14 | 14.95 | [6 empty] | 9.92 | 15.94 | 10.63
2010-03-07 | 6.395 | 6.59 |  |  |  |  | 6.65 | 1.1995 |  |  |  |  | 15.5 |  |  |  | 0 | 0.3165 |  |  | 0.1515 | 0.27 | [5 empty] | 31.05 |  |  |  |  | 61.55 |  | 21.4 |  | 11.95 | 0.041 |  | 3.85 | 64.96 | 0.855 |  |  |  |  | 17.158 | 14.044 | [6 empty] | 9.92 | 15.94 | 10.63
2010-03-08 | 6.35 | 6.67 |  |  |  |  | 7.93 | 1.3 |  |  |  |  | 42 |  |  |  | 0 | 0.306 |  |  | 0.198 | 0.233 | [5 empty] | 30.7 |  |  |  |  | 61.4 |  | 22.2 |  | 11.9 | 0.065 |  | 3.5 | 75.23 | 1.1 |  |  |  |  | 18.285 | 14.242 | [6 empty] | 9.92 | 15.94 | 10.63
2010-03-09 | 7.5 | 6.18 |  |  |  |  | 7.36 | 1.25 |  |  |  |  | 54 |  |  |  | 0 | 0.308 |  |  | 0.133 | 0.3 | [5 empty] | 30 |  |  |  |  | 60 |  | 23.1 |  | 10.4 | 0.057 |  | 3.5 | 80.66 | 1.24 |  |  |  |  | 17.811 | 14.723 | [6 empty] | 9.92 | 12.76 | 10.63
2010-03-10 | 6.47 | 6.58 |  |  |  |  | 7.58 | 1.2 |  |  |  |  | 36 |  |  |  | 0 | 0.315 |  |  | 0.145 | 0.231 | [5 empty] | 30.1 |  |  |  |  | 60.2 |  | 23.4 |  | 11.8 | 0.061 |  | 3.6 | 70.34 | 1.01 |  |  |  |  | 17.568 | 14.454 | [6 empty] | 9.92 | 12.76 | 11.11
2010-03-11 | 6.45 | 6.46 |  |  |  |  | 7.07 | 1.23 |  |  |  |  | 31 |  |  |  | 0 | 0.302 |  |  | 0.147 | 0.354 | [5 empty] | 29.8 |  |  |  |  | 59.6 |  | 28.6 |  | 11.2 | 0.067 |  | 3.4 | 84.52 | 1.14 |  |  |  |  | 19.216 | 16.197 | [6 empty] | 9.92 | 12.76 | 11.11
2010-03-12 | 6.54 | 6.03 |  |  |  |  | 6.89 | 1.25 |  |  |  |  | 28 |  |  |  | 0 | 0.292 |  |  | 0.199 | 0.223 | [5 empty] | 28.6 |  |  |  |  | 57.2 |  | 27 |  | 11.3 | 0.074 |  | 3.2 | 74.33 | 0.99 |  |  |  |  | 18.183 | 15.05 | [6 empty] | 9.92 | 12.76 | 13.02
2010-03-13 | 6.26 | 5.87 |  |  |  |  | 6.72 | 1.32 |  |  |  |  | 35 |  |  |  | 0 | 0.294 |  |  | 0.123 | 0.373 | [5 empty] | 26.3 |  |  |  |  | 52.6 |  | 28.9 |  | 10.1 | 0.09 |  | 3 | 80.68 | 1.15 |  |  |  |  | 17.94 | 14.85 | [6 empty] | 9.92 | 12.76 | 13.02
2010-03-14 | 6.4 | 5.95 |  |  |  |  | 6.805 | 1.285 |  |  |  |  | 31.5 |  |  |  | 0 | 0.293 |  |  | 0.161 | 0.298 | [5 empty] | 27.45 |  |  |  |  | 54.9 |  | 27.95 |  | 10.7 | 0.082 |  | 3.1 | 77.505 | 1.07 |  |  |  |  | 18.0615 | 14.95 | [6 empty] | 9.92 | 12.76 | 13.02
2010-03-15 | 6.33 | 5.9 |  |  |  |  | 6.27 | 1.15 |  |  |  |  | 30 |  |  |  | 0 | 0.302 |  |  | 0.788 | 0.589 | [5 empty] | 25.6 |  |  |  |  | 51.3 |  | 15 |  | 6.2 | 0.114 |  | 3.8 | 69.68 | 0.99 |  |  |  |  | 18.791 | 14.791 | [6 empty] | 9.13 | 12.76 | 14.22
2010-03-16 | 6.33 | 5.84 |  |  |  |  | 6.91 | 0.96 |  |  |  |  | 33 |  |  |  | 0 | 0.304 |  |  | 0.264 | 0.402 | [5 empty] | 31.8 |  |  |  |  | 63.6 |  | 17.9 |  | 11.8 | 0.127 |  | 3.8 | 60.19 | 0.95 |  |  |  |  | 18.243 | 14.317 | [6 empty] | 9.13 | 12.76 | 11.83
2010-03-17 | 7.01 | 6.3 |  |  |  |  | 7.22 | 1.24 |  |  |  |  | 33 |  |  |  | 0 | 0.325 |  |  | 0.194 | 0.244 | [5 empty] | 32.4 |  |  |  |  | 64.9 |  | 18.4 |  | 10.4 | 0.109 |  | 3.7 | 86.35 | 1.44 |  |  |  |  | 16.402 | 14.635 | [6 empty] | 9.13 | 12.76 | 14.22
2010-03-18 | 6.4 | 7 |  |  |  |  | 7.36 | 1.11 |  |  |  |  | 9 |  |  |  | 0 | 0.297 |  |  | 0.205 | 0.176 | [5 empty] | 31.4 |  |  |  |  | 62.8 |  | 25.9 |  | 14.8 | 0.13 |  | 3.7 | 75.3 | 1.03 |  |  |  |  | 16.97 | 15.944 | [6 empty] | 9.13 | 12.76 | 14.22
2010-03-19 | 6.45 | 6.35 |  |  |  |  | 6.96 | 1.14 |  |  |  |  | 35 |  |  |  | 0 | 0.299 |  |  | 0.116 | 0.169 | [5 empty] | 31.8 |  |  |  |  | 63.6 |  | 25.3 |  | 11.8 | 0.095 |  | 3.7 | 70.4 | 0.98 |  |  |  |  | 16.03 | 15.057 | [6 empty] | 9.13 | 17.86 | 14.22
2010-03-20 | 6.29 | 6.52 |  |  |  |  | 7.75 | 1.17 |  |  |  |  | 37 |  |  |  | 0 | 0.306 |  |  | 0.094 | 0.146 | [5 empty] | 32.7 |  |  |  |  | 65.4 |  | 24.5 |  | 11.6 | 0.083 |  | 4 | 70.45 | 0.99 |  |  |  |  | 15.86 | 14.79 | [6 empty] | 9.13 | 17.86 | 14.22
2010-03-21 | 6.37 | 6.435 |  |  |  |  | 7.355 | 1.155 |  |  |  |  | 36 |  |  |  | 0 | 0.3025 |  |  | 0.105 | 0.1575 | [5 empty] | 32.25 |  |  |  |  | 64.5 |  | 24.9 |  | 11.7 | 0.089 |  | 3.85 | 69.92 | 1.09 |  |  |  |  | 15.701 | 14.686 | [6 empty] | 9.13 | 17.86 | 14.22
2010-03-22 | 6.44 | 6.55 |  |  |  |  | 7.04 | 1.25 |  |  |  |  | 39 |  |  |  | 1 | 0.311 |  |  | 0.24 | 0.26 | [5 empty] | 31.2 |  |  |  |  | 62.5 |  | 25.5 |  | 13.4 | 0.101 |  | 3.8 | 84.67 | 1.32 |  |  |  |  | 16.89 | 14.96 | [6 empty] | 9.13 | 17.86 | 13.02
2010-03-23 | 7.52 | 6.48 |  |  |  |  | 6.74 | 1.11 |  |  |  |  | 43 |  |  |  | 0 | 0.303 |  |  | 0.085 | 0.176 | [5 empty] | 31.6 |  |  |  |  | 63.2 |  | 23.3 |  | 14.8 | 0.074 |  | 3.7 | 69.63 | 0.99 |  |  |  |  | 16.007 | 15.026 | [6 empty] | 9.13 | 17.86 | 13.02
2010-03-24 | 6.98 | 6.515 |  |  |  |  | 6.89 | 1.16 |  |  |  |  | 41 |  |  |  | 0.5 | 0.307 |  |  | 0.1625 | 0.218 | [5 empty] | 31.4 |  |  |  |  | 62.85 |  | 24.4 |  | 14.1 | 0.0875 |  | 3.75 | 73.89 | 1.08 |  |  |  |  | 16.003 | 14.958 | [6 empty] | 9.13 | 17.86 | 11.83
2010-03-25 | 7.25 | 6.4975 |  |  |  |  | 6.815 | 1.2 |  |  |  |  | 42 |  |  |  | 0.25 | 0.305 |  |  | 0.12375 | 0.197 | [5 empty] | 31.5 |  |  |  |  | 63.025 |  | 23.85 |  | 14.45 | 0.08075 |  | 3.725 | 69.57 | 0.9 |  |  |  |  | 15.991 | 15.017 | [6 empty] | 9.13 | 17.86 | 11.83
2010-03-26 | 6.33 | 6.52 |  |  |  |  | 6.69 | 1.22 |  |  |  |  | 36 |  |  |  | 0 | 0.303 |  |  | 0.103 | 0.26 | [5 empty] | 26.9 |  |  |  |  | 53.8 |  | 23.9 |  | 12.8 | 0.098 |  | 4 | 70.63 | 0.95 |  |  |  |  | 15.769 | 14.756 | [6 empty] | 9.13 | 17.86 | 11.83
2010-03-27 | 6.33 | 6.59 |  |  |  |  | 6.96 | 1.25 |  |  |  |  | 37 |  |  |  | 0 | 0.299 |  |  | 0.067 | 0.441 | [5 empty] | 32.3 |  |  |  |  | 64.6 |  | 22.1 |  | 12.6 | 0.094 |  | 4.3 | 68.91 | 0.83 |  |  |  |  | 16.02 | 15.02 | [6 empty] | 9.13 | 17.86 | 12.54
2010-03-28 | 6.33 | 6.555 |  |  |  |  | 6.825 | 1.2 |  |  |  |  | 36.5 |  |  |  | 0 | 0.301 |  |  | 0.085 | 0.3505 | [5 empty] | 29.6 |  |  |  |  | 59.2 |  | 23 |  | 12.7 | 0.096 |  | 4.15 | 70.34 | 0.99 |  |  |  |  | 15.647 | 14.61 | [6 empty] | 9.13 | 17.86 | 12.54
2010-03-29 | 6.38 | 6.63 |  |  |  |  | 6.75 | 1.34 |  |  |  |  | 32 |  |  |  | 0 | 0.298 |  |  | 0.272 | 0.302 | [5 empty] | 30.1 |  |  |  |  | 60.2 |  | 22.8 |  | 11.7 | 0.08 |  | 4.3 | 80.17 | 1.14 |  |  |  |  | 16.676 | 14.699 | [6 empty] | 9.13 | 17.54 | 13.02
2010-03-30 | 6.38 | 6.58 |  |  |  |  | 6.86 | 1.21 |  |  |  |  | 35 |  |  |  | 0 | 0.303 |  |  | 0.072 | 0.187 | [5 empty] | 33.2 |  |  |  |  | 66.4 |  | 20.4 |  | 10.9 | 0.057 |  | 4 | 65.51 | 0.92 |  |  |  |  | 15.014 | 13.951 | [6 empty] | 9.13 | 17.54 | 13.02
2010-03-31 | 6.46 | 6.52 |  |  |  |  | 7.21 | 1.28 |  |  |  |  | 31 |  |  |  | 0 | 0.303 |  |  | 0.068 | 0.131 | [5 empty] | 34.1 |  |  |  |  | 68.2 |  | 21.3 |  | 15.7 | 0.099 |  | 4.3 | 76.8 | 0.98 |  |  |  |  | 16.415 | 15.412 | [6 empty] | 9.13 | 17.54 | 14.22
2010-04-01 | 6.47 | 6.33 |  |  |  |  | 7.31 | 1.19 |  |  |  |  | 34 |  |  |  | 0 | 0.295 |  |  | 0.095 | 0.153 | [5 empty] | 33.6 |  |  |  |  | 67.4 |  | 25.8 |  | 15.1 | 0.116 |  | 4.1 | 69.92 | 0.97 |  |  |  |  | 15.718 | 14.684 | [6 empty] | 9.13 | 17.54 | 14.22
2010-04-02 | 6.51 | 6.44 |  |  |  |  | 7.37 | 1.23 |  |  |  |  | 43 |  |  |  | 0 | 0.299 |  |  | 0.088 | 0.142 | [5 empty] | 35.3 |  |  |  |  | 70.6 |  | 23.7 |  | 14.9 | 0.101 |  | 4.8 | 75.3 | 1.07 |  |  |  |  | 15.903 | 14.883 | [6 empty] | 9.13 | 17.54 | 14.22
2010-04-03 | 6.62 | 6.46 |  |  |  |  | 6.47 | 1.41 |  |  |  |  | 34 |  |  |  | 0 | 0.309 |  |  | 0.113 | 0.32 | [5 empty] | 33.6 |  |  |  |  | 67.1 |  | 22.7 |  | 12.6 | 0.101 |  | 4.5 | 80.48 | 1.03 |  |  |  |  | 16.01 | 14.96 | [6 empty] | 9.13 | 17.54 | 15.42
2010-04-04 | 6.565 | 6.45 |  |  |  |  | 6.92 | 1.32 |  |  |  |  | 38.5 |  |  |  | 0 | 0.304 |  |  | 0.1005 | 0.231 | [5 empty] | 34.45 |  |  |  |  | 68.85 |  | 23.2 |  | 13.75 | 0.101 |  | 4.65 | 77.89 | 1.05 |  |  |  |  | 15.9565 | 14.9215 | [6 empty] | 9.13 | 17.54 | 14.82
2010-04-05 | 6.47 | 6.35 |  |  |  |  | 6.6 | 1.15 |  |  |  |  | 41 |  |  |  | 0 | 0.366 |  |  | 0.155 | 0.248 | [5 empty] | 35.1 |  |  |  |  | 70.2 |  | 37.7 |  | 14.8 | 0.093 |  | 4.4 | 84.58 | 1.52 |  |  |  |  | 16.306 | 14.379 | [6 empty] | 9.13 | 17.54 | 15.42
2010-04-06 | 6.45 | 6.48 |  |  |  |  | 8.77 | 1.15 |  |  |  |  | 38 |  |  |  | 0 | 0.306 |  |  | 0.086 | 0.198 | [5 empty] | 30.1 |  |  |  |  | 60.2 |  | 26.2 |  | 14.3 | 0.145 |  | 4.2 | 80.68 | 1.34 |  |  |  |  | 15.616 | 14.683 | [6 empty] | 9.13 | 17.54 | 15.42
2010-04-07 | 6.45 | 5.45 |  |  |  |  | 7.53 | 1.21 |  |  |  |  | 45 |  |  |  | 0 | 0.313 |  |  | 0.139 | 0.758 | [5 empty] | 30.2 |  |  |  |  | 60.5 |  | 25.8 |  | 13.9 | 0.168 |  | 5.1 | 80.66 | 1.25 |  |  |  |  | 15.865 | 14.88 | [6 empty] | 9.13 | 17.54 | 15.42
2010-04-08 | 6.34 | 5.21 |  |  |  |  | 7.37 | 1.29 |  |  |  |  | 42 |  |  |  | 0 | 0.303 |  |  | 0.089 | 0.214 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 26.8 |  | 11.8 | 0.067 |  | 5.2 | 80.19 | 1.18 |  |  |  |  | 15.858 | 14.712 | [6 empty] | 9.13 | 17.54 | 11.83
2010-04-09 | 6.36 | 5.24 |  |  |  |  | 7.34 | 1.23 |  |  |  |  | 41 |  |  |  | 0 | 0.301 |  |  | 0.51 | 0.29 | [5 empty] | 29.6 |  |  |  |  | 59.2 |  | 26.4 |  | 9.8 | 0.053 |  | 5 | 79.69 | 1.2 |  |  |  |  | 15.821 | 14.863 | [6 empty] | 9.13 | 17.54 | 11.83
2010-04-10 | 6.33 | 6.39 |  |  |  |  | 7.44 | 1.27 |  |  |  |  | 42 |  |  |  | 0 | 0.31 |  |  | 0.108 | 0.185 | [5 empty] | 30 |  |  |  |  | 60 |  | 24.2 |  | 10.1 | 0.061 |  | 5.1 | 80.2 | 1.18 |  |  |  |  | 15.74 | 14.85 | [6 empty] | 9.13 | 17.54 | 11.83
2010-04-11 | 6.345 | 5.815 |  |  |  |  | 7.39 | 1.32 |  |  |  |  | 41.5 |  |  |  | 0 | 0.3055 |  |  | 0.309 | 0.2375 | [5 empty] | 29.8 |  |  |  |  | 59.6 |  | 25.3 |  | 9.95 | 0.057 |  | 5.05 | 75.28 | 1.19 |  |  |  |  | 14.506 | 13.638 | [6 empty] | 10.72 | 17.54 | 11.83
2010-04-12 | 6.49 | 6.4 |  |  |  |  | 7.72 | 1.55 |  |  |  |  | 42 |  |  |  | 0 | 0.289 |  |  | 0.415 | 0.249 | [5 empty] | 27.5 |  |  |  |  | 55 |  | 22.1 |  | 10.7 | 0.098 |  | 5.2 | 89.96 | 1.23 |  |  |  |  | 16.408 | 14.694 | [6 empty] | 10.72 | 17.54 | 11.83
2010-04-13 | 6.49 | 6.51 |  |  |  |  | 7.11 | 1.48 |  |  |  |  | 38 |  |  |  | 0 | 0.337 |  |  | 0.098 | 0.35 | [5 empty] | 29.4 |  |  |  |  | 58.8 |  | 22.9 |  | 11.7 | 0.074 |  | 5.4 | 80.19 | 0.97 |  |  |  |  | 15.74 | 14.869 | [6 empty] | 11.51 | 17.54 | 10.67
2010-04-14 | 6.52 | 6.5 |  |  |  |  | 7.03 | 1.53 |  |  |  |  | 36 |  |  |  | 0 | 0.33 |  |  | 0.074 | 0.367 | [5 empty] | 27.3 |  |  |  |  | 54.6 |  | 24.1 |  | 11.3 | 0.069 |  | 4.6 | 80.66 | 0.95 |  |  |  |  | 15.558 | 14.791 | [6 empty] | 11.51 | 17.54 | 10.63
2010-04-15 | 6.47 | 6.74 |  |  |  |  | 7.26 | 1.6 |  |  |  |  | 36 |  |  |  | 0 | 0.325 |  |  | 0.097 | 0.308 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 21.9 |  | 11.6 | 0.072 |  | 4.5 | 84.65 | 1.01 |  |  |  |  | 15.559 | 14.718 | [6 empty] | 11.51 | 17.54 | 11.83
2010-04-16 | 6.42 | 6.83 |  |  |  |  | 7.54 | 1.31 |  |  |  |  | 34 |  |  |  | 0 | 0.308 |  |  | 0.085 | 0.115 | [5 empty] | 28.7 |  |  |  |  | 57.4 |  | 26 |  | 11.8 | 0.081 |  | 5 | 75.23 | 1.06 |  |  |  |  | 15.145 | 14.41 | [6 empty] | 11.51 | 17.54 | 11.83
2010-04-17 | 6.49 | 6.49 |  |  |  |  | 6.55 | 1.23 |  |  |  |  | 37 |  |  |  | 0 | 0.331 |  |  | 0.099 | 0.35 | [5 empty] | 23.55 |  |  |  |  | 47.1 |  | 25.5 |  | 5.7 | 0.15 |  | 4.65 | 70.41 | 0.92 |  |  |  |  | 15.7 | 14.88 | [6 empty] | 11.51 | 17.54 | 10.63
2010-04-18 | 6.455 | 6.66 |  |  |  |  | 7.045 | 1.15 |  |  |  |  | 35.5 |  |  |  | 0 | 0.3195 |  |  | 0.092 | 0.2325 | [5 empty] | 23.6 |  |  |  |  | 47.2 |  | 25.75 |  | 8.75 | 0.1155 |  | 4.9 | 65.4 | 1 |  |  |  |  | 14.626 | 13.834 | [6 empty] | 11.51 | 17.54 | 10.63
2010-04-19 | 6.46 | 6.53 |  |  |  |  | 6.01 | 1.3 |  |  |  |  | 44 |  |  |  | 0 | 0.335 |  |  | 0.13 | 0.554 | [5 empty] | 23.5 |  |  |  |  | 47 |  | 26.9 |  | 7.1 | 0.062 |  | 4.4 | 80.88 | 1.18 |  |  |  |  | 16.409 | 14.824 | [6 empty] | 11.51 | 17.54 | 13.02
2010-04-20 | 6.4 | 6.17 |  |  |  |  | 7.49 | 1.28 |  |  |  |  | 43 |  |  |  | 0 | 0.354 |  |  | 0.096 | 0.435 | [5 empty] | 23.7 |  |  |  |  | 47.4 |  | 25.7 |  | 9.8 | 0.068 |  | 5.4 | 75.28 | 0.89 |  |  |  |  | 16.376 | 15.725 | [6 empty] | 11.51 | 17.54 | 10.63
2010-04-21 | 6.43 | 6.65 |  |  |  |  | 7.24 | 1.23 |  |  |  |  | 31 |  |  |  | 0 | 0.295 |  |  | 0.168 | 0.339 | [5 empty] | 25.1 |  |  |  |  | 50.3 |  | 24.9 |  | 8.2 | 0.185 |  | 5.4 | 79.87 | 0.98 |  |  |  |  | 17.143 | 16.414 | [6 empty] | 11.51 | 17.54 | 9.43
2010-04-22 | 6.35 | 5.91 |  |  |  |  | 7.55 | 1.31 |  |  |  |  | 36 |  |  |  | 0 | 0.301 |  |  | 0.092 | 0.304 | [5 empty] | 25.4 |  |  |  |  | 50.8 |  | 23.2 |  | 8.9 | 0.014 |  | 5.5 | 70.34 | 0.88 |  |  |  |  | 15.291 | 14.605 | [6 empty] | 11.51 | 17.54 | 9.43
2010-04-23 | 6.41 | 5.98 |  |  |  |  | 7.59 | 1.32 |  |  |  |  | 30 |  |  |  | 0 | 0.294 |  |  | 0.088 | 0.279 | [5 empty] | 27.1 |  |  |  |  | 54.2 |  | 21.8 |  | 9.6 | 0.124 |  | 5.6 | 75.29 | 1 |  |  |  |  | 15.464 | 14.729 | [6 empty] | 11.51 | 17.54 | 8.72
2010-04-24 | 6.32 | 5.99 |  |  |  |  | 7.49 | 1.22 |  |  |  |  | 47 |  |  |  | 0 | 0.304 |  |  | 0.074 | 0.256 | [5 empty] | 23 |  |  |  |  | 46 |  | 22.2 |  | 11.7 | 0.114 |  | 7.7 | 65.03 | 0.85 |  |  |  |  | 14.51 | 14.28 | [6 empty] | 11.51 | 17.54 | 8.72
2010-04-25 | 6.365 | 5.985 |  |  |  |  | 7.54 | 1.27 |  |  |  |  | 38.5 |  |  |  | 0 | 0.299 |  |  | 0.081 | 0.2675 | [5 empty] | 25.05 |  |  |  |  | 50.1 |  | 22 |  | 10.65 | 0.119 |  | 6.65 | 70.16 | 0.925 |  |  |  |  | 14.987 | 14.5045 | [6 empty] | 11.51 | 17.54 | 8.72
2010-04-26 | 6.48 | 6.29 |  |  |  |  | 6.47 | 1.42 |  |  |  |  | 35 |  |  |  | 0 | 0.378 |  |  | 0.264 | 0.268 | [5 empty] | 17.6 |  |  |  |  | 35.3 |  | 12.4 |  | 11.175 | 0.25 |  | 7.6 | 74.79 | 0.95 |  |  |  |  | 15.908 | 14.34 | [6 empty] | 11.51 | 17.54 | 8.72
2010-04-27 | 6.45 | 6.01 |  |  |  |  | 6.36 | 1.33 |  |  |  |  | 33 |  |  |  | 0 | 0.312 |  |  | 0.06 | 0.058 | [5 empty] | 19.8 |  |  |  |  | 39.6 |  | 11.3 |  | 10.9125 | 0.25 |  | 7.4 | 69.48 | 0.82 |  |  |  |  | 15.378 | 14.691 | [6 empty] | 11.51 | 17.54 | 8.72
2010-04-28 | 7.48 | 5.99 |  |  |  |  | 7.54 | 1.39 |  |  |  |  | 41 |  |  |  | 0 | 0.424 |  |  | 0.07 | 0.305 | [5 empty] | 23.6 |  |  |  |  | 47.2 |  | 14.2 |  | 6 | 0.038 |  | 8.4 | 65.03 | 0.7 |  |  |  |  | 14.833 | 14.161 | [6 empty] | 11.51 | 17.54 | 7.52
2010-04-29 | 6.48 | 5.93 |  |  |  |  | 7.53 | 1.36 |  |  |  |  | 48 |  |  |  | 0 | 0.395 |  |  | 0.121 | 0.306 | [5 empty] | 25.2 |  |  |  |  | 50.4 |  | 20 |  | 10.4 | 0.094 |  | 8.8 | 65.03 | 0.73 |  |  |  |  | 14.792 | 14.103 | [6 empty] | 11.51 | 17.54 | 7.04
2010-04-30 | 6.48 | 5.82 |  |  |  |  | 7.64 | 1.28 |  |  |  |  | 46 |  |  |  | 0 | 0.413 |  |  | 0.098 | 0.381 | [5 empty] | 22.1 |  |  |  |  | 44.2 |  | 21.2 |  | 9.6 | 0.154 |  | 6.9 | 69.92 | 0.96 |  |  |  |  | 14.83 | 14.195 | [6 empty] | 11.51 | 17.54 | 7.04
2010-05-01 | 6.51 | 6.44 |  |  |  |  | 7.48 | 1.35 |  |  |  |  | 42 |  |  |  | 0 | 0.421 |  |  | 0.103 | 0.238 | [5 empty] | 23 |  |  |  |  | 46 |  | 22.3 |  | 7.4 | 0.098 |  | 7 | 65.09 | 0.77 |  |  |  |  | 14.63 | 13.92 | [6 empty] | 11.51 | 17.54 | 7.04
2010-05-02 | 6.495 | 6.13 |  |  |  |  | 7.56 | 1.315 |  |  |  |  | 44 |  |  |  | 0 | 0.417 |  |  | 0.1005 | 0.3095 | [5 empty] | 22.55 |  |  |  |  | 45.1 |  | 21.75 |  | 8.5 | 0.126 |  | 6.95 | 70.76 | 0.96 |  |  |  |  | 14.398 | 13.676 | [6 empty] | 11.51 | 17.54 | 7.04
2010-05-03 | 6.59 | 7.12 |  |  |  |  | 7.64 | 1.3 |  |  |  |  | 40 |  |  |  | 0 | 0.467 |  |  | 0.21 | 0.475 | [5 empty] | 24.6 |  |  |  |  | 49.1 |  | 20.9 |  | 6.9 | 0.091 |  | 7.4 | 65.03 | 0.99 |  |  |  |  | 14.476 | 12.887 | [6 empty] | 10.72 | 16.33 | 7.04
2010-05-04 | 6.62 | 7.02 |  |  |  |  | 7.4 | 1.17 |  |  |  |  | 34 |  |  |  | 0 | 0.494 |  |  | 0.054 | 0.241 | [5 empty] | 22.1 |  |  |  |  | 44.3 |  | 15.8 |  | 5.9 | 0.027 |  | 8 | 60.15 | 0.9 |  |  |  |  | 13.866 | 13.136 | [6 empty] | 10.72 | 15.31 | 6.32
2010-05-05 | 5.79 | 6.01 |  |  |  |  | 7.4 | 1.25 |  |  |  |  | 33 |  |  |  | 0 | 0.413 |  |  | 0.083 | 0.267 | [5 empty] | 21.7 |  |  |  |  | 43.4 |  | 16.6 |  | 3.3 | 0.086 |  | 6.7 | 65.03 | 0.77 |  |  |  |  | 15.261 | 14.591 | [6 empty] | 10.72 | 15.31 | 6.32
2010-05-06 | 5.63 | 5.94 |  |  |  |  | 7.34 | 1.25 |  |  |  |  | 42 |  |  |  | 0 | 0.493 |  |  | 0.125 | 0.242 | [5 empty] | 21.8 |  |  |  |  | 43.6 |  | 19.3 |  | 3.6 | 0.074 |  | 6.9 | 69.59 | 0.98 |  |  |  |  | 14.762 | 14.16 | [6 empty] | 9.92 | 15.31 | 6.32
2010-05-07 | 6.22 | 5.92 |  |  |  |  | 7.34 | 0.99 |  |  |  |  | 37 |  |  |  | 0 | 0.395 |  |  | 0.156 | 0.125 | [5 empty] | 25 |  |  |  |  | 50.1 |  | 19 |  | 6.6 | 0.25 |  | 7.2 | 65.03 | 1.13 |  |  |  |  | 14.587 | 13.936 | [6 empty] | 9.92 | 15.31 | 10.63
2010-05-08 | 6.9 | 6.18 |  |  |  |  | 7.63 | 1.15 |  |  |  |  | 38 |  |  |  | 0 | 0.387 |  |  | 0.1 | 0.085 | [5 empty] | 24.8 |  |  |  |  | 49.6 |  | 20.6 |  | 8.7 | 0.153 |  | 7.4 | 65.03 | 0.95 |  |  |  |  | 14.65 | 14.04 | [6 empty] | 9.13 | 15.31 | 10.63
2010-05-09 | 6.56 | 6.05 |  |  |  |  | 7.485 | 1.11 |  |  |  |  | 37.5 |  |  |  | 0 | 0.391 |  |  | 0.128 | 0.105 | [5 empty] | 24.9 |  |  |  |  | 49.85 |  | 19.8 |  | 7.65 | 0.2015 |  | 7.3 | 65.03 | 1.12 |  |  |  |  | 13.91 | 13.215 | [6 empty] | 9.13 | 15.31 | 10.63
2010-05-10 | 7.02 | 6.52 |  |  |  |  | 7.19 | 1.17 |  |  |  |  | 39 |  |  |  | 0 | 0.589 |  |  | 0.148 | 0.145 | [5 empty] | 23.2 |  |  |  |  | 46.4 |  | 12.2 |  | 6.8 | 0.112 |  | 8.5 | 80.18 | 1.42 |  |  |  |  | 15.631 | 14.077 | [6 empty] | 9.13 | 15.31 | 10.63
2010-05-11 | 4.71 | 6.52 |  |  |  |  | 6.78 | 1.16 |  |  |  |  | 37 |  |  |  | 0 | 0.588 |  |  | 0.104 | 0.083 | [5 empty] | 24.2 |  |  |  |  | 48.4 |  | 13.9 |  | 7 | 0.118 |  | 7.9 | 75.3 | 1.17 |  |  |  |  | 15.312 | 14.678 | [6 empty] | 9.13 | 15.31 | 10.63
2010-05-12 | 5.29 | 6.47 |  |  |  |  | 7.02 | 1.11 |  |  |  |  | 43 |  |  |  | 0 | 0.572 |  |  | 0.121 | 0.141 | [5 empty] | 25.1 |  |  |  |  | 50.2 |  | 16.2 |  | 8.3 | 0.108 |  | 8.4 | 70.34 | 1.2 |  |  |  |  | 14.461 | 13.809 | [6 empty] | 9.13 | 15.31 | 10.63
2010-05-13 | 5.56 | 6.31 |  |  |  |  | 7.16 | 1.24 |  |  |  |  | 41 |  |  |  | 0 | 0.661 |  |  | 0.112 | 0.273 | [5 empty] | 21.7 |  |  |  |  | 43.4 |  | 15.3 |  | 8.7 | 0.113 |  | 8.6 | 74.79 | 1.19 |  |  |  |  | 14.623 | 13.946 | [6 empty] | 9.13 | 15.31 | 10.63
2010-05-14 | 6.74 | 6.4 |  |  |  |  | 7.17 | 1.38 |  |  |  |  | 43 |  |  |  | 0 | 0.24 |  |  | 0.086 | 0.098 | [5 empty] | 23.8 |  |  |  |  | 47.6 |  | 16 |  | 9.2 | 0.097 |  | 8.7 | 79.78 | 1.23 |  |  |  |  | 14.519 | 13.899 | [6 empty] | 9.13 | 15.31 | 10.63
2010-05-15 | 6.74 | 6.48 |  |  |  |  | 6.82 | 1.29 |  |  |  |  | 44 |  |  |  | 0 | 0.4505 |  |  | 0.101 | 0.097 | [5 empty] | 25.6 |  |  |  |  | 51.2 |  | 15.4 |  | 9 | 0.118 |  | 8.5 | 75.76 | 1.22 |  |  |  |  | 14.4 | 13.71 | [6 empty] | 9.13 | 15.31 | 10.63
2010-05-16 | 6.74 | 6.44 |  |  |  |  | 6.995 | 1.2 |  |  |  |  | 43.5 |  |  |  | 0 | 0.34525 |  |  | 0.0935 | 0.0975 | [5 empty] | 24.7 |  |  |  |  | 49.4 |  | 15.7 |  | 9.1 | 0.1075 |  | 8.6 | 65.31 | 1.66 |  |  |  |  | 13.679 | 12.972 | [6 empty] | 9.13 | 15.31 | 10.63
2010-05-17 | 6.74 | 6.46 |  |  |  |  | 6.9075 | 1.32 |  |  |  |  | 43.75 |  |  |  | 0 | 0.39787 |  |  | 0.09725 | 0.09725 | [5 empty] | 25.15 |  |  |  |  | 50.3 |  | 15.55 |  | 9.05 | 0.11275 |  | 8.55 | 79.69 | 1.3 |  |  |  |  | 15.4 | 13.829 | [6 empty] | 9.92 | 15.31 | 10.63
2010-05-18 | 6.82 | 6.59 |  |  |  |  | 7.28 | 1.34 |  |  |  |  | 49 |  |  |  | 0 | 0.37156 |  |  | 0.094 | 0.083 | [5 empty] | 25.5 |  |  |  |  | 51 |  | 17.1 |  | 8.7 | 0.114 |  | 8 | 75.23 | 1.01 |  |  |  |  | 15.161 | 14.541 | [6 empty] | 9.92 | 15.31 | 9.62
2010-05-19 | 6.35 | 6.62 |  |  |  |  | 7.5 | 1.31 |  |  |  |  | 40 |  |  |  | 0 | 0.38472 |  |  | 0.129 | 0.139 | [5 empty] | 24.2 |  |  |  |  | 48.4 |  | 18.6 |  | 7.8 | 0.101 |  | 8.3 | 85.8 | 1.35 |  |  |  |  | 15.335 | 14.669 | [6 empty] | 9.92 | 15.31 | 9.43
2010-05-20 | 7.09 | 6.45 |  |  |  |  | 6.72 | 1.26 |  |  |  |  | 31 |  |  |  | 0 | 0.37814 |  |  | 0.152 | 0.761 | [5 empty] | 24.5 |  |  |  |  | 49 |  | 15.6 |  | 8.7 | 0.071 |  | 9 | 81.09 | 1.39 |  |  |  |  | 14.52 | 13.917 | [6 empty] | 9.92 | 15.31 | 9.43
2010-05-21 | 6.35 | 6.18 |  |  |  |  | 7.39 | 1.21 |  |  |  |  | 28 |  |  |  | 0 | 0.38143 |  |  | 0.183 | 0.216 | [5 empty] | 24.2 |  |  |  |  | 48.4 |  | 18.3 |  | 7.8 | 0.223 |  | 9 | 70.03 | 1.12 |  |  |  |  | 14.329 | 13.639 | [6 empty] | 10.72 | 15.31 | 9.43
2010-05-22 | 6.41 | 6.59 |  |  |  |  | 7.9 | 1.26 |  |  |  |  | 41 |  |  |  | 0 | 0.37979 |  |  | 0.085 | 0.112 | [5 empty] | 25.4 |  |  |  |  | 50.8 |  | 19.4 |  | 7.1 | 0.133 |  | 9.2 | 79.69 | 1.32 |  |  |  |  | 14.58 | 14.01 | [6 empty] | 9.13 | 15.31 | 10.63
2010-05-23 | 6.38 | 6.385 |  |  |  |  | 7.645 | 1.2 |  |  |  |  | 34.5 |  |  |  | 0 | 0.38061 |  |  | 0.134 | 0.164 | [5 empty] | 24.8 |  |  |  |  | 49.6 |  | 18.85 |  | 7.45 | 0.178 |  | 9.1 | 59.71 | 1.03 |  |  |  |  | 12.833 | 12.16 | [6 empty] | 9.13 | 15.31 | 10.63
2010-05-24 | 5.78 | 6.3 |  |  |  |  | 7.59 | 1.13 |  |  |  |  | 37 |  |  |  | 0 | 0.3802 |  |  | 0.129 | 0.121 | [5 empty] | 24.3 |  |  |  |  | 48.7 |  | 19.6 |  | 8.9 | 0.1 |  | 9.9 | 90.45 | 1.71 |  |  |  |  | 15.976 | 14.476 | [6 empty] | 9.13 | 15.31 | 10.63
2010-05-25 | 6.41 | 6.47 |  |  |  |  | 7.63 | 1.29 |  |  |  |  | 33 |  |  |  | 0 | 0.3804 |  |  | 0.178 | 0.104 | [5 empty] | 25.1 |  |  |  |  | 50.1 |  | 18.5 |  | 8.9 | 0.114 |  | 1.02 | 79.68 | 1.28 |  |  |  |  | 14.769 | 14.077 | [6 empty] | 9.13 | 14.29 | 9.67
2010-05-26 | 5.49 | 6.43 |  |  |  |  | 7.68 | 1.2 |  |  |  |  | 53 |  |  |  | 0 | 0.3803 |  |  | 0.094 | 0.11 | [5 empty] | 24.6 |  |  |  |  | 49.2 |  | 19.5 |  | 7.3 | 0.138 |  | 10 | 75.79 | 1.21 |  |  |  |  | 14.921 | 14.307 | [6 empty] | 9.13 | 14.29 | 9.67
2010-05-27 | 5.08 | 5.8 |  |  |  |  | 7.41 | 1.05 |  |  |  |  | 37 |  |  |  | 0 | 0.38035 |  |  | 0.15 | 0.132 | [5 empty] | 23 |  |  |  |  | 46 |  | 12 |  | 7.3 | 0.105 |  | 9.9 | 69.92 | 1.24 |  |  |  |  | 14.54 | 13.857 | [6 empty] | 9.13 | 14.29 | 9.67
2010-05-28 | 6.47 | 6.43 |  |  |  |  | 7.63 | 1.23 |  |  |  |  | 48 |  |  |  | 0 | 0.38032 |  |  | 0.104 | 0.101 | [5 empty] | 23.9 |  |  |  |  | 46.9 |  | 18.7 |  | 8.4 | 0.121 |  | 10 | 80.17 | 1.29 |  |  |  |  | 15.102 | 14.471 | [6 empty] | 9.163 | 14.29 | 9.67
2010-05-29 | 6.28 | 6.4 |  |  |  |  | 6.89 | 1.26 |  |  |  |  | 53 |  |  |  | 0 | 0.38034 |  |  | 0.113 | 0.118 | [5 empty] | 24.8 |  |  |  |  | 49.6 |  | 17.8 |  | 8.1 | 0.136 |  | 9.2 | 75.37 | 1.26 |  |  |  |  | 14.25 | 13.57 | [6 empty] | 9.13 | 14.29 | 9.67
2010-05-30 | 6.375 | 6.415 |  |  |  |  | 7.26 | 1.16 |  |  |  |  | 50.5 |  |  |  | 0 | 0.38033 |  |  | 0.1085 | 0.1095 | [5 empty] | 24.35 |  |  |  |  | 48.25 |  | 18.25 |  | 8.25 | 0.1285 |  | 9.6 | 69.92 | 1 |  |  |  |  | 14.45 | 14.7 | [6 empty] | 9.13 | 14.29 | 9.67
2010-05-31 | 7.06 | 6.49 |  |  |  |  | 7.06 | 1.09 |  |  |  |  | 31 |  |  |  | 0 | 0.38033 |  |  | 0.214 | 0.105 | [5 empty] | 24.6 |  |  |  |  | 49.2 |  | 20.2 |  | 8.1 | 0.201 |  | 9.1 | 90.03 | 1.6 |  |  |  |  | 16.772 | 15.22 | [6 empty] | 9.13 | 14.29 | 10.15
2010-06-01 | 6.52 | 5.02 |  |  |  |  | 7.22 | 1.33 |  |  |  |  | 39 |  |  |  | 8 | 0.38033 |  |  | 0.56 | 0.318 | [5 empty] | 24.3 |  |  |  |  | 48.6 |  | 7.6 |  | 7.9 | 0.246 |  | 9.1 | 89.9 | 1.41 |  |  |  |  | 15.506 | 14.903 | [6 empty] | 9.13 | 14.29 | 10.15
2010-06-02 | 6.42 | 6.27 |  |  |  |  | 7.23 | 1.4 |  |  |  |  | 40 |  |  |  | 0 | 0.38033 |  |  | 0.101 | 0.142 | [5 empty] | 26.7 |  |  |  |  | 53.3 |  | 12.5 |  | 9.2 | 0.184 |  | 9.8 | 80.17 | 1.05 |  |  |  |  | 15.517 | 14.876 | [6 empty] | 10.72 | 17.86 | 10.39
2010-06-03 | 5.61 | 6.33 |  |  |  |  | 7.25 | 1.42 |  |  |  |  | 46 |  |  |  | 0 | 0.38033 |  |  | 0.121 | 0.126 | [5 empty] | 27.5 |  |  |  |  | 55 |  | 13.5 |  | 9.7 | 0.11 |  | 9.9 | 75.81 | 0.93 |  |  |  |  | 15.339 | 14.67 | [6 empty] | 10.72 | 17.86 | 10.39
2010-06-04 | 6.77 | 6.33 |  |  |  |  | 7.1 | 1.48 |  |  |  |  | 30 |  |  |  | 0 | 0.38033 |  |  | 0.279 | 0.109 | [5 empty] | 27.5 |  |  |  |  | 55.1 |  | 10.7 |  | 11.1 | 0.163 |  | 10.8 | 69.92 | 0.74 |  |  |  |  | 15.002 | 14.281 | [6 empty] | 9.92 | 17.86 | 10.39
2010-06-05 | 6.81 | 6.4 |  |  |  |  | 7.21 | 1.54 |  |  |  |  | 38 |  |  |  | 0 | 0.38033 |  |  | 0.097 | 0.112 | [5 empty] | 26.7 |  |  |  |  | 53.4 |  | 14.3 |  | 8.6 | 0.154 |  | 10.5 | 79.69 | 0.95 |  |  |  |  | 15.15 | 14.52 | [6 empty] | 9.92 | 17.86 | 10.39
2010-06-06 | 6.79 | 6.365 |  |  |  |  | 7.155 | 1.33 |  |  |  |  | 34 |  |  |  | 0 | 0.38033 |  |  | 0.188 | 0.1105 | [5 empty] | 27.1 |  |  |  |  | 54.25 |  | 12.5 |  | 9.85 | 0.1585 |  | 10.65 | 69.99 | 1.06 |  |  |  |  | 13.996 | 13.32 | [6 empty] | 9.92 | 17.86 | 10.39
2010-06-07 | 7.45 | 6.24 |  |  |  |  | 6.89 | 1.45 |  |  |  |  | 36 |  |  |  | 0 | 0.38033 |  |  | 0.213 | 0.119 | [5 empty] | 26.4 |  |  |  |  | 52.8 |  | 13.7 |  | 8.2 | 0.15 |  | 10.4 | 80.24 | 1.14 |  |  |  |  | 17.148 | 14.06 | [6 empty] | 9.92 | 17.86 | 10.39
2010-06-08 | 7.71 | 6.95 |  |  |  |  | 7.69 | 1.21 |  |  |  |  | 35 |  |  |  | 1 | 0.38033 |  |  | 0.144 | 0.137 | [5 empty] | 27.5 |  |  |  |  | 54.9 |  | 19.8 |  | 9.025 | 0.184 |  | 9.9 | 73.65 | 1.07 |  |  |  |  | 17.816 | 14.669 | [6 empty] | 9.92 | 17.86 | 10.39
2010-06-09 | 6.34 | 7.33 |  |  |  |  | 7.48 | 1.06 |  |  |  |  | 42 |  |  |  | 4 | 0.38033 |  |  | 0.279 | 0.172 | [5 empty] | 28 |  |  |  |  | 56 |  | 19.4 |  | 10.9 | 0.218 |  | 11.1 | 73.63 | 1.17 |  |  |  |  | 18.125 | 14.985 | [6 empty] | 9.92 | 15.82 | 10.55
2010-06-10 | 6.37 | 6.45 |  |  |  |  | 7.38 | 1.07 |  |  |  |  | 42 |  |  |  | 2 | 0.38033 |  |  | 0.289 | 0.207 | [5 empty] | 27.1 |  |  |  |  | 54.2 |  | 20.2 |  | 9.7 | 0.202 |  | 11.1 | 73.65 | 1.19 |  |  |  |  | 16.183 | 14.776 | [6 empty] | 9.92 | 16.84 | 10.55
2010-06-11 | 6.46 | 6.24 |  |  |  |  | 7.44 | 1.26 |  |  |  |  | 32 |  |  |  | 0 | 0.38033 |  |  | 0.134 | 0.113 | [5 empty] | 27.9 |  |  |  |  | 55.8 |  | 23.4 |  | 10.8 | 0.148 |  | 11.7 | 89.96 | 1.4 |  |  |  |  | 17.7 | 15.553 | [6 empty] | 9.13 | 16.84 | 10.55
2010-06-12 | 6.36 | 6.37 |  |  |  |  | 6.47 | 1.25 |  |  |  |  | 39 |  |  |  | 7 | 0.38033 |  |  | 0.503 | 0.138 | [5 empty] | 28.8 |  |  |  |  | 57.7 |  | 12.6 |  | 10.3 | 0.241 |  | 12.3 | 77.68 | 1 |  |  |  |  | 17.4 | 15.69 | [6 empty] | 9.92 | 16.84 | 11.35
2010-06-13 | 6.41 | 6.305 |  |  |  |  | 6.955 | 1.21 |  |  |  |  | 35.5 |  |  |  | 3.5 | 0.38033 |  |  | 0.3185 | 0.1255 | [5 empty] | 28.35 |  |  |  |  | 56.75 |  | 18 |  | 10.55 | 0.1945 |  | 12 | 83.07 | 1.2 |  |  |  |  | 15.734 | 15.684 | [6 empty] | 9.92 | 16.84 | 11.35
2010-06-14 | 6.58 | 6.38 |  |  |  |  | 7.51 | 1.16 |  |  |  |  | 29 |  |  |  | 1 | 0.38033 |  |  | 0.86 | 0.311 | [5 empty] | 27.4 |  |  |  |  | 54.9 |  | 21.3 |  | 12.1 | 0.25 |  | 12.8 | 91.15 | 1.42 |  |  |  |  | 19.133 | 16.059 | [6 empty] | 5.17 | 17.35 | 10.63
2010-06-15 | 6.59 | 6.58 |  |  |  |  | 7.13 | 1.19 |  |  |  |  | 39 |  |  |  | 3 | 0.48 |  |  | 0.207 | 0.11 | [5 empty] | 29.9 |  |  |  |  | 59.8 |  | 24 |  | 9.8 | 0.25 |  | 13.4 | 75.75 | 1.23 |  |  |  |  | 17.421 | 14.22 | [6 empty] | 9.92 | 17.35 | 10.83
2010-06-16 | 6.36 | 6.17 |  |  |  |  | 7.18 | 1.82 |  |  |  |  | 39 |  |  |  | 2 | 0.492 |  |  | 0.243 | 0.168 | [5 empty] | 30.1 |  |  |  |  | 60.2 |  | 21.7 |  | 7.4 | 0.218 |  | 12.6 | 74.09 | 0.46 |  |  |  |  | 17.988 | 14.779 | [6 empty] | 10.4 | 18.37 | 10.63
2010-06-17 | 6.59 | 5.84 |  |  |  |  | 7.16 | 1.35 |  |  |  |  | 38 |  |  |  | 2 | 0.314 |  |  | 0.221 | 0.144 | [5 empty] | 21.3 |  |  |  |  | 42.6 |  | 25 |  | 7.8 | 0.215 |  | 13 | 94.86 | 1.54 |  |  |  |  | 17.956 | 14.856 | [6 empty] | 8.81 | 15.31 | 10.63
2010-06-18 | 6.59 | 6.72 |  |  |  |  | 7.4 | 1.11 |  |  |  |  | 34 |  |  |  | 3 | 0.339 |  |  | 0.189 | 0.189 | [5 empty] | 27.7 |  |  |  |  | 55.4 |  | 23.8 |  | 9.9 | 0.217 |  | 12 | 78.19 | 1.33 |  |  |  |  | 18.199 | 14.567 | [6 empty] | 8.81 | 13.78 | 11.11
2010-06-19 | 6.69 | 6.7 |  |  |  |  | 6.58 | 1.08 |  |  |  |  | 51 |  |  |  | 6 | 0.377 |  |  | 0.52 | 0.235 | [5 empty] | 31.2 |  |  |  |  | 62.4 |  | 26.2 |  | 11.3 | 0.25 |  | 12.2 | 89.47 | 1.56 |  |  |  |  | 17.09 | 15.36 | [6 empty] | 8.81 | 14.545 | 10.87
2010-06-20 | 6.64 | 6.71 |  |  |  |  | 6.99 | 1.06 |  |  |  |  | 42.5 |  |  |  | 4.5 | 0.358 |  |  | 0.3545 | 0.212 | [5 empty] | 29.45 |  |  |  |  | 58.9 |  | 25 |  | 10.6 | 0.2335 |  | 12.1 | 85.07 | 1.54 |  |  |  |  | 14.985 | 14.852 | [6 empty] | 7.7 | 11.74 | 14.46
2010-06-21 | 5.83 | 7.08 |  |  |  |  | 7.08 | 1.26 |  |  |  |  | 38 |  |  |  | 2 | 0.36 |  |  | 0.337 | 0.233 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 24.1 |  | 11.5 | 0.25 |  | 12.9 | 100.24 | 1.93 |  |  |  |  | 15.714 | 14.238 | [6 empty] | 7.7 | 11.74 | 14.46
2010-06-22 | 5.78 | 5.82 |  |  |  |  | 7.46 | 1.22 |  |  |  |  | 36 |  |  |  | 1 | 0.416 |  |  | 0.503 | 0.344 | [5 empty] | 30.5 |  |  |  |  | 61 |  | 20.3 |  | 10.4 | 0.25 |  | 12.8 | 100.22 | 1.71 |  |  |  |  | 16.125 | 15.516 | [6 empty] | 7.39 | 12.76 | 14.46
2010-06-23 | 5.9 | 5.87 |  |  |  |  | 7.52 | 1.12 |  |  |  |  | 39 |  |  |  | 2 | 0.401 |  |  | 0.517 | 0.402 | [5 empty] | 32.2 |  |  |  |  | 64.4 |  | 26.4 |  | 12.6 | 0.224 |  | 12.9 | 99.53 | 1.74 |  |  |  |  | 16.321 | 15.794 | [6 empty] | 7.86 | 12.26 | 14.46
2010-06-24 | 5.78 | 6.18 |  |  |  |  | 7.18 | 1.17 |  |  |  |  | 39 |  |  |  | 0 | 0.484 |  |  | 0.903 | 0.319 | [5 empty] | 32.6 |  |  |  |  | 65.2 |  | 25.8 |  | 12.9 | 0.25 |  | 13.6 | 100.22 | 2 |  |  |  |  | 15.59 | 14.65 | [6 empty] | 7.86 | 12.76 | 14.46
2010-06-25 | 5.8 | 5.8 |  |  |  |  | 7.1 | 1.21 |  |  |  |  | 39 |  |  |  | 0 | 0.61 |  |  | 0.61 | 0.276 | [5 empty] | 32.6 |  |  |  |  | 65.2 |  | 26.7 |  | 13 | 0.25 |  | 13.6 | 110.49 | 1.78 |  |  |  |  | 17.217 | 16.76 | [6 empty] | 7.86 | 12.76 | 14.46
2010-06-26 | 6.4 | 6.1 |  |  |  |  | 7.2 | 1.15 |  |  |  |  | 44 |  |  |  | 1 | 0.479 |  |  | 0.31 | 0.224 | [5 empty] | 30.1 |  |  |  |  | 60.1 |  | 23.3 |  | 9.6 | 0.25 |  | 13.7 | 100.24 | 1.81 |  |  |  |  | 16.05 | 15.4 | [6 empty] | 7.86 | 12.76 | 14.46
2010-06-27 | 6.1 | 5.95 |  |  |  |  | 7.15 | 1.12 |  |  |  |  | 41.5 |  |  |  | 0.5 | 0.5445 |  |  | 0.46 | 0.25 | [5 empty] | 31.35 |  |  |  |  | 62.65 |  | 25 |  | 11.3 | 0.25 |  | 13.65 | 100.22 | 1.8 |  |  |  |  | 16.16 | 15.61 | [6 empty] | 8.34 | 12.25 | 14.46
2010-06-28 | 5.81 | 6.08 |  |  |  |  | 7.14 | 1.21 |  |  |  |  | 39 |  |  |  | 1 | 0.524 |  |  | 0.213 | 0.183 | [5 empty] | 32.8 |  |  |  |  | 65.8 |  | 26.9 |  | 14.2 | 0.25 |  | 14.5 | 105.13 | 1.71 |  |  |  |  | 18.815 | 16.335 | [6 empty] | 8.34 | 12.25 | 14.46
2010-06-29 | 5.81 | 6.44 |  |  |  |  | 7.13 | 0.95 |  |  |  |  | 38 |  |  |  | 2 | 0.478 |  |  | 0.636 | 0.192 | [5 empty] | 32 |  |  |  |  | 64 |  | 29.1 |  | 19 | 0.25 |  | 14.7 | 94.84 | 1.91 |  |  |  |  | 18.247 | 15.079 | [6 empty] | 8.34 | 12.25 | 14.46
2010-06-30 | 5.76 | 5.8 |  |  |  |  | 7.12 | 1.05 |  |  |  |  | 41 |  |  |  | 3 | 0.443 |  |  | 0.542 | 0.192 | [5 empty] | 30.5 |  |  |  |  | 61.1 |  | 24.9 |  | 13.7 | 0.25 |  | 14.7 | 97.02 | 1.9 |  |  |  |  | 18.188 | 14.91 | [6 empty] | 8.34 | 12.25 | 14.46
2010-07-01 | 5.8 | 5.72 |  |  |  |  | 7.24 | 1.15 |  |  |  |  | 37 |  |  |  | 3 | 0.522 |  |  | 0.386 | 0.169 | [5 empty] | 29.1 |  |  |  |  | 58.3 |  | 25.1 |  | 12 | 0.25 |  | 14.8 | 105.11 | 1.94 |  |  |  |  | 17.006 | 15.416 | [6 empty] | 8.34 | 12.25 | 14.46
2010-07-02 | 6.01 | 5.87 |  |  |  |  | 7.25 | 1.17 |  |  |  |  | 38 |  |  |  | 1 | 0.468 |  |  | 0.108 | 0.158 | [5 empty] | 30.2 |  |  |  |  | 60.4 |  | 25.8 |  | 11.8 | 0.25 |  | 14.9 | 94.88 | 1.53 |  |  |  |  | 16.127 | 15.968 | [6 empty] | 8.34 | 30.62 | 14.46
2010-07-03 | 5.85 | 5.98 |  |  |  |  | 6.87 | 1.05 |  |  |  |  | 38 |  |  |  | 0 | 0.483 |  |  | 0.194 | 0.139 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 21.6 |  | 13.7 | 0.25 |  | 15.6 | 95.76 | 1.86 |  |  |  |  | 15.55 | 14.92 | [6 empty] | 8.34 | 30.62 | 14.46
2010-07-04 | 5.93 | 5.925 |  |  |  |  | 7.06 | 1.07 |  |  |  |  | 38 |  |  |  | 0.5 | 0.4755 |  |  | 0.151 | 0.1485 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 23.7 |  | 12.75 | 0.25 |  | 15.25 | 85 | 1.63 |  |  |  |  | 15.03 | 14.27 | [6 empty] | 8.34 | 30.62 | 14.46
2010-07-05 | 5.91 | 6.22 |  |  |  |  | 7.03 | 1.44 |  |  |  |  | 37 |  |  |  | 3 | 0.466 |  |  | 0.364 | 0.16 | [5 empty] | 31.3 |  |  |  |  | 62.6 |  | 25.5 |  | 12.2 | 0.25 |  | 15 | 100.72 | 1.5 |  |  |  |  | 16.173 | 15.555 | [6 empty] | 8.34 | 30.62 | 14.46
2010-07-06 | 5.79 | 6.01 |  |  |  |  | 7.05 | 1.36 |  |  |  |  | 37 |  |  |  | 4 | 0.54 |  |  | 0.515 | 0.148 | [5 empty] | 29.9 |  |  |  |  | 59.9 |  | 26.7 |  | 12 | 0.25 |  | 15.3 | 99.73 | 1.73 |  |  |  |  | 15.321 | 14.619 | [6 empty] | 8.34 | 31.13 | 14.46
2010-07-07 | 5.85 | 5.24 |  |  |  |  | 6.97 | 1.41 |  |  |  |  | 32 |  |  |  | 1 | 0.529 |  |  | 0.344 | 0.14 | [5 empty] | 31.8 |  |  |  |  | 63.6 |  | 26.1 |  | 11.2 | 0.245 |  | 14.7 | 100.23 | 1.69 |  |  |  |  | 15.315 | 14.675 | [6 empty] | 8.34 | 31.13 | 14.46
2010-07-08 | 5.81 | 6.22 |  |  |  |  | 7.08 | 1.32 |  |  |  |  | 31 |  |  |  | 0 | 0.515 |  |  | 0.321 | 0.173 | [5 empty] | 32.9 |  |  |  |  | 65.8 |  | 24.7 |  | 11.4 | 0.211 |  | 14.6 | 95.04 | 1.57 |  |  |  |  | 15.62 | 14.915 | [6 empty] | 8.34 | 31.13 | 14.46
2010-07-09 | 5.89 | 6.46 |  |  |  |  | 7.2 | 1.18 |  |  |  |  | 36 |  |  |  | 4 | 0.493 |  |  | 0.696 | 0.161 | [5 empty] | 32.9 |  |  |  |  | 65.9 |  | 26.9 |  | 12.3 | 0.233 |  | 14.9 | 105.53 | 1.66 |  |  |  |  | 19.117 | 16.86 | [6 empty] | 7.55 | 31.13 | 14.46
2010-07-10 | 5.91 | 5.92 |  |  |  |  | 7.25 | 1.16 |  |  |  |  | 34 |  |  |  | 4 | 0.499 |  |  | 0.254 | 0.165 | [5 empty] | 31.6 |  |  |  |  | 63.2 |  | 23.8 |  | 12.9 | 0.237 |  | 16.4 | 109.52 | 1.87 |  |  |  |  | 19.75 | 16.42 | [6 empty] | 7.23 | 32.66 | 14.46
2010-07-11 | 5.9 | 6.19 |  |  |  |  | 7.225 | 0.91 |  |  |  |  | 35 |  |  |  | 4 | 0.496 |  |  | 0.475 | 0.163 | [5 empty] | 32.25 |  |  |  |  | 64.55 |  | 25.35 |  | 12.6 | 0.235 |  | 15.65 | 95.41 | 1.95 |  |  |  |  | 17.99 | 15.142 | [6 empty] | 7.23 | 32.66 | 14.46
2010-07-12 | 5.92 | 6.25 |  |  |  |  | 7.28 | 1.08 |  |  |  |  | 34 |  |  |  | 0 | 0.562 |  |  | 0.382 | 0.194 | [5 empty] | 33.7 |  |  |  |  | 67.4 |  | 26.1 |  | 12.4 | 0.237 |  | 17.5 | 105.6 | 2.2 |  |  |  |  | 18.387 | 14.633 | [6 empty] | 6.91 | 32.66 | 14.46
2010-07-13 | 5.88 | 6.31 |  |  |  |  | 7.22 | 1.35 |  |  |  |  | 35 |  |  |  | 0 | 0.689 |  |  | 0.511 | 0.186 | [5 empty] | 33.5 |  |  |  |  | 67 |  | 26 |  | 12.1 | 0.233 |  | 17.6 | 125.18 | 2.57 |  |  |  |  | 19.595 | 15.498 | [6 empty] | 6.75 | 34.19 | 14.46
2010-07-14 | 5.9 | 6.28 |  |  |  |  | 7.25 | 1.48 |  |  |  |  | 34.5 |  |  |  | 0 | 0.6255 |  |  | 0.4465 | 0.19 | [5 empty] | 33.6 |  |  |  |  | 67.2 |  | 26.05 |  | 12.25 | 0.235 |  | 17.55 | 139.82 | 2.14 |  |  |  |  | 19.183 | 17.519 | [6 empty] | 6.75 | 24.19 | 14.46
2010-07-15 | 5.81 | 6.81 |  |  |  |  | 7.2 | 1.41 |  |  |  |  | 36 |  |  |  | 2 | 0.661 |  |  | 0.193 | 0.175 | [5 empty] | 33.5 |  |  |  |  | 67.1 |  | 29.8 |  | 13.9 | 0.223 |  | 18.2 | 135.43 | 2.45 |  |  |  |  | 16.491 | 15.921 | [6 empty] | 7.86 | 36.74 | 14.46
2010-07-16 | 5.96 | 6.08 |  |  |  |  | 7.16 | 1.37 |  |  |  |  | 36 |  |  |  | 6 | 0.712 |  |  | 0.121 | 0.514 | [5 empty] | 29.7 |  |  |  |  | 59.4 |  | 18.8 |  | 13.3 | 0.245 |  | 17.9 | 150.29 | 2.52 |  |  |  |  | 18.1 | 17.55 | [6 empty] | 7.86 | 45.93 | 14.46
2010-07-17 | 5.885 | 6.445 |  |  |  |  | 7.18 | 1.23 |  |  |  |  | 36 |  |  |  | 4 | 0.6865 |  |  | 0.157 | 0.3445 | [5 empty] | 31.6 |  |  |  |  | 63.25 |  | 24.3 |  | 13.6 | 0.234 |  | 18.05 | 130.11 | 2.52 |  |  |  |  | 16.4 | 15.77 | [6 empty] | 7.86 | 45.93 | 14.46
2010-07-18 | 5.9225 | 6.2625 |  |  |  |  | 7.17 | 0.94 |  |  |  |  | 36 |  |  |  | 5 | 0.69925 |  |  | 0.139 | 0.42925 | [5 empty] | 30.65 |  |  |  |  | 61.325 |  | 21.55 |  | 13.45 | 0.2395 |  | 17.975 | 124.67 | 2.52 |  |  |  |  | 16.55 | 16.34 | [6 empty] | 7.86 | 45.93 | 14.46
2010-07-19 | 5.98 | 6.37 |  |  |  |  | 7.04 | 1.34 |  |  |  |  | 34 |  |  |  | 6 | 0.646 |  |  | 0.98 | 0.297 | [5 empty] | 31.2 |  |  |  |  | 61.5 |  | 20.5 |  | 13.7 | 0.25 |  | 19.3 | 159.47 | 3.13 |  |  |  |  | 17.314 | 16.243 | [6 empty] | 8.15 | 21 | 38
2010-07-20 | 7.19 | 6.42 |  |  |  |  | 7.61 | 1.64 |  |  |  |  | 38 |  |  |  | 0 | 0.561 |  |  | 0.135 | 0.109 | [5 empty] | 24.3 |  |  |  |  | 48.9 |  | 22.1 |  | 8.2 | 0.146 |  | 19.2 | 154.99 | 2.45 |  |  |  |  | 17.818 | 17.195 | [6 empty] | 8.34 | 10.72 | 8.95
2010-07-21 | 6.66 | 6.29 |  |  |  |  | 6.878 | 1.7 |  |  |  |  | 37 |  |  |  | 4 | 0.611 |  |  | 0.114 | 0.123 | [5 empty] | 24 |  |  |  |  | 48.1 |  | 21.2 |  | 8.4 | 0.236 |  | 19.3 | 151.09 | 2.52 |  |  |  |  | 16.819 | 16.257 | [6 empty] | 8.02 | 5.61 | 9.91
2010-07-22 | 7.03 | 6.46 |  |  |  |  | 6.99 | 1.63 |  |  |  |  | 36 |  |  |  | 2 | 0.507 |  |  | 0.131 | 0.191 | [5 empty] | 22.6 |  |  |  |  | 46.2 |  | 22.3 |  | 8 | 0.224 |  | 19.6 | 154.99 | 2.66 |  |  |  |  | 17.047 | 16.401 | [6 empty] | 8.34 | 4.08 | 9.91
2010-07-23 | 6.64 | 6.3 |  |  |  |  | 6.83 | 1.56 |  |  |  |  | 43 |  |  |  | 1 | 0.597 |  |  | 0.106 | 0.462 | [5 empty] | 25.8 |  |  |  |  | 51.6 |  | 21.3 |  | 6.2 | 0.188 |  | 19.5 | 139.73 | 2.68 |  |  |  |  | 15.62 | 14.957 | [6 empty] | 8.5 | 4.08 | 9.91
2010-07-24 | 6.47 | 5.68 |  |  |  |  | 7.06 | 1.72 |  |  |  |  | 44 |  |  |  | 1 | 0.503 |  |  | 0.111 | 0.408 | [5 empty] | 25.6 |  |  |  |  | 51.2 |  | 12.3 |  | 7.2 | 0.209 |  | 18.9 | 145.9 | 2.4 |  |  |  |  | 16.77 | 16.05 | [6 empty] | 8.02 | 4.08 | 10.63
2010-07-25 | 6.555 | 5.99 |  |  |  |  | 6.945 | 1.73 |  |  |  |  | 43.5 |  |  |  | 1 | 0.55 |  |  | 0.1085 | 0.435 | [5 empty] | 25.7 |  |  |  |  | 51.4 |  | 16.8 |  | 6.7 | 0.1985 |  | 19.2 | 130.05 | 2.4 |  |  |  |  | 15.0645 | 14.312 | [6 empty] | 8.02 | 22.96 | 10.39
2010-07-26 | 6.5 | 6.48 |  |  |  |  | 7.29 | 1.72 |  |  |  |  | 39 |  |  |  | 1 | 0.498 |  |  | 0.201 | 0.174 | [5 empty] | 27 |  |  |  |  | 54 |  | 17.1 |  | 7.3 | 0.173 |  | 20.4 | 135.01 | 2.37 |  |  |  |  | 16.638 | 14.973 | [6 empty] | 8.02 | 22.96 | 10.39
2010-07-27 | 6.62 | 6.31 |  |  |  |  | 7.7 | 1.52 |  |  |  |  | 39 |  |  |  | 2 | 0.56 |  |  | 0.177 | 0.291 | [5 empty] | 26 |  |  |  |  | 52 |  | 19.2 |  | 9.4 | 0.119 |  | 19.3 | 130.05 | 2.4 |  |  |  |  | 15.73 | 15.047 | [6 empty] | 8.02 | 22.96 | 10.39
2010-07-28 | 6.35 | 6.49 |  |  |  |  | 7.22 | 1.67 |  |  |  |  | 43 |  |  |  | 3 | 0.55 |  |  | 0.359 | 0.174 | [5 empty] | 23.2 |  |  |  |  | 46.4 |  | 20.1 |  | 8.6 | 0.11 |  | 18 | 139.91 | 2.38 |  |  |  |  | 16.429 | 15.691 | [6 empty] | 7.55 | 20.41 | 10.15
2010-07-29 | 6.91 | 6.24 |  |  |  |  | 7.06 | 1.71 |  |  |  |  | 45 |  |  |  | 0 | 0.594 |  |  | 0.2 | 0.152 | [5 empty] | 23.3 |  |  |  |  | 46.6 |  | 18.9 |  | 7.3 | 0.151 |  | 18.3 | 129.39 | 2.5 |  |  |  |  | 14.656 | 13.939 | [6 empty] | 8.02 | 14.29 | 10.15
2010-07-30 | 7.11 | 6.58 |  |  |  |  | 7.9 | 1.58 |  |  |  |  | 41 |  |  |  | 4 | 1.09 |  |  | 0.639 | 0.215 | [5 empty] | 27.3 |  |  |  |  | 54.6 |  | 21.4 |  | 9.3 | 0.204 |  | 18 | 150.6 | 2.4 |  |  |  |  | 17.934 | 17.201 | [6 empty] | 8.02 | 30.62 | 11.35
2010-07-31 | 7.18 | 6.58 |  |  |  |  | 7.11 | 1.71 |  |  |  |  | 30 |  |  |  | 0 | 0.882 |  |  | 0.15 | 0.634 | [5 empty] | 24.4 |  |  |  |  | 48.8 |  | 12.1 |  | 8.5 | 0.185 |  | 18.4 | 140.3 | 2.48 |  |  |  |  | 15.87 | 15.2 | [6 empty] | 8.34 | 13.27 | 10.63
2010-08-01 | 7.145 | 6.58 |  |  |  |  | 7.505 | 1.63 |  |  |  |  | 35.5 |  |  |  | 2 | 0.986 |  |  | 0.3945 | 0.4245 | [5 empty] | 25.85 |  |  |  |  | 51.7 |  | 16.75 |  | 8.9 | 0.1945 |  | 18.2 | 135.43 | 4.52 |  |  |  |  | 15.699 | 14.944 | [6 empty] | 8.34 | 13.27 | 10.63
2010-08-02 | 6.22 | 6.33 |  |  |  |  | 7.02 | 1.58 |  |  |  |  | 42 |  |  |  | 2 | 0.726 |  |  | 0.209 | 0.136 | [5 empty] | 25.5 |  |  |  |  | 51 |  | 15.9 |  | 7.6 | 0.159 |  | 18.2 | 150.76 | 2.69 |  |  |  |  | 16.834 | 16.028 | [6 empty] | 8.34 | 11.23 | 11.11
2010-08-03 | 6.23 | 6.15 |  |  |  |  | 7.33 | 2.98 |  |  |  |  | 41 |  |  |  | 0 | 0.661 |  |  | 0.164 | 0.175 | [5 empty] | 26.4 |  |  |  |  | 52.8 |  | 18.1 |  | 8.7 | 0.183 |  | 18.4 | 146.39 | 1.32 |  |  |  |  | 16.211 | 15.459 | [6 empty] | 13.89 | 15.31 | 11.83
2010-08-04 | 7.41 | 6.21 |  |  |  |  | 7.46 | 1.6 |  |  |  |  | 38 |  |  |  | 4 | 0.68 |  |  | 0.676 | 0.192 | [5 empty] | 26.5 |  |  |  |  | 53.1 |  | 25.4 |  | 9.8 | 0.214 |  | 18.7 | 174.86 | 3.2 |  |  |  |  | 17.199 | 16.536 | [6 empty] | 13.89 | 15.31 | 13.89
2010-08-05 | 6.89 | 6.23 |  |  |  |  | 7.42 | 1.51 |  |  |  |  | 40 |  |  |  | 2 | 0.534 |  |  | 0.325 | 0.151 | [5 empty] | 24.9 |  |  |  |  | 49.9 |  | 22.1 |  | 9.8 | 0.208 |  | 19 | 150.6 | 3.27 |  |  |  |  | 18.152 | 15.262 | [6 empty] | 14.68 | 8.68 | 11.83
2010-08-06 | 6.65 | 6 |  |  |  |  | 6.84 | 1.88 |  |  |  |  | 42 |  |  |  | 0 | 0.501 |  |  | 0.109 | 0.119 | [5 empty] | 27.7 |  |  |  |  | 55.5 |  | 20.6 |  | 9.1 | 0.25 |  | 19.5 | 159.86 | 2.76 |  |  |  |  | 19.169 | 15.645 | [6 empty] | 8.34 | 8.68 | 12.31
2010-08-07 | 6.65 | 6.42 |  |  |  |  | 7.3 | 1.78 |  |  |  |  | 40 |  |  |  | 1 | 0.458 |  |  | 0.113 | 0.128 | [5 empty] | 28.6 |  |  |  |  | 57.2 |  | 20 |  | 8.4 | 0.202 |  | 19.7 | 150.12 | 2.67 |  |  |  |  | 18.93 | 15.33 | [6 empty] | 7.55 | 22.45 | 13.02
2010-08-08 | 6.65 | 6.21 |  |  |  |  | 7.07 | 1.72 |  |  |  |  | 41 |  |  |  | 0.5 | 0.4795 |  |  | 0.111 | 0.1235 | [5 empty] | 28.15 |  |  |  |  | 56.35 |  | 20.3 |  | 8.75 | 0.226 |  | 19.6 | 136.56 | 2.47 |  |  |  |  | 18.321 | 14.784 | [6 empty] | 7.945 | 15.565 | 12.665
2010-08-09 | 6.85 | 6.55 |  |  |  |  | 7.24 | 1.65 |  |  |  |  | 36 |  |  |  | 0 | 0.526 |  |  | 0.138 | 0.157 | [5 empty] | 26.4 |  |  |  |  | 52.8 |  | 20.1 |  | 8.8 | 0.25 |  | 18.6 | 150.29 | 2.71 |  |  |  |  | 19.053 | 15.637 | [6 empty] | 6.75 | 10.21 | 11.83
2010-08-10 | 6.9 | 6.22 |  |  |  |  | 7.18 | 1.46 |  |  |  |  | 50 |  |  |  | 4 | 0.617 |  |  | 0.153 | 0.161 | [5 empty] | 25.9 |  |  |  |  | 51.9 |  | 21.9 |  | 8.4 | 0.25 |  | 18.6 | 145.68 | 2.87 |  |  |  |  | 18.924 | 15.269 | [6 empty] | 6.12 | 7.65 | 11.83
2010-08-11 | 6.44 | 6.17 |  |  |  |  | 7.28 | 1.33 |  |  |  |  | 39 |  |  |  | 3 | 0.554 |  |  | 0.25 | 0.156 | [5 empty] | 26 |  |  |  |  | 51.9 |  | 20.3 |  | 8.6 | 0.25 |  | 19.3 | 144.74 | 2.9 |  |  |  |  | 18.444 | 15.535 | [6 empty] | 5.48 | 8.16 | 11.83
2010-08-12 | 6.84 | 6.25 |  |  |  |  | 7.15 | 1.57 |  |  |  |  | 36 |  |  |  | 0 | 0.618 |  |  | 0.216 | 0.17 | [5 empty] | 25.3 |  |  |  |  | 50.6 |  | 21.1 |  | 8.5 | 0.202 |  | 19.1 | 139.84 | 2.93 |  |  |  |  | 18.317 | 14.099 | [6 empty] | 5.64 | 8.16 | 11.83
2010-08-13 | 6.38 | 6.47 |  |  |  |  | 7.31 | 1.77 |  |  |  |  | 44 |  |  |  | 2 | 0.797 |  |  | 0.11 | 0.27 | [5 empty] | 27.8 |  |  |  |  | 55.6 |  | 21.2 |  | 8.4 | 0.22 |  | 18.3 | 150.09 | 2.97 |  |  |  |  | 18.189 | 14.376 | [6 empty] | 8.34 | 10.21 | 11.35
2010-08-14 | 6.79 | 6.42 |  |  |  |  | 7.25 | 1.7 |  |  |  |  | 39 |  |  |  | 1 | 0.635 |  |  | 0.183 | 0.147 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 22.9 |  | 8.45 | 0.197 |  | 18.7 | 135.92 | 2.57 |  |  |  |  | 17.672 | 14.441 | [6 empty] | 7.55 | 20.41 | 11.83
2010-08-15 | 6.585 | 6.445 |  |  |  |  | 7.28 | 1.63 |  |  |  |  | 41.5 |  |  |  | 1.5 | 0.716 |  |  | 0.1465 | 0.2085 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 22.05 |  | 8.425 | 0.2085 |  | 18.5 | 134.95 | 2.54 |  |  |  |  | 18.051 | 14.681 | [6 empty] | 7.55 | 21.43 | 11.83
2010-08-16 | 6.67 | 6.24 |  |  |  |  | 7.3 | 1.68 |  |  |  |  | 40 |  |  |  | 0 | 0.62 |  |  | 0.288 | 0.161 | [5 empty] | 28.9 |  |  |  |  | 57.9 |  | 27.3 |  | 8.4375 | 0.175 |  | 19.3 | 155.65 | 2.73 |  |  |  |  | 19.575 | 16.043 | [6 empty] | 7.55 | 10.21 | 11.83
2010-08-17 | 6.59 | 6.2 |  |  |  |  | 7.06 | 1.74 |  |  |  |  | 39 |  |  |  | 0 | 0.616 |  |  | 0.212 | 0.175 | [5 empty] | 27.3 |  |  |  |  | 54.6 |  | 26.6 |  | 8.4313 | 0.136 |  | 20 | 124.67 | 1.85 |  |  |  |  | 19.251 | 15.787 | [6 empty] | 7.55 | 10.21 | 11.83
2010-08-18 | 6.63 | 6.22 |  |  |  |  | 7.18 | 1.71 |  |  |  |  | 39.5 |  |  |  | 0 | 0.618 |  |  | 0.25 | 0.168 | [5 empty] | 28.1 |  |  |  |  | 56.25 |  | 26.95 |  | 8.4344 | 0.1555 |  | 19.65 | 140.16 | 2.29 |  |  |  |  | 19.413 | 15.915 | [6 empty] | 7.55 | 10.21 | 11.83
2010-08-19 | 6.77 | 6.56 |  |  |  |  | 7.9 | 2.21 |  |  |  |  | 36 |  |  |  | 1 | 0.499 |  |  | 0.133 | 0.373 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 21.1 |  | 8.4328 | 0.142 |  | 20.6 | 170.56 | 2.95 |  |  |  |  | 18.562 | 15.009 | [6 empty] | 5.96 | 10.21 | 11.83
2010-08-20 | 6.74 | 6.9 |  |  |  |  | 7.17 | 2.14 |  |  |  |  | 30 |  |  |  | 0 | 0.528 |  |  | 0.375 | 0.369 | [5 empty] | 25.8 |  |  |  |  | 51.6 |  | 19.9 |  | 8.4336 | 0.094 |  | 20 | 165.26 | 2.7 |  |  |  |  | 18.94 | 15.5 | [6 empty] | 5.96 | 10.21 | 11.83
2010-08-21 | 6.755 | 6.73 |  |  |  |  | 7.535 | 2.175 |  |  |  |  | 33 |  |  |  | 0.5 | 0.5135 |  |  | 0.254 | 0.371 | [5 empty] | 26.95 |  |  |  |  | 53.9 |  | 20.5 |  | 8.4332 | 0.118 |  | 20.3 | 167.91 | 2.825 |  |  |  |  | 18.751 | 15.2545 | [6 empty] | 5.96 | 10.21 | 11.83
2010-08-22 | 6.7475 | 6.815 |  |  |  |  | 7.3525 | 2.41 |  |  |  |  | 31.5 |  |  |  | 0.25 | 0.52075 |  |  | 0.3145 | 0.37 | [5 empty] | 26.375 |  |  |  |  | 52.75 |  | 20.2 |  | 8.4334 | 0.106 |  | 20.15 | 160.52 | 2.87 |  |  |  |  | 17.406 | 13.812 | [6 empty] | 7.55 | 10.21 | 12.31
2010-08-23 | 6.46 | 6.41 |  |  |  |  | 6.54 | 1.94 |  |  |  |  | 31 |  |  |  | 1 | 0.492 |  |  | 0.24 | 0.616 | [5 empty] | 26.1 |  |  |  |  | 52.2 |  | 23.3 |  | 8.4333 | 0.25 |  | 18.4 | 135.94 | 2.41 |  |  |  |  | 18.214 | 14.182 | [6 empty] | 7.55 | 10.21 | 12.31
2010-08-24 | 6.48 | 6.26 |  |  |  |  | 7.18 | 1.7 |  |  |  |  | 30 |  |  |  | 1 | 0.587 |  |  | 0.207 | 0.307 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 24 |  | 7.1 | 0.172 |  | 18.1 | 130.05 | 2.19 |  |  |  |  | 18.782 | 15.176 | [6 empty] | 8.34 | 10.34 | 13.06
2010-08-25 | 6.52 | 6.38 |  |  |  |  | 6.88 | 1.85 |  |  |  |  | 39 |  |  |  | 5 | 0.606 |  |  | 0.395 | 0.261 | [5 empty] | 28.8 |  |  |  |  | 57.7 |  | 25.6 |  | 9.8 | 2.5 |  | 18.4 | 149.68 | 2.33 |  |  |  |  | 19.805 | 16.245 | [6 empty] | 8.02 | 10.34 | 13.77
2010-08-26 | 6.66 | 6.53 |  |  |  |  | 7.6 | 1.63 |  |  |  |  | 22 |  |  |  | 0 | 0.635 |  |  | 0.374 | 0.294 | [5 empty] | 28.6 |  |  |  |  | 57.3 |  | 22.5 |  | 9.8 | 0.25 |  | 18.6 | 150.58 | 2.45 |  |  |  |  | 20.983 | 16.773 | [6 empty] | 8.34 | 8.68 | 13.3
2010-08-27 | 6.83 | 6.73 |  |  |  |  | 7.28 | 1.65 |  |  |  |  | 30 |  |  |  | 2 | 0.44 |  |  | 0.215 | 0.313 | [5 empty] | 28.7 |  |  |  |  | 57.3 |  | 22.5 |  | 9.4 | 0.249 |  | 19.4 | 140.33 | 2.33 |  |  |  |  | 20.197 | 15.998 | [6 empty] | 8.02 | 9.51 | 13.3
2010-08-28 | 6.96 | 7.07 |  |  |  |  | 6.99 | 1.59 |  |  |  |  | 39 |  |  |  | 2 | 0.459 |  |  | 0.295 | 0.708 | [5 empty] | 28.2 |  |  |  |  | 56.3 |  | 20.4 |  | 8.2 | 0.25 |  | 19.3 | 125.16 | 2.37 |  |  |  |  | 18.57 | 14.34 | [6 empty] | 8.34 | 9.095 | 13.3
2010-08-29 | 6.895 | 6.9 |  |  |  |  | 7.135 | 1.62 |  |  |  |  | 34.5 |  |  |  | 2 | 0.4495 |  |  | 0.255 | 0.5105 | [5 empty] | 28.45 |  |  |  |  | 56.8 |  | 21.45 |  | 8.8 | 0.2495 |  | 19.35 | 132.745 | 2.35 |  |  |  |  | 19.3835 | 15.169 | [6 empty] | 8.18 | 9.3025 | 13.3
2010-08-30 | 6.73 | 7.02 |  |  |  |  | 7.88 | 1.42 |  |  |  |  | 36 |  |  |  | 6 | 0.518 |  |  | 0.222 | 0.344 | [5 empty] | 28.7 |  |  |  |  | 57.3 |  | 24 |  | 9.8 | 0.25 |  | 18.8 | 135.43 | 2.05 |  |  |  |  | 19.715 | 15.093 | [6 empty] | 8.02 | 9.1987 | 13.3
2010-08-31 | 7.05 | 6.42 |  |  |  |  | 7.53 | 1.27 |  |  |  |  | 38 |  |  |  | 5 | 0.496 |  |  | 0.075 | 0.225 | [5 empty] | 27.7 |  |  |  |  | 55.3 |  | 22.7 |  | 8.2 | 0.25 |  | 18.6 | 134.95 | 2.63 |  |  |  |  | 20.646 | 15.709 | [6 empty] | 8.02 | 9.2506 | 13.3
2010-09-01 | 6.7 | 6.41 |  |  |  |  | 7.62 | 1.66 |  |  |  |  | 34 |  |  |  | 1 | 0.46 |  |  | 0.264 | 0.165 | [5 empty] | 28 |  |  |  |  | 56 |  | 22 |  | 8.7 | 0.25 |  | 18.9 | 140.33 | 2.41 |  |  |  |  | 20.759 | 15.634 | [6 empty] | 8.02 | 8.68 | 13.3
2010-09-02 | 6.71 | 6.46 |  |  |  |  | 7.35 | 1.77 |  |  |  |  | 30 |  |  |  | 4 | 0.429 |  |  | 0.336 | 0.186 | [5 empty] | 29.9 |  |  |  |  | 59.9 |  | 24 |  | 9.2 | 0.25 |  | 19.1 | 134.92 | 2.25 |  |  |  |  | 20.333 | 15.228 | [6 empty] | 8.5 | 18.88 | 12.1
2010-09-03 | 6.71 | 6.3 |  |  |  |  | 6.88 | 1.74 |  |  |  |  | 43 |  |  |  | 2 | 0.478 |  |  | 0.262 | 0.413 | [5 empty] | 29.8 |  |  |  |  | 59.6 |  | 23.1 |  | 9.1 | 0.153 |  | 18.5 | 134.95 | 2.33 |  |  |  |  | 20.213 | 15.067 | [6 empty] | 9.13 | 18.88 | 12.1
2010-09-04 | 6.84 | 6.42 |  |  |  |  | 7.04 | 1.81 |  |  |  |  | 41 |  |  |  | 1 | 0.424 |  |  | 0.243 | 0.435 | [5 empty] | 31.1 |  |  |  |  | 62.2 |  | 23.7 |  | 8.9 | 0.202 |  | 19 | 125.6 | 2.16 |  |  |  |  | 19.04 | 14.35 | [6 empty] | 9.77 | 19.9 | 12.58
2010-09-05 | 6.775 | 6.36 |  |  |  |  | 6.96 | 1.65 |  |  |  |  | 42 |  |  |  | 1.5 | 0.451 |  |  | 0.2525 | 0.424 | [5 empty] | 30.45 |  |  |  |  | 60.9 |  | 23.4 |  | 9 | 0.1775 |  | 18.75 | 120.33 | 2.39 |  |  |  |  | 18.642 | 13.524 | [6 empty] | 9.77 | 19.9 | 12.58
2010-09-06 | 6.62 | 6.21 |  |  |  |  | 7.11 | 1.61 |  |  |  |  | 50 |  |  |  | 3 | 1.542 |  |  | 0.24 | 0.534 | [5 empty] | 29 |  |  |  |  | 58 |  | 25.9 |  | 10.5 | 0.136 |  | 19.5 | 130.49 | 2.59 |  |  |  |  | 19.154 | 14.098 | [6 empty] | 9.45 | 7.65 | 14.25
2010-09-07 | 6.67 | 6.28 |  |  |  |  | 7.6 | 1.65 |  |  |  |  | 38 |  |  |  | 2 | 1.192 |  |  | 0.331 | 0.398 | [5 empty] | 31.3 |  |  |  |  | 62.6 |  | 24.6 |  | 9.4 | 0.25 |  | 18.9 | 130.54 | 2.5 |  |  |  |  | 19.414 | 14.273 | [6 empty] | 9.45 | 15.31 | 14.25
2010-09-08 | 6.19 | 6.45 |  |  |  |  | 7.67 | 1.74 |  |  |  |  | 41 |  |  |  | 0 | 1.111 |  |  | 0.213 | 0.437 | [5 empty] | 33.6 |  |  |  |  | 67.2 |  | 23.3 |  | 11.1 | 0.25 |  | 17.8 | 120.28 | 2.15 |  |  |  |  | 19.17 | 14.049 | [6 empty] | 9.45 | 22.96 | 14.25
2010-09-09 | 7.01 | 6.6 |  |  |  |  | 7.62 | 1.71 |  |  |  |  | 36 |  |  |  | 2 | 0.962 |  |  | 0.31 | 0.263 | [5 empty] | 33.7 |  |  |  |  | 67.4 |  | 26.1 |  | 10.7 | 0.25 |  | 17.7 | 119.62 | 2.06 |  |  |  |  | 19.541 | 14.415 | [6 empty] | 9.45 | 30.62 | 13.06
2010-09-10 | 6.62 | 6.67 |  |  |  |  | 7.45 | 1.59 |  |  |  |  | 33 |  |  |  | 4 | 0.796 |  |  | 0.252 | 0.33 | [5 empty] | 30.3 |  |  |  |  | 60.7 |  | 26.4 |  | 10.8 | 0.25 |  | 16.7 | 109.32 | 1.91 |  |  |  |  | 19.318 | 14.166 | [6 empty] | 9.77 | 13.78 | 13.06
2010-09-11 | 6.55 | 6.93 |  |  |  |  | 6.61 | 1.74 |  |  |  |  | 24 |  |  |  | 0 | 0.753 |  |  | 0.43 | 0.439 | [5 empty] | 29.4 |  |  |  |  | 58.8 |  | 26.1 |  | 9.3 | 0.25 |  | 16.6 | 110.01 | 2.04 |  |  |  |  | 18.38 | 13.22 | [6 empty] | 9.77 | 13.28 | 13.06
2010-09-12 | 6.585 | 6.8 |  |  |  |  | 7.03 | 1.665 |  |  |  |  | 28.5 |  |  |  | 2 | 0.7745 |  |  | 0.341 | 0.3845 | [5 empty] | 29.85 |  |  |  |  | 59.75 |  | 26.25 |  | 10.05 | 0.25 |  | 16.65 | 94.84 | 1.61 |  |  |  |  | 17.617 | 13.338 | [6 empty] | 9.77 | 13.78 | 13.06
2010-09-13 | 7.26 | 6.4 |  |  |  |  | 6.64 | 1.79 |  |  |  |  | 41 |  |  |  | 3 | 0.782 |  |  | 0.043 | 0.655 | [5 empty] | 30.5 |  |  |  |  | 61 |  | 25.2 |  | 7.6 | 0.25 |  | 15.4 | 115.39 | 1.96 |  |  |  |  | 19.124 | 13.976 | [6 empty] | 9.77 | 13.78 | 14.25
2010-09-14 | 6.39 | 6.34 |  |  |  |  | 7.55 | 1.84 |  |  |  |  | 34 |  |  |  | 1 | 0.783 |  |  | 0.312 | 0.569 | [5 empty] | 32.7 |  |  |  |  | 65.4 |  | 27.3 |  | 9.1 | 0.168 |  | 15.1 | 129.59 | 1.75 |  |  |  |  | 19.026 | 13.851 | [6 empty] | 10.08 | 28.07 | 13.3
2010-09-15 | 7.11 | 6.17 |  |  |  |  | 7.7 | 1.74 |  |  |  |  | 33 |  |  |  | 0 | 0.582 |  |  | 0.457 | 0.394 | [5 empty] | 31.3 |  |  |  |  | 62.6 |  | 26.5 |  | 8.9 | 0.152 |  | 15.6 | 111.91 | 1.89 |  |  |  |  | 19.197 | 14.007 | [6 empty] | 10.4 | 38.75 | 13.3
2010-09-16 | 6.07 | 6.26 |  |  |  |  | 7.75 | 1.76 |  |  |  |  | 35 |  |  |  | 1 | 0.647 |  |  | 0.416 | 0.385 | [5 empty] | 34.4 |  |  |  |  | 68.8 |  | 25.5 |  | 9.1 | 0.232 |  | 15 | 105.11 | 1.65 |  |  |  |  | 19.174 | 13.978 | [6 empty] | 10.4 | 38.27 | 13.3
2010-09-17 | 6.52 | 6.17 |  |  |  |  | 7.48 | 1.73 |  |  |  |  | 27 |  |  |  | 2 | 0.614 |  |  | 0.743 | 0.263 | [5 empty] | 35.9 |  |  |  |  | 71.8 |  | 26.7 |  | 8.7 | 0.13 |  | 15.5 | 104.6 | 1.56 |  |  |  |  | 19.61 | 14.422 | [6 empty] | 10.72 | 45.93 | 13.3
2010-09-18 | 6.3 | 6.24 |  |  |  |  | 7.63 | 1.82 |  |  |  |  | 38 |  |  |  | 2 | 0.601 |  |  | 0.312 | 0.317 | [5 empty] | 29.8 |  |  |  |  | 59.6 |  | 21.2 |  | 9.2 | 0.143 |  | 15.7 | 120.79 | 1.96 |  |  |  |  | 19.21 | 14.5 | [6 empty] | 10.72 | 45.73 | 13.3
2010-09-19 | 6.41 | 6.205 |  |  |  |  | 7.555 | 1.775 |  |  |  |  | 32.5 |  |  |  | 2 | 0.6075 |  |  | 0.5275 | 0.29 | [5 empty] | 32.85 |  |  |  |  | 65.7 |  | 23.95 |  | 8.95 | 0.1365 |  | 15.6 | 112.695 | 1.76 |  |  |  |  | 19.41 | 14.461 | [6 empty] | 10.72 | 45.83 | 13.3
2010-09-20 | 6.97 | 6.32 |  |  |  |  | 7.11 | 1.8 |  |  |  |  | 35 |  |  |  | 0 | 0.511 |  |  | 0.904 | 0.342 | [5 empty] | 34.1 |  |  |  |  | 68.3 |  | 23.2 |  | 9.8 | 0.151 |  | 14.8 | 110.21 | 1.76 |  |  |  |  | 19.239 | 14.057 | [6 empty] | 10.72 | 45.93 | 11.86
2010-09-21 | 6.29 | 6.48 |  |  |  |  | 7.09 | 1.65 |  |  |  |  | 46 |  |  |  | 0 | 0.596 |  |  | 0.804 | 0.53 | [5 empty] | 34.4 |  |  |  |  | 68.8 |  | 24.5 |  | 10.6 | 0.156 |  | 14.2 | 100.17 | 1.62 |  |  |  |  | 19.034 | 13.904 | [6 empty] | 10.72 | 45.93 | 11.86
2010-09-22 | 6.7 | 5.98 |  |  |  |  | 7.48 | 1.41 |  |  |  |  | 54 |  |  |  | 7 | 0.717 |  |  | 0.972 | 1.126 | [5 empty] | 29 |  |  |  |  | 58 |  | 21.6 |  | 10 | 0.175 |  | 13.9 | 110.49 | 2.02 |  |  |  |  | 19.615 | 14.606 | [6 empty] | 10.72 | 25.51 | 11.86
2010-09-23 | 5.9 | 6.68 |  |  |  |  | 7.02 | 1.66 |  |  |  |  | 68 |  |  |  | 5 | 0.71 |  |  | 1.19 | 1.089 | [5 empty] | 30.5 |  |  |  |  | 61 |  | 22.2 |  | 8.2 | 0.174 |  | 14.2 | 113.2 | 2.12 |  |  |  |  | 18.909 | 13.597 | [6 empty] | 10.72 | 30.62 | 11.86
2010-09-24 | 6.15 | 6.36 |  |  |  |  | 7.52 | 1.59 |  |  |  |  | 53 |  |  |  | 4 | 0.671 |  |  | 0.586 | 0.558 | [5 empty] | 31.9 |  |  |  |  | 63.8 |  | 23.2 |  | 8.4 | 0.222 |  | 13 | 115.78 | 2.21 |  |  |  |  | 19.112 | 13.846 | [6 empty] | 10.72 | 33.17 | 13.06
2010-09-25 | 7.09 | 6.74 |  |  |  |  | 7.07 | 1.5 |  |  |  |  | 51 |  |  |  | 4 | 0.674 |  |  | 0.412 | 0.77 | [5 empty] | 29.9 |  |  |  |  | 59.8 |  | 24.1 |  | 8.6 | 0.25 |  | 13.2 | 116.87 | 2.37 |  |  |  |  | 18.728 | 13.694 | [6 empty] | 9.11 | 35.72 | 13.06
2010-09-26 | 6.62 | 6.55 |  |  |  |  | 7.295 | 1.7 |  |  |  |  | 52 |  |  |  | 4 | 0.6725 |  |  | 0.499 | 0.664 | [5 empty] | 30.9 |  |  |  |  | 61.8 |  | 23.65 |  | 8.5 | 0.236 |  | 13.1 | 114.66 | 2.18 |  |  |  |  | 18.5 | 13.43 | [6 empty] | 12.3 | 38.27 | 14.25
2010-09-27 | 6.855 | 6.645 |  |  |  |  | 7.1825 | 1.59 |  |  |  |  | 51.5 |  |  |  | 4 | 0.67325 |  |  | 0.4555 | 0.717 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 23.875 |  | 8.55 | 0.243 |  | 13.15 | 110.25 | 1.98 |  |  |  |  | 18.76 | 14 | [6 empty] | 12.3 | 38.27 | 14.25
2010-09-28 | 6.7375 | 6.5975 |  |  |  |  | 7.2387 | 1.81 |  |  |  |  | 51.75 |  |  |  | 4 | 0.67288 |  |  | 0.47725 | 0.6905 | [5 empty] | 30.65 |  |  |  |  | 61.3 |  | 23.7625 |  | 8.525 | 0.2395 |  | 13.125 | 116.07 | 2.04 |  |  |  |  | 19.2 | 13.69 | [6 empty] | 12.3 | 38.27 | 14.25
2010-09-29 | 6.17 | 6.64 |  |  |  |  | 7.07 | 1.65 |  |  |  |  | 46 |  |  |  | 3 | 0.614 |  |  | 0.513 | 0.588 | [5 empty] | 31.8 |  |  |  |  | 63.6 |  | 25.5 |  | 8.2 | 0.134 |  | 12.8 | 105.84 | 1.8 |  |  |  |  | 18.972 | 13.933 | [6 empty] | 12.3 | 45.93 | 11.86
2010-09-30 | 7.4 | 6.59 |  |  |  |  | 6.61 | 1.49 |  |  |  |  | 53 |  |  |  | 1 | 0.641 |  |  | 0.561 | 0.343 | [5 empty] | 32.5 |  |  |  |  | 65 |  | 24.6 |  | 9.9 | 0.25 |  | 13.1 | 109.85 | 2.11 |  |  |  |  | 18.906 | 13.835 | [6 empty] | 11.51 | 43.38 | 13.06
2010-10-01 | 6.785 | 6.7 |  |  |  |  | 6.94 | 1.4 |  |  |  |  | 48 |  |  |  | 4 | 0.585 |  |  | 0.527 | 0.464 | [5 empty] | 34.5 |  |  |  |  | 69 |  | 23.6 |  | 10.3 | 0.25 |  | 13.3 | 105.09 | 2.03 |  |  |  |  | 18.957 | 13.927 | [6 empty] | 13.1 | 35.72 | 14.25
2010-10-02 | 6.65 | 6.67 |  |  |  |  | 7.57 | 1.51 |  |  |  |  | 51 |  |  |  | 0 | 0.794 |  |  | 0.575 | 0.316 | [5 empty] | 30.2 |  |  |  |  | 60.3 |  | 23.4 |  | 10.2 | 0.25 |  | 14.2 | 123.49 | 2.5 |  |  |  |  | 18.98 | 13.98 | [6 empty] | 11.96 | 30.62 | 11.86
2010-10-03 | 6.7175 | 6.685 |  |  |  |  | 7.255 | 1.455 |  |  |  |  | 49.5 |  |  |  | 2 | 0.6895 |  |  | 0.551 | 0.39 | [5 empty] | 32.35 |  |  |  |  | 64.65 |  | 23.5 |  | 10.25 | 0.25 |  | 13.75 | 110.25 | 2.18 |  |  |  |  | 17.839 | 13.354 | [6 empty] | 11.96 | 30.62 | 11.86
2010-10-04 | 6.32 | 6.41 |  |  |  |  | 6.45 | 1.33 |  |  |  |  | 54 |  |  |  | 2 | 0.861 |  |  | 0.43 | 0.729 | [5 empty] | 35.4 |  |  |  |  | 70.8 |  | 23.9 |  | 7.5 | 0.25 |  | 14.5 | 120.7 | 2.47 |  |  |  |  | 19.645 | 14.44 | [6 empty] | 13.1 | 30.62 | 14.25
2010-10-05 | 6.35 | 6.39 |  |  |  |  | 7.02 | 1.35 |  |  |  |  | 54 |  |  |  | 3 | 0.725 |  |  | 0.836 | 0.294 | [5 empty] | 29.9 |  |  |  |  | 59.8 |  | 24.7 |  | 8.6 | 0.137 |  | 14.2 | 119.29 | 2.54 |  |  |  |  | 18.997 | 13.937 | [6 empty] | 6.75 | 35.72 | 12.34
2010-10-06 | 6.6 | 6.52 |  |  |  |  | 6.91 | 1.56 |  |  |  |  | 49 |  |  |  | 0 | 0.824 |  |  | 0.656 | 0.226 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 22.7 |  | 9.5 | 0.237 |  | 13.8 | 116.87 | 2.25 |  |  |  |  | 19.011 | 13.937 | [6 empty] | 8.72 | 35.72 | 12.34
2010-10-07 | 6.68 | 6.35 |  |  |  |  | 7.12 | 1.71 |  |  |  |  | 53 |  |  |  | 0 | 0.652 |  |  | 0.359 | 0.34 | [5 empty] | 27.4 |  |  |  |  | 54.9 |  | 23.3 |  | 9.8 | 0.158 |  | 13.5 | 116.87 | 2.12 |  |  |  |  | 18.946 | 13.871 | [6 empty] | 8.81 | 35.72 | 9.95
2010-10-08 | 6.59 | 6.47 |  |  |  |  | 7.74 | 1.64 |  |  |  |  | 50 |  |  |  | 1 | 0.873 |  |  | 0.55 | 0.378 | [5 empty] | 28.8 |  |  |  |  | 57.8 |  | 22.2 |  | 9.9 | 0.099 |  | 13.7 | 114.86 | 2.1 |  |  |  |  | 18.996 | 13.934 | [6 empty] | 8.5 | 35.72 | 9.95
2010-10-09 | 6.85 | 6.38 |  |  |  |  | 7.17 | 1.63 |  |  |  |  | 54 |  |  |  | 0 | 0.744 |  |  | 0.41 | 0.387 | [5 empty] | 31.2 |  |  |  |  | 62.4 |  | 24.5 |  | 9 | 0.101 |  | 13.3 | 115.23 | 2.25 |  |  |  |  | 18.55 | 13.5 | [6 empty] | 8.02 | 35.72 | 9.95
2010-10-10 | 7.01 | 6.8 |  |  |  |  | 7.16 | 1.58 |  |  |  |  | 39 |  |  |  | 1 | 0.75 |  |  | 0.68 | 0.393 | [5 empty] | 24.2 |  |  |  |  | 48.4 |  | 21.7 |  | 9.3 | 0.229 |  | 11.8 | 110.25 | 2.09 |  |  |  |  | 18.71 | 13.657 | [6 empty] | 7.69 | 29.6 | 9.95
2010-10-11 | 6.93 | 6.59 |  |  |  |  | 7.165 | 1.605 |  |  |  |  | 46.5 |  |  |  | 0.5 | 0.747 |  |  | 0.545 | 0.39 | [5 empty] | 27.7 |  |  |  |  | 55.4 |  | 23.1 |  | 9.15 | 0.165 |  | 12.55 | 112.74 | 2.17 |  |  |  |  | 18.63 | 13.5785 | [6 empty] | 7.855 | 32.66 | 9.95
2010-10-12 | 7.17 | 6.98 |  |  |  |  | 7.18 | 1.61 |  |  |  |  | 42 |  |  |  | 0 | 0.674 |  |  | 0.56 | 0.435 | [5 empty] | 27.1 |  |  |  |  | 54.1 |  | 23.4 |  | 10.1 | 0.211 |  | 11.7 | 114.42 | 2.12 |  |  |  |  | 18.971 | 13.926 | [6 empty] | 7.69 | 27.56 | 9.95
2010-10-13 | 6.64 | 6.99 |  |  |  |  | 7.37 | 1.55 |  |  |  |  | 50 |  |  |  | 2 | 0.671 |  |  | 0.241 | 0.474 | [5 empty] | 27.1 |  |  |  |  | 54.2 |  | 23.9 |  | 9.4 | 0.244 |  | 11.8 | 94.9 | 1.52 |  |  |  |  | 19.079 | 14.018 | [6 empty] | 6.84 | 35.72 | 9.95
2010-10-14 | 6.85 | 6.58 |  |  |  |  | 7.18 | 1.59 |  |  |  |  | 51 |  |  |  | 3 | 0.669 |  |  | 0.477 | 0.355 | [5 empty] | 27.3 |  |  |  |  | 54.7 |  | 26.4 |  | 9.7 | 0.052 |  | 11.8 | 116.86 | 2.19 |  |  |  |  | 19.081 | 14.022 | [6 empty] | 7.69 | 33.17 | 9.95
2010-10-15 | 6.6 | 6.48 |  |  |  |  | 7.14 | 1.68 |  |  |  |  | 43 |  |  |  | 0 | 0.697 |  |  | 0.399 | 0.412 | [5 empty] | 27.2 |  |  |  |  | 54.4 |  | 25.9 |  | 7.3 | 0.061 |  | 11.1 | 109.99 | 1.92 |  |  |  |  | 18.937 | 13.272 | [6 empty] | 7.69 | 31.64 | 9.95
2010-10-16 | 6.24 | 5.89 |  |  |  |  | 7.06 | 1.51 |  |  |  |  | 53 |  |  |  | 2 | 0.554 |  |  | 0.413 | 0.411 | [5 empty] | 26.9 |  |  |  |  | 53.8 |  | 26.8 |  | 5.6 | 0.045 |  | 10.9 | 114.91 | 2.12 |  |  |  |  | 19.38 | 14.37 | [6 empty] | 7.69 | 35.72 | 9.95
2010-10-17 | 6.42 | 6.185 |  |  |  |  | 7.1 | 1.595 |  |  |  |  | 48 |  |  |  | 1 | 0.6255 |  |  | 0.406 | 0.4115 | [5 empty] | 27.05 |  |  |  |  | 54.1 |  | 26.35 |  | 6.45 | 0.053 |  | 11 | 100.11 | 1.87 |  |  |  |  | 18.23 | 13.223 | [6 empty] | 7.69 | 38.27 | 11.38
2010-10-18 | 6.6 | 6.69 |  |  |  |  | 6.86 | 1.51 |  |  |  |  | 51 |  |  |  | 0 | 0.542 |  |  | 0.495 | 0.226 | [5 empty] | 29.5 |  |  |  |  | 59 |  | 26.3 |  | 11 | 0.174 |  | 11.8 | 111.44 | 2.12 |  |  |  |  | 18.978 | 13.933 | [6 empty] | 7.69 | 38.27 | 11.38
2010-10-19 | 6.49 | 6.04 |  |  |  |  | 6.91 | 1.46 |  |  |  |  | 47 |  |  |  | 3 | 0.793 |  |  | 0.694 | 0.344 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 23.3 |  | 9.1 | 0.071 |  | 11.6 | 94.82 | 1.83 |  |  |  |  | 19.683 | 13.068 | [6 empty] | 7.69 | 35.72 | 10.18
2010-10-20 | 6.49 | 6.02 |  |  |  |  | 7.17 | 1.69 |  |  |  |  | 44 |  |  |  | 2 | 0.655 |  |  | 0.631 | 0.453 | [5 empty] | 25.3 |  |  |  |  | 50.6 |  | 24.8 |  | 5.5 | 0.104 |  | 10.3 | 115.32 | 2.12 |  |  |  |  | 16.61 | 13.745 | [6 empty] | 7.69 | 35.72 | 9.47
2010-10-21 | 6.49 | 6.03 |  |  |  |  | 7.04 | 1.575 |  |  |  |  | 45.5 |  |  |  | 2.5 | 0.724 |  |  | 0.6625 | 0.3985 | [5 empty] | 26.35 |  |  |  |  | 52.7 |  | 24.05 |  | 7.3 | 0.0875 |  | 10.95 | 105.07 | 1.975 |  |  |  |  | 18.1465 | 13.4065 | [6 empty] | 7.69 | 35.72 | 9.825
2010-10-22 | 7.42 | 6.02 |  |  |  |  | 7 | 1.55 |  |  |  |  | 42 |  |  |  | 1 | 0.635 |  |  | 0.652 | 0.469 | [5 empty] | 27.6 |  |  |  |  | 55.3 |  | 23.1 |  | 7.8 | 0.17 |  | 10.3 | 110.25 | 2.12 |  |  |  |  | 14.97 | 13.626 | [6 empty] | 7.69 | 38.27 | 9.47
2010-10-23 | 7.04 | 6.38 |  |  |  |  | 7.15 | 1.66 |  |  |  |  | 41 |  |  |  | 0 | 0.805 |  |  | 0.644 | 0.338 | [5 empty] | 29.9 |  |  |  |  | 59.8 |  | 22.8 |  | 8.2 | 0.155 |  | 10.8 | 110.25 | 2.1 |  |  |  |  | 14.67 | 13.3 | [6 empty] | 7.69 | 38.27 | 10.66
2010-10-24 | 7.23 | 6.2 |  |  |  |  | 7.075 | 1.605 |  |  |  |  | 41.5 |  |  |  | 0.5 | 0.72 |  |  | 0.648 | 0.4035 | [5 empty] | 28.75 |  |  |  |  | 57.55 |  | 22.95 |  | 8 | 0.1625 |  | 10.55 | 105.84 | 1.98 |  |  |  |  | 15.402 | 13.477 | [6 empty] | 7.69 | 38.27 | 10.66
2010-10-25 | 5.61 | 6.51 |  |  |  |  | 7.64 | 1.61 |  |  |  |  | 58 |  |  |  | 4 | 0.584 |  |  | 0.0641 | 0.647 | [5 empty] | 29 |  |  |  |  | 58 |  | 25.8 |  | 6.3 | 0.155 |  | 10 | 115.37 | 2.17 |  |  |  |  | 15.261 | 13.916 | [6 empty] | 7.69 | 38.27 | 9.95
2010-10-26 | 7.05 | 6.56 |  |  |  |  | 7.2 | 1.62 |  |  |  |  | 46 |  |  |  | 2 | 0.565 |  |  | 0.541 | 0.1694 | [5 empty] | 28.5 |  |  |  |  | 57 |  | 25.8 |  | 9.2 | 0.204 |  | 9.4 | 104.56 | 1.96 |  |  |  |  | 14.46 | 13.27 | [6 empty] | 10.72 | 28.07 | 13.06
2010-10-27 | 6.75 | 6.28 |  |  |  |  | 7.22 | 1.67 |  |  |  |  | 53 |  |  |  | 0 | 0.791 |  |  | 0.684 | 0.36 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 23.6 |  | 9.7 | 0.25 |  | 9.2 | 116.87 | 2.11 |  |  |  |  | 15.006 | 14.052 | [6 empty] | 28.07 | 43.38 | 11.86
2010-10-28 | 6.68 | 6.32 |  |  |  |  | 6.8 | 1.52 |  |  |  |  | 46 |  |  |  | 2 | 0.702 |  |  | 0.761 | 0.364 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 21.5 |  | 10.7 | 0.25 |  | 8.9 | 110.25 | 2.59 |  |  |  |  | 14.871 | 13.85 | [6 empty] | 28.07 | 33.17 | 11.86
2010-10-29 | 6.43 | 6.51 |  |  |  |  | 7.16 | 1.78 |  |  |  |  | 54 |  |  |  | 1 | 0.81 |  |  | 0.596 | 0.375 | [5 empty] | 27.2 |  |  |  |  | 54.4 |  | 13.1 |  | 9.7 | 0.132 |  | 10 | 110.76 | 1.85 |  |  |  |  | 14.874 | 13.843 | [6 empty] | 28.07 | 35.72 | 11.86
2010-10-30 | 5.98 | 6.11 |  |  |  |  | 7.33 | 1.61 |  |  |  |  | 58 |  |  |  | 4 | 1.149 |  |  | 0.641 | 0.625 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 15.9 |  | 9.9 | 0.137 |  | 10.1 | 110.21 | 2.14 |  |  |  |  | 14.6 | 13.33 | [6 empty] | 8.67 | 40.82 | 11.86
2010-10-31 | 6.205 | 6.31 |  |  |  |  | 7.245 | 1.695 |  |  |  |  | 56 |  |  |  | 2.5 | 0.9795 |  |  | 0.6185 | 0.5 | [5 empty] | 27.8 |  |  |  |  | 55.6 |  | 14.5 |  | 9.8 | 0.1345 |  | 10.05 | 110.485 | 1.995 |  |  |  |  | 14.737 | 13.5865 | [6 empty] | 18.37 | 38.27 | 11.86
2010-11-01 | 7.22 | 6 |  |  |  |  | 7.75 | 1.5 |  |  |  |  | 42 |  |  |  | 3 | 1.164 |  |  | 0.787 | 0.317 | [5 empty] | 34.4 |  |  |  |  | 68.9 |  | 33.6 |  | 9.6 | 0.09225 |  | 9.1 | 93.13 | 1.4475 |  |  |  |  | 15.814 | 13.297 | [6 empty] | 10.37 | 48.48 | 15.4
2010-11-02 | 6.61 | 6.8 |  |  |  |  | 7.34 | 1.86 |  |  |  |  | 43 |  |  |  | 2 | 1.474 |  |  | 0.338 | 0.52 | [5 empty] | 28.5 |  |  |  |  | 57 |  | 28.4 |  | 8 | 0.0915 |  | 8.8 | 91.49 | 1.185 |  |  |  |  | 15.274 | 13.721 | [6 empty] | 8.66 | 40.82 | 10.61
2010-11-03 | 6.77 | 6.47 |  |  |  |  | 7.26 | 1.56 |  |  |  |  | 47 |  |  |  | 3 | 0.955 |  |  | 0.549 | 0.628 | [5 empty] | 30.2 |  |  |  |  | 60.4 |  | 29.9 |  | 7.2 | 0.093 |  | 9.1 | 94.77 | 1.71 |  |  |  |  | 14.195 | 13.152 | [6 empty] | 8.66 | 42.35 | 10.61
2010-11-04 | 6.3 | 5.85 |  |  |  |  | 7.41 | 2.14 |  |  |  |  | 46 |  |  |  | 0 | 0.718 |  |  | 0.384 | 0.593 | [5 empty] | 28.7 |  |  |  |  | 57.5 |  | 30.4 |  | 7.6 | 0.09 |  | 9.2 | 88.21 | 0.66 |  |  |  |  | 15.272 | 14.293 | [6 empty] | 8.66 | 42.35 | 10.61
2010-11-05 | 5.78 | 6.29 |  |  |  |  | 7.54 | 1.47 |  |  |  |  | 45 |  |  |  | 3 | 0.834 |  |  | 0.369 | 0.756 | [5 empty] | 27.3 |  |  |  |  | 54.6 |  | 28.5 |  | 4.4 | 0.072 |  | 8.8 | 97.02 | 1.72 |  |  |  |  | 14.747 | 13.799 | [6 empty] | 8.66 | 42.35 | 9.41
2010-11-06 | 6.12 | 5.62 |  |  |  |  | 7.5 | 1.63 |  |  |  |  | 74 |  |  |  | 0 | 1.668 |  |  | 0.597 | 0.382 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 28.2 |  | 8.5 | 0.173 |  | 8.1 | 100.22 | 1.74 |  |  |  |  | 15.21 | 13.49 | [6 empty] | 9.13 | 43.28 | 13
2010-11-07 | 5.95 | 5.955 |  |  |  |  | 7.52 | 1.36 |  |  |  |  | 59.5 |  |  |  | 1.5 | 1.251 |  |  | 0.483 | 0.569 | [5 empty] | 28.25 |  |  |  |  | 56.5 |  | 28.35 |  | 6.45 | 0.1225 |  | 8.45 | 85 | 1.64 |  |  |  |  | 14.198 | 12.877 | [6 empty] | 9.13 | 43.38 | 13
2010-11-08 | 6.01 | 6.35 |  |  |  |  | 7.13 | 1.45 |  |  |  |  | 58 |  |  |  | 4 | 2.179 |  |  | 0.686 | 0.494 | [5 empty] | 31.6 |  |  |  |  | 63.2 |  | 24.5 |  | 7.9 | 0.181 |  | 10.2 | 95.34 | 1.74 |  |  |  |  | 14.934 | 13.573 | [6 empty] | 9.13 | 48.48 | 14.2
2010-11-09 | 6.18 | 6.19 |  |  |  |  | 7.46 | 1.41 |  |  |  |  | 57 |  |  |  | 1 | 1.667 |  |  | 0.2 | 0.724 | [5 empty] | 33.7 |  |  |  |  | 67.4 |  | 29.7 |  | 8.7 | 0.152 |  | 10.4 | 99.23 | 1.98 |  |  |  |  | 14.436 | 13.289 | [6 empty] | 6.75 | 48.48 | 14.2
2010-11-10 | 6.18 | 6.02 |  |  |  |  | 7.02 | 1.47 |  |  |  |  | 46 |  |  |  | 2 | 1.426 |  |  | 0.275 | 0.631 | [5 empty] | 31.8 |  |  |  |  | 63.6 |  | 28.5 |  | 5.6 | 0.153 |  | 9.7 | 104.21 | 1.94 |  |  |  |  | 14.918 | 13.868 | [6 empty] | 5.17 | 51.03 | 12.52
2010-11-11 | 6.11 | 6.31 |  |  |  |  | 6.95 | 1.46 |  |  |  |  | 54 |  |  |  | 1 | 1.784 |  |  | 0.253 | 0.482 | [5 empty] | 30.8 |  |  |  |  | 61.6 |  | 29.3 |  | 7.15 | 0.128 |  | 9.4 | 94.48 | 1.82 |  |  |  |  | 14.051 | 13.091 | [6 empty] | 5.17 | 51.03 | 14.2
2010-11-12 | 7.25 | 6.35 |  |  |  |  | 7.21 | 1.52 |  |  |  |  | 44 |  |  |  | 0 | 1.333 |  |  | 0.292 | 0.497 | [5 empty] | 31.1 |  |  |  |  | 62.3 |  | 26.4 |  | 8.1 | 0.134 |  | 8.8 | 101.44 | 1.81 |  |  |  |  | 14.895 | 13.85 | [6 empty] | 5.17 | 51.03 | 14.68
2010-11-13 | 7.17 | 6.46 |  |  |  |  | 7.2 | 1.53 |  |  |  |  | 41 |  |  |  | 0 | 0.757 |  |  | 0.33 | 0.446 | [5 empty] | 30.5 |  |  |  |  | 61 |  | 24.8 |  | 7.6 | 0.199 |  | 9.2 | 99.23 | 2.03 |  |  |  |  | 14.03 | 12.66 | [6 empty] | 5.17 | 51.03 | 13.48
2010-11-14 | 7.21 | 6.405 |  |  |  |  | 7.205 | 1.525 |  |  |  |  | 42.5 |  |  |  | 0 | 1.045 |  |  | 0.311 | 0.4715 | [5 empty] | 30.8 |  |  |  |  | 61.65 |  | 25.6 |  | 7.85 | 0.1665 |  | 9 | 90.41 | 2.03 |  |  |  |  | 13.803 | 12.419 | [6 empty] | 5.17 | 51.03 | 11.81
2010-11-15 | 5.75 | 6.31 |  |  |  |  | 7.2025 | 1.09 |  |  |  |  | 53 |  |  |  | 4 | 0.848 |  |  | 0.241 | 0.819 | [5 empty] | 24 |  |  |  |  | 48 |  | 25.8 |  | 7.725 | 0.168 |  | 9 | 106.15 | 2.52 |  |  |  |  | 14.75 | 13.293 | [6 empty] | 5.17 | 51.03 | 11.81
2010-11-16 | 6 | 5.94 |  |  |  |  | 7.12 | 1.62 |  |  |  |  | 44 |  |  |  | 2 | 1.1 |  |  | 0.389 | 0.337 | [5 empty] | 23.8 |  |  |  |  | 47.6 |  | 25.5 |  | 6.7 | 0.167 |  | 7.7 | 100.02 | 1.72 |  |  |  |  | 14.549 | 13.589 | [6 empty] | 7.55 | 51.03 | 11.81
2010-11-17 | 6.34 | 5.85 |  |  |  |  | 6.77 | 1.86 |  |  |  |  | 43 |  |  |  | 2 | 0.752 |  |  | 0.446 | 0.447 | [5 empty] | 29 |  |  |  |  | 58.1 |  | 22.4 |  | 8.2 | 0.154 |  | 7.8 | 116.87 | 1.91 |  |  |  |  | 15.874 | 14.074 | [6 empty] | 22.53 | 4.81 | 9.04
2010-11-18 | 6.35 | 6.22 |  |  |  |  | 7.24 | 1.81 |  |  |  |  | 44 |  |  |  | 0 | 1.319 |  |  | 0.775 | 0.451 | [5 empty] | 29.1 |  |  |  |  | 58.2 |  | 21.8 |  | 8.8 | 0.151 |  | 8.1 | 103.64 | 1.61 |  |  |  |  | 14.964 | 13.677 | [6 empty] | 23 | 13.74 | 9.04
2010-11-19 | 6.8 | 6.6 |  |  |  |  | 7.02 | 1.77 |  |  |  |  | 49 |  |  |  | 3 | 1.46 |  |  | 0.6 | 0.463 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 21.6 |  | 8.3 | 0.048 |  | 7.8 | 88.53 | 1 |  |  |  |  | 14.98 | 14.484 | [6 empty] | 26.25 | 12.93 | 8.43
2010-11-20 | 6.34 | 6.75 |  |  |  |  | 7.01 | 1.79 |  |  |  |  | 48 |  |  |  | 3 | 1.24 |  |  | 0.498 | 0.669 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 22.1 |  | 8.1 | 0.098 |  | 7.9 | 96.085 | 1.305 |  |  |  |  | 14.972 | 14.0805 | [6 empty] | 29.87 | 11.48 | 8.99
2010-11-21 | 6.57 | 6.675 |  |  |  |  | 7.015 | 1.78 |  |  |  |  | 48.5 |  |  |  | 3 | 1.35 |  |  | 0.549 | 0.566 | [5 empty] | 28.8 |  |  |  |  | 57.6 |  | 21.85 |  | 8.2 | 0.073 |  | 7.85 | 92.3075 | 1.1525 |  |  |  |  | 14.976 | 14.2823 | [6 empty] | 28.06 | 12.205 | 8.71
2010-11-22 | 6.79 | 7.16 |  |  |  |  | 8.59 | 1.785 |  |  |  |  | 45 |  |  |  | 8 | 1.244 |  |  | 2.29 | 0.415 | [5 empty] | 25.4 |  |  |  |  | 50.8 |  | 25.6 |  | 9.9 | 0.086 |  | 6 | 94.1963 | 1.2288 |  |  |  |  | 14.974 | 14.1814 | [6 empty] | 22.16 | 16.26 | 8.77
2010-11-23 | 6.39 | 6.85 |  |  |  |  | 7.2 | 1.7825 |  |  |  |  | 48 |  |  |  | 4 | 1.608 |  |  | 0.605 | 0.865 | [5 empty] | 32 |  |  |  |  | 64 |  | 29.1 |  | 12.4 | 0.104 |  | 6.5 | 160 | 1.1906 |  |  |  |  | 14.975 | 14.2318 | [6 empty] | 37.9 | 17.69 | 8.58
2010-11-24 | 6.6 | 6.83 |  |  |  |  | 7.34 | 1.7838 |  |  |  |  | 38 |  |  |  | 4 | 0.98 |  |  | 0.89 | 0.876 | [5 empty] | 25.4 |  |  |  |  | 50.8 |  | 24.1 |  | 7.9 | 0.083 |  | 5.6 | 140 | 1.2097 |  |  |  |  | 14.9745 | 14.2066 | [6 empty] | 29.59 | 19.63 | 6.65
2010-11-25 | 6.59 | 6.8 |  |  |  |  | 7.54 | 1.7831 |  |  |  |  | 43 |  |  |  | 3 | 0.7 |  |  | 0.946 | 0.695 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 22.3 |  | 9 | 0.119 |  | 5.5 | 130 | 1.2002 |  |  |  |  | 14.9748 | 14.2192 | [6 empty] | 26.59 | 16.53 | 5.85
2010-11-26 | 5.14 | 6.86 |  |  |  |  | 7.28 | 1.7834 |  |  |  |  | 40 |  |  |  | 0 | 0.715 |  |  | 0.781 | 1.003 | [5 empty] | 29.9 |  |  |  |  | 59.8 |  | 17.1 |  | 5.8 | 0.25 |  | 5.5 | 135 | 1.2049 |  |  |  |  | 14.9746 | 14.2129 | [6 empty] | 30.78 | 23.8 | 8.15
2010-11-27 | 5.95 | 5.93 |  |  |  |  | 6.64 | 1.7833 |  |  |  |  | 40 |  |  |  | 3 | 0.625 |  |  | 0.567 | 0.704 | [5 empty] | 33.7 |  |  |  |  | 67.4 |  | 16.2 |  | 7.6 | 0.198 |  | 5.1 | 132.5 | 1.2025 |  |  |  |  | 14.9747 | 14.2161 | [6 empty] | 30.59 | 18.22 | 7.22
2010-11-28 | 5.9 | 6.74 |  |  |  |  | 7.36 | 1.62 |  |  |  |  | 53 |  |  |  | 6 | 1.225 |  |  | 0.876 | 1.039 | [5 empty] | 25.4 |  |  |  |  | 50.8 |  | 18.2 |  | 6.9 | 0.113 |  | 5.8 | 99.8 | 1.35 |  |  |  |  | 16.793 | 15.233 | [6 empty] | 38.72 | 4.7 | 10.77
2010-11-29 | 7.16 | 5.99 |  |  |  |  | 6.53 | 2.04 |  |  |  |  | 49 |  |  |  | 1 | 0.616 |  |  | 0.87 | 0.505 | [5 empty] | 32 |  |  |  |  | 64.1 |  | 20.7 |  | 7.9 | 0.098 |  | 6.3 | 104.63 | 1.32 |  |  |  |  | 15.726 | 14.127 | [6 empty] | 25.13 | 13.73 | 6.1
2010-11-30 | 7.17 | 6.74 |  |  |  |  | 7.68 | 1.72 |  |  |  |  | 43 |  |  |  | 0 | 0.82 |  |  | 0.709 | 0.235 | [5 empty] | 33 |  |  |  |  | 66.1 |  | 20 |  | 8.7 | 0.084 |  | 6 | 99.23 | 1.66 |  |  |  |  | 14.506 | 13.347 | [6 empty] | 26.66 | 9.31 | 15.67
2010-12-01 | 6.29 | 6.77 |  |  |  |  | 8.02 | 1.55 |  |  |  |  | 37 |  |  |  | 1 | 0.893 |  |  | 0.811 | 0.489 | [5 empty] | 29.9 |  |  |  |  | 59.8 |  | 19.2 |  | 8.2 | 0.171 |  | 5.1 | 94.77 | 1.46 |  |  |  |  | 15.002 | 14.302 | [6 empty] | 26.01 | 9.91 | 11.24
2010-12-02 | 5.93 | 6.42 |  |  |  |  | 7.44 | 1.47 |  |  |  |  | 44 |  |  |  | 1 | 1.74 |  |  | 0.641 | 0.493 | [5 empty] | 29 |  |  |  |  | 58 |  | 19.5 |  | 9.1 | 0.172 |  | 4.8 | 90.96 | 1.58 |  |  |  |  | 14.708 | 13.549 | [6 empty] | 25.93 | 11.28 | 11.57
2010-12-03 | 6.64 | 6.6 |  |  |  |  | 7.37 | 1.68 |  |  |  |  | 39 |  |  |  | 0 | 1.789 |  |  | 0.685 | 0.289 | [5 empty] | 36 |  |  |  |  | 71.9 |  | 40.4 |  | 12.9 | 0.193 |  | 5.2 | 104.12 | 1.62 |  |  |  |  | 15.066 | 14.335 | [6 empty] | 23.47 | 13.96 | 16.09
2010-12-04 | 6.62 | 6.82 |  |  |  |  | 7.46 | 1.81 |  |  |  |  | 38 |  |  |  | 0 | 1.593 |  |  | 0.663 | 0.335 | [5 empty] | 32.5 |  |  |  |  | 64.95 |  | 29.95 |  | 11 | 0.1825 |  | 5 | 97.54 | 1.6 |  |  |  |  | 14.89 | 13.38 | [6 empty] | 24.7 | 12.62 | 13.83
2010-12-05 | 6.58 | 6.91 |  |  |  |  | 7.48 | 1.54 |  |  |  |  | 41.5 |  |  |  | 0 | 1.2555 |  |  | 0.674 | 0.529 | [5 empty] | 34.25 |  |  |  |  | 68.425 |  | 35.175 |  | 11.95 | 0.18775 |  | 5.1 | 100.83 | 1.61 |  |  |  |  | 14.7625 | 13.5395 | [6 empty] | 24.085 | 13.29 | 14.96
2010-12-06 | 6.54 | 7 |  |  |  |  | 7.5 | 1.27 |  |  |  |  | 45 |  |  |  | 0 | 0.918 |  |  | 1.04 | 0.723 | [5 empty] | 28.5 |  |  |  |  | 57 |  | 26.7 |  | 8.5 | 0.135 |  | 5.6 | 94.93 | 1.88 |  |  |  |  | 14.635 | 13.699 | [6 empty] | 23.47 | 13.37 | 8.5
2010-12-07 | 7 | 6.08 |  |  |  |  | 7.17 | 1.31 |  |  |  |  | 40 |  |  |  | 3 | 0.739 |  |  | 0.758 | 0.735 | [5 empty] | 30 |  |  |  |  | 60 |  | 25.6 |  | 9.2 | 0.137 |  | 6 | 105.6 | 2.26 |  |  |  |  | 14.604 | 13.442 | [6 empty] | 23 | 13.88 | 8.68
2010-12-08 | 6.65 | 6.94 |  |  |  |  | 7.68 | 1.47 |  |  |  |  | 40 |  |  |  | 0 | 1.3 |  |  | 0.796 | 0.612 | [5 empty] | 28.2 |  |  |  |  | 56.5 |  | 26.1 |  | 10.3 | 0.148 |  | 6.1 | 99.31 | 1.8 |  |  |  |  | 14.928 | 13.773 | [6 empty] | 19.25 | 14.2 | 9.29
2010-12-09 | 6.63 | 6.29 |  |  |  |  | 7.13 | 1.53 |  |  |  |  | 39 |  |  |  | 1 | 0.939 |  |  | 0.824 | 0.596 | [5 empty] | 26.9 |  |  |  |  | 53.8 |  | 23.6 |  | 7.8 | 0.182 |  | 6 | 100.72 | 1.85 |  |  |  |  | 15.14 | 13.524 | [6 empty] | 22.53 | 13.28 | 7.68
2010-12-10 | 6.67 | 6.36 |  |  |  |  | 7.18 | 1.82 |  |  |  |  | 37 |  |  |  | 0 | 1.493 |  |  | 0.753 | 0.607 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 23.4 |  | 9 | 0.137 |  | 6.3 | 100.9 | 1.52 |  |  |  |  | 14.393 | 13.702 | [6 empty] | 25.18 | 13.54 | 7.28
2010-12-11 | 6.71 | 6.43 |  |  |  |  | 7.91 | 1.65 |  |  |  |  | 43 |  |  |  | 1 | 1.317 |  |  | 0.54 | 0.491 | [5 empty] | 25.9 |  |  |  |  | 51.8 |  | 23.5 |  | 8.2 | 0.149 |  | 5.7 | 100.24 | 1.83 |  |  |  |  | 14.94 | 13.07 | [6 empty] | 21.78 | 14.63 | 7.14
2010-12-12 | 6.535 | 6.52 |  |  |  |  | 7.495 | 1.575 |  |  |  |  | 41.5 |  |  |  | 4 | 1.1855 |  |  | 0.723 | 0.8015 | [5 empty] | 26.3 |  |  |  |  | 52.65 |  | 23.9 |  | 8.25 | 0.139 |  | 5.25 | 90.215 | 1.535 |  |  |  |  | 15.215 | 13.1705 | [6 empty] | 21.45 | 13.905 | 7.53
2010-12-13 | 6.36 | 6.61 |  |  |  |  | 7.08 | 1.5 |  |  |  |  | 40 |  |  |  | 7 | 1.054 |  |  | 0.906 | 1.112 | [5 empty] | 26.7 |  |  |  |  | 53.5 |  | 24.3 |  | 8.3 | 0.129 |  | 4.8 | 80.19 | 1.24 |  |  |  |  | 15.49 | 13.271 | [6 empty] | 21.12 | 13.18 | 7.92
2010-12-14 | 6.62 | 6.47 |  |  |  |  | 7.26 | 1.46 |  |  |  |  | 40 |  |  |  | 0 | 0.65 |  |  | 0.421 | 0.475 | [5 empty] | 28 |  |  |  |  | 55.8 |  | 21.5 |  | 9.6 | 0.013 |  | 4.8 | 83.79 | 1.33 |  |  |  |  | 14.358 | 13.63 | [6 empty] | 18.78 | 12.89 | 6.67
2010-12-15 | 6.81 | 6.54 |  |  |  |  | 7.13 | 1.54 |  |  |  |  | 42 |  |  |  | 0 | 0.903 |  |  | 0.399 | 0.625 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 23.5 |  | 9.9 | 0.084 |  | 5.4 | 80.53 | 1.23 |  |  |  |  | 14.358 | 13.196 | [6 empty] | 22.01 | 13.55 | 6.58
2010-12-16 | 6.08 | 5.87 |  |  |  |  | 7.01 | 1.47 |  |  |  |  | 39 |  |  |  | 1 | 0.504 |  |  | 0.389 | 0.612 | [5 empty] | 27.3 |  |  |  |  | 54.6 |  | 19 |  | 8.1 | 0.058 |  | 5.3 | 81.59 | 1.32 |  |  |  |  | 14.145 | 13.25 | [6 empty] | 23.71 | 13.7 | 6.17
2010-12-17 | 6.445 | 6.4 |  |  |  |  | 7.76 | 1.31 |  |  |  |  | 40 |  |  |  | 0 | 0.508 |  |  | 0.372 | 0.723 | [5 empty] | 24.8 |  |  |  |  | 49.6 |  | 20.2 |  | 8.4 | 0.063 |  | 5.2 | 85.51 | 1.56 |  |  |  |  | 15.156 | 13.536 | [6 empty] | 22.86 | 13.625 | 6.375
2010-12-18 | 6.81 | 6.49 |  |  |  |  | 7.88 | 1.49 |  |  |  |  | 37 |  |  |  | 0 | 0.511 |  |  | 0.343 | 0.519 | [5 empty] | 25.1 |  |  |  |  | 50.2 |  | 20.1 |  | 8.1 | 0.061 |  | 5.5 | 90.45 | 1.42 |  |  |  |  | 14.8 | 14.12 | [6 empty] | 23.285 | 13.6625 | 6.2725
2010-12-19 | 6.87 | 6.555 |  |  |  |  | 1.43 | 1.4 |  |  |  |  | 42 |  |  |  | 0 | 0.5305 |  |  | 0.5345 | 0.6335 | [5 empty] | 26.05 |  |  |  |  | 52.1 |  | 22.25 |  | 8.85 | 0.0985 |  | 5.55 | 79.69 | 1.32 |  |  |  |  | 13.884 | 13.162 | [6 empty] | 23.0725 | 13.6438 | 6.3238
2010-12-20 | 6.93 | 6.62 |  |  |  |  | 7.66 | 1.31 |  |  |  |  | 47 |  |  |  | 0 | 0.55 |  |  | 0.726 | 0.748 | [5 empty] | 27 |  |  |  |  | 54 |  | 24.4 |  | 9.6 | 0.136 |  | 5.6 | 90.41 | 1.8 |  |  |  |  | 14.79 | 13.19 | [6 empty] | 20.47 | 13.7 | 6.48
2010-12-21 | 6.765 | 6.465 |  |  |  |  | 7.38 | 1.28 |  |  |  |  | 50.5 |  |  |  | 0 | 0.994 |  |  | 0.505 | 0.679 | [5 empty] | 28.15 |  |  |  |  | 56.3 |  | 24.65 |  | 8.2 | 0.1145 |  | 5.5 | 79.39 | 1.4 |  |  |  |  | 14.589 | 13.459 | [6 empty] | 31.42 | 13.82 | 9.02
2010-12-22 | 6.6 | 6.31 |  |  |  |  | 7.1 | 1.28 |  |  |  |  | 54 |  |  |  | 0 | 1.438 |  |  | 0.284 | 0.61 | [5 empty] | 29.3 |  |  |  |  | 58.6 |  | 24.9 |  | 6.8 | 0.093 |  | 5.4 | 85 | 1.5 |  |  |  |  | 13.896 | 14.818 | [6 empty] | 31.42 | 13.82 | 9.02
2010-12-23 | 5.22 | 6.47 |  |  |  |  | 7.25 | 1.13 |  |  |  |  | 55 |  |  |  | 1 | 1.554 |  |  | 0.298 | 0.231 | [5 empty] | 33.3 |  |  |  |  | 66.6 |  | 21.6 |  | 8.9 | 0.073 |  | 5.7 | 75.3 | 1.46 |  |  |  |  | 14.29 | 13.19 | [6 empty] | 33.53 | 13.57 | 9.14
2010-12-24 | 6.27 | 6.46 |  |  |  |  | 7.15 | 1.04 |  |  |  |  | 48 |  |  |  | 0 | 1.49 |  |  | 0.393 | 0.338 | [5 empty] | 32.4 |  |  |  |  | 64.8 |  | 23.2 |  | 10.6 | 0.187 |  | 5.1 | 68.86 | 1.23 |  |  |  |  | 14.45 | 13.8 | [6 empty] | 27.23 | 13.28 | 10.29
2010-12-25 | 6.48 | 6.81 |  |  |  |  | 7.54 | 1.28 |  |  |  |  | 67 |  |  |  | 3 | 2.603 |  |  | 0.418 | 0.313 | [5 empty] | 32.2 |  |  |  |  | 64.4 |  | 31.7 |  | 9.6 | 0.192 |  | 5 | 74.78 | 1.33 |  |  |  |  | 14.56 | 13.01 | [6 empty] | 26.76 | 12.81 | 10.93
2010-12-26 | 6.045 | 6.375 |  |  |  |  | 7.36 | 1.36 |  |  |  |  | 70.5 |  |  |  | 2 | 2.652 |  |  | 0.396 | 0.4525 | [5 empty] | 31.25 |  |  |  |  | 62.5 |  | 30.95 |  | 8.85 | 0.189 |  | 5 | 59.58 | 0.77 |  |  |  |  | 12.706 | 13.628 | [6 empty] | 26.76 | 12.81 | 10.93
2010-12-27 | 5.61 | 5.94 |  |  |  |  | 7.18 | 1.15 |  |  |  |  | 74 |  |  |  | 1 | 2.701 |  |  | 0.374 | 0.592 | [5 empty] | 30.3 |  |  |  |  | 60.6 |  | 30.2 |  | 8.1 | 0.186 |  | 5 | 50.78 | 0.59 |  |  |  |  | 14.794 | 13.233 | [6 empty] | 27.22 | 12.94 | 9.16
2010-12-28 | 6.16 | 6.19 |  |  |  |  | 7.27 | 1.37 |  |  |  |  | 71 |  |  |  | 0 | 1.774 |  |  | 0.294 | 0.276 | [5 empty] | 31.4 |  |  |  |  | 62.8 |  | 28.2 |  | 8.7 | 0.173 |  | 5.1 | 61.74 | 0.68 |  |  |  |  | 14.345 | 13.684 | [6 empty] | 23.97 | 12.37 | 16.99
2010-12-29 | 6.07 | 6.02 |  |  |  |  | 6.55 | 1.58 |  |  |  |  | 71 |  |  |  | 2 | 2.357 |  |  | 0.31 | 0.52 | [5 empty] | 31.3 |  |  |  |  | 62.6 |  | 29.3 |  | 7.9 | 0.17 |  | 4.6 | 69.92 | 0.84 |  |  |  |  | 14.335 | 13.14 | [6 empty] | 27.7 | 13.55 | 13.4
2010-12-30 | 6.01 | 5.96 |  |  |  |  | 7.2 | 1.57 |  |  |  |  | 74 |  |  |  | 0 | 1.587 |  |  | 0.321 | 0.268 | [5 empty] | 34.1 |  |  |  |  | 68.2 |  | 30.2 |  | 8.2 | 0.174 |  | 4.7 | 85.62 | 1.2 |  |  |  |  | 15.128 | 14.022 | [6 empty] | 27.03 | 13.28 | 13.15
2010-12-31 | 6.29 | 6.3 |  |  |  |  | 7.15 | 1.66 |  |  |  |  | 69 |  |  |  | 0 | 1.768 |  |  | 0.295 | 0.286 | [5 empty] | 33.1 |  |  |  |  | 66.2 |  | 28.8 |  | 9.1 | 0.143 |  | 4.4 | 85.16 | 1.22 |  |  |  |  | 14.15 | 13.417 | [6 empty] | 25.66 | 14.63 | 12.67

## 2011
All of the data presented below was copied verbatim from spreadsheets transcribed by Debbie Rideout, Town PLO
| pH | [6 empty] | Chlorine |  |  |  | Colour | [5 empty] | Turbidity | [5 empty] | Total Dissolved Solids |  |  |  |  | Conductivity |  |  |  |  | Hardness |  | Alkalinity |  | Aluminum | Temperature |  | Cl Used | Cl Demand | UVT |  | UVA |  | Flows within plant |  |  |  | Flows from plant |  |  | Chemical Dosages
Date | Raw | PTC | PTC (OL) | SWC | Filter | Finish (OL) | Finish | Free | Total | Sample | Analyzer | Raw A | Raw T | SWC A | Filter A | Finish A | Finish T | Raw | Raw (OL) | SWC | Filter | Finish | Finish (OL) | Raw | PTC | SWC | Filter | Finish | Raw | PTC | SWC | Filter | Finish | Raw | Finish | Raw | Finish | Finish (Free) | Raw | Finish |  |  | Raw | Filter | Raw | Filter | Raw | Finish | Filter | Backwash | Bishop's | Botwood | GFW | Chlorine | Alum | Limestone | Lime
2011-01-01 | 6.79 | 6.4 |  |  |  |  | 7.73 | 1.65 |  |  |  |  | 61 |  |  |  | 0 | 1.486 |  |  | 0.194 | 0.277 | [5 empty] | 33.1 |  |  |  |  | 66.2 |  | 24.1 |  | 9.9 | 0.077 |  | 4.4 | 80.59 | 1.25 |  |  |  |  | 14.06 | 12.63 | [6 empty] | 26.61 | 13.77 | 16.09
2011-01-02 | 6.865 | 6.62 |  |  |  |  | 7.43 | 1.415 |  |  |  |  | 55 |  |  |  | 1 | 1.56 |  |  | 0.3825 | 0.392 | [5 empty] | 32.3 |  |  |  |  | 64.65 |  | 23.45 |  | 9.85 | 0.0925 |  | 4.15 | 70.36 | 1.07 |  |  |  |  | 14.3815 | 12.896 | [6 empty] | 23.865 | 14.215 | 14
2011-01-03 | 6.94 | 6.84 |  |  |  |  | 7.13 | 1.18 |  |  |  |  | 49 |  |  |  | 2 | 1.634 |  |  | 0.571 | 0.507 | [5 empty] | 31.5 |  |  |  |  | 63.1 |  | 22.8 |  | 9.8 | 0.108 |  | 3.9 | 60.13 | 0.89 |  |  |  |  | 14.703 | 13.162 | [6 empty] | 21.12 | 13.66 | 11.91
2011-01-04 | 6.19 | 6.92 |  |  |  |  | 7.29 | 1.26 |  |  |  |  | 36 |  |  |  | 0 | 1.624 |  |  | 0.284 | 0.386 | [5 empty] | 29.6 |  |  |  |  | 59.2 |  | 16.5 |  | 7.7 | 0.173 |  | 4.4 | 69.92 | 0.99 |  |  |  |  | 14.951 | 14.132 | [6 empty] | 27.63 | 13.88 | 9.26
2011-01-05 | 6.14 | 6.4 |  |  |  |  | 7.17 | 1.3 |  |  |  |  | 47 |  |  |  | 5 | 1.647 |  |  | 0.2765 | 0.437 | [5 empty] | 32.5 |  |  |  |  | 65 |  | 17.5 |  | 9.6 | 0.187 |  | 4.1 | 94.9 | 1.89 |  |  |  |  | 15.412 | 13.498 | [6 empty] | 22.95 | 14.55 | 12.64
2011-01-06 | 6.23 | 6.11 |  |  |  |  | 6.69 | 1.71 |  |  |  |  | 53 |  |  |  | 3 | 1.46 |  |  | 0.269 | 0.392 | [5 empty] | 31.8 |  |  |  |  | 63.6 |  | 24 |  | 8.8 | 0.132 |  | 4.1 | 85.99 | 1.11 |  |  |  |  | 14.991 | 13.857 | [6 empty] | 23.01 | 14.66 | 7.81
2011-01-07 | 6.31 | 6.28 |  |  |  |  | 6.95 | 1.55 |  |  |  |  | 50 |  |  |  | 8 | 1.531 |  |  | 0.388 | 0.216 | [5 empty] | 34.2 |  |  |  |  | 68.4 |  | 24.6 |  | 8.1 | 0.199 |  | 4.4 | 79.38 | 0.84 |  |  |  |  | 16.322 | 15.037 | [6 empty] | 23.1 | 13.39 | 6.76
2011-01-08 | 5.85 | 6.18 |  |  |  |  | 8.02 | 1.45 |  |  |  |  | 44 |  |  |  | 4 | 1.584 |  |  | 0.475 | 0.276 | [5 empty] | 33.2 |  |  |  |  | 66.4 |  | 24 |  | 10.1 | 0.164 |  | 4.1 | 80.17 | 1.14 |  |  |  |  | 15.926 | 14.022 | [6 empty] | 25.06 | 13.38 | 13.28
2011-01-09 | 6.295 | 6.2 |  |  |  |  | 8.08 | 1.79 |  |  |  |  | 45.5 |  |  |  | 2.5 | 1.4155 |  |  | 0.455 | 0.3 | [5 empty] | 35.4 |  |  |  |  | 70.8 |  | 24.15 |  | 10.35 | 0.1395 |  | 4.35 | 80.2 | 1.11 |  |  |  |  | 14.461 | 12.547 | [6 empty] | 23.61 | 13.395 | 14.58
2011-01-10 | 6.74 | 6.22 |  |  |  |  | 8.14 | 1.49 |  |  |  |  | 47 |  |  |  | 1 | 1.247 |  |  | 0.435 | 0.324 | [5 empty] | 37.6 |  |  |  |  | 75.2 |  | 24.3 |  | 10.6 | 0.115 |  | 4.6 | 65.03 | 0.72 |  |  |  |  | 14.956 | 13.376 | [6 empty] | 22.16 | 13.41 | 15.88
2011-01-11 | 6.38 | 6.67 |  |  |  |  | 7.72 | 1.57 |  |  |  |  | 55 |  |  |  | 0 | 1.241 |  |  | 0.21 | 0.128 | [5 empty] | 36 |  |  |  |  | 72 |  | 27.9 |  | 12.3 | 0.088 |  | 4.6 | 69.5 | 0.67 |  |  |  |  | 15.597 | 14.061 | [6 empty] | 22.37 | 14.47 | 13.86
2011-01-12 | 6.02 | 6.6 |  |  |  |  | 7.68 | 1.69 |  |  |  |  | 46 |  |  |  | 3 | 1.148 |  |  | 0.193 | 0.134 | [5 empty] | 37.6 |  |  |  |  | 75.2 |  | 24.9 |  | 9.9 | 0.16 |  | 4.1 | 71.11 | 0.65 |  |  |  |  | 14.946 | 13.801 | [6 empty] | 23.32 | 12.16 | 13.22
2011-01-13 | 5.73 | 6.83 |  |  |  |  | 7.28 | 1.21 |  |  |  |  | 42 |  |  |  | 2 | 1.096 |  |  | 0.294 | 0.132 | [5 empty] | 34.2 |  |  |  |  | 68.4 |  | 26.5 |  | 8.6 | 0.188 |  | 4.1 | 74.99 | 1.02 |  |  |  |  | 15.976 | 15.295 | [6 empty] | 22.49 | 16.27 | 12.16
2011-01-14 | 6.41 | 6.43 |  |  |  |  | 7.98 | 1.39 |  |  |  |  | 41 |  |  |  | 0 | 1.155 |  |  | 0.134 | 0.143 | [5 empty] | 35.6 |  |  |  |  | 71.3 |  | 25.2 |  | 9.3 | 0.188 |  | 4 | 74.82 | 1 |  |  |  |  | 14.793 | 14.198 | [6 empty] | 26.76 | 14.03 | 12.51
2011-01-15 | 6.35 | 6.33 |  |  |  |  | 8.26 | 1.55 |  |  |  |  | 42 |  |  |  | 0 | 0.976 |  |  | 0.139 | 0.155 | [5 empty] | 38.2 |  |  |  |  | 76.4 |  | 35.5 |  | 12.1 | 0.184 |  | 4 | 69.92 | 0.72 |  |  |  |  | 15.06 | 13.99 | [6 empty] | 26.76 | 14.16 | 19
2011-01-16 | 6.125 | 6.355 |  |  |  |  | 8.515 | 1.52 |  |  |  |  | 40 |  |  |  | 0 | 0.9575 |  |  | 0.2675 | 0.1475 | [5 empty] | 39.25 |  |  |  |  | 78.5 |  | 35.1 |  | 10.95 | 0.1415 |  | 4.95 | 69.92 | 0.81 |  |  |  |  | 14.645 | 13.596 | [6 empty] | 26.76 | 14.16 | 19
2011-01-17 | 5.9 | 6.38 |  |  |  |  | 8.77 | 1.5 |  |  |  |  | 38 |  |  |  | 0 | 0.939 |  |  | 0.396 | 0.14 | [5 empty] | 40.3 |  |  |  |  | 80.6 |  | 34.7 |  | 9.8 | 0.099 |  | 5.9 | 70.41 | 0.87 |  |  |  |  | 15.069 | 13.463 | [6 empty] | 30.55 | 15.03 | 14.47
2011-01-18 | 6.07 | 6.51 |  |  |  |  | 7.72 | 1.54 |  |  |  |  | 43 |  |  |  | 0 | 0.916 |  |  | 0.556 | 0.171 | [5 empty] | 34.5 |  |  |  |  | 69 |  | 34.1 |  | 8.9 | 0.146 |  | 3.7 | 75.28 | 0.98 |  |  |  |  | 15.193 | 13.577 | [6 empty] | 23.78 | 13.41 | 14.24
2011-01-19 | 6.8 | 5.73 |  |  |  |  | 8.29 | 1.31 |  |  |  |  | 41 |  |  |  | 0 | 0.818 |  |  | 0.141 | 0.197 | [5 empty] | 39.4 |  |  |  |  | 78.8 |  | 28.1 |  | 13.3 | 0.171 |  | 4 | 75.3 | 0.89 |  |  |  |  | 16.718 | 15.514 | [6 empty] | 20.19 | 14.59 | 19.62
2011-01-20 | 6.64 | 6.39 |  |  |  |  | 8.62 | 1.48 |  |  |  |  | 41 |  |  |  | 0 | 0.782 |  |  | 0.101 | 0.159 | [5 empty] | 36.5 |  |  |  |  | 73.2 |  | 25.4 |  | 12.8 | 0.13 |  | 4.3 | 65.03 | 0.71 |  |  |  |  | 14.225 | 13.477 | [6 empty] | 22.53 | 13.77 | 18.04
2011-01-21 | 7.2 | 6.31 |  |  |  |  | 8.51 | 1.32 |  |  |  |  | 31 |  |  |  | 4 | 0.739 |  |  | 0.1665 | 0.475 | [5 empty] | 37.2 |  |  |  |  | 74.3 |  | 26.1 |  | 9 | 0.21 |  | 4.2 | 74.82 | 1.04 |  |  |  |  | 15.091 | 14.41 | [6 empty] | 25.95 | 15.68 | 22.42
2011-01-22 | 6.43 | 5.92 |  |  |  |  | 7.62 | 1.67 |  |  |  |  | 34 |  |  |  | 0 | 0.77 |  |  | 0.232 | 1.087 | [5 empty] | 46.1 |  |  |  |  | 92.2 |  | 26 |  | 6.9 | 0.02 |  | 4.4 | 70.41 | 0.67 |  |  |  |  | 14.81 | 13.67 | [6 empty] | 36.83 | 15.6 | 16.62
2011-01-23 | 6.55 | 6.01 |  |  |  |  | 8.075 | 1.64 |  |  |  |  | 32.5 |  |  |  | 0 | 0.716 |  |  | 0.221 | 0.761 | [5 empty] | 43.1 |  |  |  |  | 86.2 |  | 25.45 |  | 8.7 | 0.081 |  | 4.2 | 72.59 | 0.685 |  |  |  |  | 15.294 | 14.17 | [6 empty] | 34.11 | 14.54 | 17.135
2011-01-24 | 6.67 | 6.1 |  |  |  |  | 8.53 | 1.61 |  |  |  |  | 31 |  |  |  | 0 | 0.662 |  |  | 0.21 | 0.435 | [5 empty] | 40.1 |  |  |  |  | 80.2 |  | 24.9 |  | 10.5 | 0.142 |  | 4 | 74.77 | 0.7 |  |  |  |  | 15.778 | 14.67 | [6 empty] | 31.39 | 13.48 | 17.65
2011-01-25 | 6.17 | 6.24 |  |  |  |  | 7.85 | 1.59 |  |  |  |  | 34 |  |  |  | 0 | 0.653 |  |  | 0.104 | 0.18 | [5 empty] | 39.6 |  |  |  |  | 79.2 |  | 36.4 |  | 12 | 0.143 |  | 3.2 | 65.03 | 0.69 |  |  |  |  | 13.626 | 12.935 | [6 empty] | 35.47 | 13.23 | 16.63
2011-01-26 | 6.42 | 6.51 |  |  |  |  | 8.38 | 1.67 |  |  |  |  | 40 |  |  |  | 0 | 0.658 |  |  | 0.136 | 0.094 | [5 empty] | 40.2 |  |  |  |  | 80.4 |  | 24.2 |  | 11.6 | 0.152 |  | 4.1 | 60.13 | 0.32 |  |  |  |  | 14.539 | 13.742 | [6 empty] | 32.75 | 13.43 | 16.62
2011-01-27 | 6.35 | 6.28 |  |  |  |  | 8.54 | 1.35 |  |  |  |  | 37 |  |  |  | 0 | 0.66 |  |  | 0.143 | 0.111 | [5 empty] | 40.7 |  |  |  |  | 81.4 |  | 25.3 |  | 12.4 | 0.108 |  | 4 | 60.15 | 0.69 |  |  |  |  | 14.55 | 13.388 | [6 empty] | 41.35 | 14.84 | 18.26
2011-01-28 | 5.79 | 6.64 |  |  |  |  | 8.66 | 1.31 |  |  |  |  | 35 |  |  |  | 0 | 0.642 |  |  | 0.084 | 0.279 | [5 empty] | 40 |  |  |  |  | 80 |  | 24.8 |  | 11.1 | 0.12 |  | 3.9 | 65.03 | 0.9 |  |  |  |  | 14.613 | 13.403 | [6 empty] | 38.05 | 15.34 | 19.19
2011-01-29 | 6 | 6.02 |  |  |  |  | 7.31 | 1.55 |  |  |  |  | 34 |  |  |  | 0 | 0.614 |  |  | 0.093 | 0.114 | [5 empty] | 38.7 |  |  |  |  | 77.4 |  | 26.2 |  | 10.7 | 0.142 |  | 3.8 | 61.32 | 0.56 |  |  |  |  | 14.15 | 13.22 | [6 empty] | 39.7 | 14.08 | 18.97
2011-01-30 | 6.325 | 6.23 |  |  |  |  | 7.94 | 1.53 |  |  |  |  | 35 |  |  |  | 0 | 0.6045 |  |  | 0.2015 | 0.121 | [5 empty] | 40.7 |  |  |  |  | 81.35 |  | 24.85 |  | 11.4 | 0.136 |  | 3.9 | 69.99 | 0.84 |  |  |  |  | 14.239 | 13.406 | [6 empty] | 38.875 | 14.44 | 15.955
2011-01-31 | 6.65 | 6.44 |  |  |  |  | 8.57 | 1.51 |  |  |  |  | 36 |  |  |  | 0 | 0.595 |  |  | 0.31 | 0.128 | [5 empty] | 42.7 |  |  |  |  | 85.3 |  | 23.5 |  | 12.1 | 0.13 |  | 4 | 70.41 | 0.75 |  |  |  |  | 15.309 | 14.116 | [6 empty] | 39.2875 | 14.8 | 12.94
2011-02-01 | 6.65 | 6.37 |  |  |  |  | 8.51 | 1.72 |  |  |  |  | 35 |  |  |  | 0 | 0.599 |  |  | 0.103 | 0.117 | [5 empty] | 45 |  |  |  |  | 90 |  | 25.3 |  | 12.4 | 0.099 |  | 3.6 | 70.56 | 0.54 |  |  |  |  | 14.925 | 14.171 | [6 empty] | 39.0812 | 13.45 | 19.6
2011-02-02 | 6.11 | 6.24 |  |  |  |  | 8.97 | 1.21 |  |  |  |  | 33 |  |  |  | 0 | 0.61 |  |  | 0.161 | 0.128 | [5 empty] | 40.4 |  |  |  |  | 80.8 |  | 25.9 |  | 12.2 | 0.148 |  | 3.5 | 60.12 | 0.68 |  |  |  |  | 15.13 | 14.407 | [6 empty] | 39.1844 | 12.97 | 21.16
2011-02-03 | 6.63 | 6.39 |  |  |  |  | 8.67 | 1.21 |  |  |  |  | 41 |  |  |  | 0 | 0.587 |  |  | 0.282 | 0.144 | [5 empty] | 44.1 |  |  |  |  | 88.2 |  | 26.2 |  | 11.9 | 0.03 |  | 3.6 | 59.73 | 0.76 |  |  |  |  | 14.953 | 13.797 | [6 empty] | 44.29 | 13.65 | 18.06
2011-02-04 | 6.15 | 6.75 |  |  |  |  | 8.74 | 1.49 |  |  |  |  | 28 |  |  |  | 0 | 0.569 |  |  | 0.08 | 0.26 | [5 empty] | 41.3 |  |  |  |  | 82.8 |  | 25 |  | 13.4 | 0.042 |  | 3.5 | 64.58 | 0.5 |  |  |  |  | 15.495 | 14.738 | [6 empty] | 41.7372 | 14.75 | 19.27
2011-02-05 | 6.7 | 6.84 |  |  |  |  | 9.16 | 1.47 |  |  |  |  | 32 |  |  |  | 0 | 0.568 |  |  | 0.121 | 0.111 | [5 empty] | 42 |  |  |  |  | 84 |  | 26.5 |  | 12.9 | 0.051 |  | 3.4 | 59.53 | 0.39 |  |  |  |  | 15.02 | 14.53 | [6 empty] | 43.0136 | 14.15 | 19.49
2011-02-06 | 6.38 | 6.66 |  |  |  |  | 9.095 | 1.475 |  |  |  |  | 32.5 |  |  |  | 0 | 0.5475 |  |  | 0.1805 | 0.129 | [5 empty] | 42.45 |  |  |  |  | 84.9 |  | 26.4 |  | 11.8 | 0.106 |  | 3.45 | 55.13 | 0.39 |  |  |  |  | 14.675 | 13.955 | [6 empty] | 42.3754 | 14.15 | 19.49
2011-02-07 | 6.06 | 6.48 |  |  |  |  | 9.03 | 1.48 |  |  |  |  | 33 |  |  |  | 0 | 0.527 |  |  | 0.24 | 0.147 | [5 empty] | 42.9 |  |  |  |  | 85.8 |  | 26.3 |  | 10.7 | 0.161 |  | 3.5 | 69.99 | 0.7 |  |  |  |  | 15.745 | 14.576 | [6 empty] | 42.6945 | 14.34 | 20.88
2011-02-08 | 6.19 | 6.27 |  |  |  |  | 8.23 | 1.61 |  |  |  |  | 33 |  |  |  | 0 | 0.525 |  |  | 0.095 | 0.085 | [5 empty] | 40.1 |  |  |  |  | 80.2 |  | 27.1 |  | 10.3 | 0.048 |  | 3.6 | 70.47 | 0.7 |  |  |  |  | 14.637 | 13.828 | [6 empty] | 42.5349 | 14.17 | 15.89
2011-02-09 | 6.1 | 6.42 |  |  |  |  | 7.94 | 1.27 |  |  |  |  | 37 |  |  |  | 0 | 0.506 |  |  | 0.13 | 0.101 | [5 empty] | 38.8 |  |  |  |  | 77.6 |  | 25.6 |  | 11 | 0.092 |  | 3.8 | 49.35 | 0.32 |  |  |  |  | 15.014 | 14.073 | [6 empty] | 23.94 | 14.03 | 14.81
2011-02-10 | 6.35 | 6.46 |  |  |  |  | 8.04 | 1.17 |  |  |  |  | 31 |  |  |  | 0 | 0.5 |  |  | 0.161 | 0.127 | [5 empty] | 38.2 |  |  |  |  | 76.4 |  | 26.6 |  | 10.9 | 0.096 |  | 3.7 | 65.53 | 0.86 |  |  |  |  | 15.879 | 14.662 | [6 empty] | 23.94 | 14.54 | 15.1
2011-02-11 | 6.89 | 6.54 |  |  |  |  | 7.38 | 1.18 |  |  |  |  | 33 |  |  |  | 0 | 0.492 |  |  | 0.132 | 0.202 | [5 empty] | 34.8 |  |  |  |  | 69.7 |  | 27.5 |  | 10.2 | 0.089 |  | 4 | 55.39 | 0.56 |  |  |  |  | 15.461 | 14.436 | [6 empty] | 31.46 | 15.66 | 12.65
2011-02-12 | 6.07 | 6.43 |  |  |  |  | 7.18 | 1.26 |  |  |  |  | 37 |  |  |  | 0 | 0.488 |  |  | 0.104 | 0.236 | [5 empty] | 35.4 |  |  |  |  | 70.8 |  | 19.2 |  | 8.4 | 0.112 |  | 3.8 | 64.1 | 0.79 |  |  |  |  | 15.27 | 14.17 | [6 empty] | 30.99 | 13.28 | 12.44
2011-02-13 | 6.135 | 6.15 |  |  |  |  | 7.175 | 1.255 |  |  |  |  | 33 |  |  |  | 0 | 0.486 |  |  | 0.1585 | 0.273 | [5 empty] | 36.9 |  |  |  |  | 73.85 |  | 27.1 |  | 9.15 | 0.082 |  | 3.65 | 59.435 | 0.615 |  |  |  |  | 15.503 | 14.4075 | [6 empty] | 27.23 | 14.025 | 14.18
2011-02-14 | 6.2 | 5.87 |  |  |  |  | 7.17 | 1.25 |  |  |  |  | 29 |  |  |  | 0 | 0.484 |  |  | 0.213 | 0.31 | [5 empty] | 38.4 |  |  |  |  | 76.9 |  | 35 |  | 9.9 | 0.052 |  | 3.5 | 54.77 | 0.44 |  |  |  |  | 15.736 | 14.645 | [6 empty] | 23.47 | 14.77 | 15.92
2011-02-15 | 6.23 | 6.1 |  |  |  |  | 7.24 | 1.3 |  |  |  |  | 37 |  |  |  | 0 | 0.464 |  |  | 0.227 | 0.097 | [5 empty] | 36.1 |  |  |  |  | 72.2 |  | 28.7 |  | 10.2 | 0.066 |  | 3.5 | 49.86 | 0.34 |  |  |  |  | 14.672 | 13.834 | [6 empty] | 23.47 | 14.2 | 16.7
2011-02-16 | 6.38 | 6.41 |  |  |  |  | 7.32 | 1.25 |  |  |  |  | 28 |  |  |  | 0 | 0.448 |  |  | 0.143 | 0.128 | [5 empty] | 38.7 |  |  |  |  | 77.4 |  | 33.5 |  | 9.6 | 0.041 |  | 3.6 | 54.82 | 0.5 |  |  |  |  | 15.031 | 14.2 | [6 empty] | 22.95 | 14.16 | 16.62
2011-02-17 | 6.62 | 6.09 |  |  |  |  | 7.37 | 1.34 |  |  |  |  | 29 |  |  |  | 0 | 0.445 |  |  | 0.101 | 0.119 | [5 empty] | 39.3 |  |  |  |  | 78.6 |  | 30.9 |  | 9.3 | 0.052 |  | 3.9 | 50.29 | 0.27 |  |  |  |  | 15.397 | 14.188 | [6 empty] | 15.03 | 13.83 | 19.4
2011-02-18 | 6.11 | 6.52 |  |  |  |  | 7.14 | 1.36 |  |  |  |  | 30 |  |  |  | 0 | 0.419 |  |  | 0.098 | 0.097 | [5 empty] | 36.2 |  |  |  |  | 72.4 |  | 28.5 |  | 9.1 | 0.049 |  | 3.8 | 55.25 | 0.45 |  |  |  |  | 14.566 | 13.841 | [6 empty] | 18.99 | 13.405 | 17.18
2011-02-19 | 6.03 | 6.84 |  |  |  |  | 7.31 | 1.41 |  |  |  |  | 29 |  |  |  | 0 | 0.413 |  |  | 0.087 | 0.084 | [5 empty] | 35.9 |  |  |  |  | 71.8 |  | 29.3 |  | 9.3 | 0.02 |  | 3.5 | 64.52 | 0.67 |  |  |  |  | 15.21 | 14.05 | [6 empty] | 17.01 | 12.98 | 14.96
2011-02-20 | 6.735 | 6.76 |  |  |  |  | 7.27 | 1.41 |  |  |  |  | 29.5 |  |  |  | 0 | 0.401 |  |  | 0.084 | 0.082 | [5 empty] | 36.7 |  |  |  |  | 73.45 |  | 27.2 |  | 9.6 | 0.023 |  | 3.65 | 55.32 | 0.47 |  |  |  |  | 14.513 | 13.341 | [6 empty] | 18 | 14.405 | 14.995
2011-02-21 | 7.44 | 6.68 |  |  |  |  | 7.23 | 1.29 |  |  |  |  | 30 |  |  |  | 0 | 0.389 |  |  | 0.081 | 0.08 | [5 empty] | 37.5 |  |  |  |  | 75.1 |  | 25.1 |  | 9.9 | 0.026 |  | 3.8 | 57.79 | 0.61 |  |  |  |  | 14.991 | 13.786 | [6 empty] | 26.05 | 15.83 | 15.03
2011-02-22 | 6.35 | 6.34 |  |  |  |  | 8.51 | 1.07 |  |  |  |  | 34 |  |  |  | 0 | 0.394 |  |  | 0.13 | 0.079 | [5 empty] | 35.8 |  |  |  |  | 71.6 |  | 21 |  | 8.6 | 0.011 |  | 3.8 | 48.51 | 0.51 |  |  |  |  | 15.074 | 13.923 | [6 empty] | 24.17 | 13.46 | 15.25
2011-02-23 | 6.7 | 6.55 |  |  |  |  | 7.37 | 1.09 |  |  |  |  | 33 |  |  |  | 0 | 0.387 |  |  | 0.087 | 0.134 | [5 empty] | 35.4 |  |  |  |  | 70.8 |  | 20.9 |  | 10.5 | 0 |  | 4 | 44.1 | 0.38 |  |  |  |  | 14.811 | 13.598 | [6 empty] | 30.89 | 11.79 | 12.05
2011-02-24 | 6.19 | 5.97 |  |  |  |  | 6.69 | 1.06 |  |  |  |  | 24 |  |  |  | 0.058 | 0.39 |  |  | 0.101 | 0.219 | [5 empty] | 37.8 |  |  |  |  | 75.6 |  | 26.4 |  | 6.9 | 0.058 |  | 3.7 | 42.51 | 2.58 |  |  |  |  | 14.463 | 13.762 | [6 empty] | 42.99 | 13.01 | 12.61
2011-02-25 | 6.18 | 6.29 |  |  |  |  | 7.16 | 1.16 |  |  |  |  | 26 |  |  |  | 0 | 0.373 |  |  | 0.098 | 0.092 | [5 empty] | 41.6 |  |  |  |  | 83.3 |  | 22 |  | 10.3 | 0.009 |  | 3.5 | 40.92 | 0.17 |  |  |  |  | 15.083 | 13.942 | [6 empty] | 25.35 | 14.15 | 18.15
2011-02-26 | 6.16 | 6.24 |  |  |  |  | 7.59 | 1.14 |  |  |  |  | 25 |  |  |  | 0 | 0.37 |  |  | 0.101 | 0.089 | [5 empty] | 38.2 |  |  |  |  | 76.5 |  | 26.4 |  | 9.8 | 0.011 |  | 3.5 | 43.81 | 0.27 |  |  |  |  | 14.07 | 14.06 | [6 empty] | 24.88 | 13.68 | 17.83
2011-02-27 | 6.145 | 6.19 |  |  |  |  | 7.315 | 1.09 |  |  |  |  | 25.5 |  |  |  | 0 | 0.378 |  |  | 0.1065 | 0.1015 | [5 empty] | 39.35 |  |  |  |  | 78.75 |  | 26.6 |  | 9.75 | 0.0235 |  | 3.5 | 50.71 | 0.52 |  |  |  |  | 15.024 | 14.286 | [6 empty] | 24.88 | 13.68 | 17.83
2011-02-28 | 6.13 | 6.14 |  |  |  |  | 7.04 | 1.19 |  |  |  |  | 26 |  |  |  | 0 | 0.386 |  |  | 0.112 | 0.114 | [5 empty] | 40.5 |  |  |  |  | 81 |  | 26.8 |  | 9.7 | 0.036 |  | 3.5 | 49.45 | 0.42 |  |  |  |  | 15.538 | 13.917 | [6 empty] | 48.81 | 13.43 | 16.64
2011-03-01 | 7.29 | 6.34 |  |  |  |  | 8.03 | 1.15 |  |  |  |  | 30 |  |  |  | 0 | 0.385 |  |  | 0.076 | 0.089 | [5 empty] | 41.5 |  |  |  |  | 83 |  | 25.7 |  | 10.4 | 0.004 |  | 3.8 | 58.96 | 0.72 |  |  |  |  | 14.981 | 14.292 | [6 empty] | 37.63 | 14.07 | 17.98
2011-03-02 | 6.47 | 6.7 |  |  |  |  | 7.86 | 0.99 |  |  |  |  | 31 |  |  |  | 0 | 0.394 |  |  | 0.092 | 0.111 | [5 empty] | 36.5 |  |  |  |  | 73.1 |  | 24.7 |  | 10.6 | 0.026 |  | 3.7 | 39.69 | 0.27 |  |  |  |  | 14.612 | 14.243 | [6 empty] | 25.35 | 14 | 18.09
2011-03-03 | 6.48 | 6.4 |  |  |  |  | 7.5 | 0.88 |  |  |  |  | 27 |  |  |  | 0 | 0.398 |  |  | 0.135 | 0.149 | [5 empty] | 39.4 |  |  |  |  | 78.8 |  | 28.3 |  | 10.4 | 0.001 |  | 3.4 | 44.1 | 0.54 |  |  |  |  | 14.475 | 14.089 | [6 empty] | 25.35 | 14.72 | 17.29
2011-03-04 | 6.36 | 6.34 |  |  |  |  | 7.25 | 0.94 |  |  |  |  | 28 |  |  |  | 0 | 0.468 |  |  | 0.098 | 0.096 | [5 empty] | 44.4 |  |  |  |  | 88.8 |  | 20.4 |  | 8.9 | 0.046 |  | 4.1 | 43.87 | 0.42 |  |  |  |  | 15.07 | 14.599 | [6 empty] | 35.03 | 11.66 | 12.39
2011-03-05 | 6.39 | 6.1 |  |  |  |  | 7.41 | 0.84 |  |  |  |  | 30 |  |  |  | 0 | 0.452 |  |  | 0.124 | 0.152 | [5 empty] | 40.9 |  |  |  |  | 81.8 |  | 19.5 |  | 8.4 | 0.099 |  | 4.1 | 29.39 | 0.12 |  |  |  |  | 14.49 | 13.79 | [6 empty] | 39.83 | 13.31 | 15.79
2011-03-06 | 6.085 | 6.255 |  |  |  |  | 7.355 | 0.905 |  |  |  |  | 29.5 |  |  |  | 0 | 0.439 |  |  | 0.121 | 0.1725 | [5 empty] | 43.05 |  |  |  |  | 86.2 |  | 28.3 |  | 9.3 | 0.0605 |  | 3.75 | 34.54 | 0.22 |  |  |  |  | 14.711 | 13.883 | [6 empty] | 33.06 | 11.8 | 13.89
2011-03-07 | 5.78 | 6.41 |  |  |  |  | 7.3 | 0.97 |  |  |  |  | 29 |  |  |  | 0 | 0.426 |  |  | 0.118 | 0.193 | [5 empty] | 45.2 |  |  |  |  | 90.6 |  | 37.1 |  | 10.2 | 0.022 |  | 3.4 | 39.69 | 0.32 |  |  |  |  | 14.932 | 13.976 | [6 empty] | 26.29 | 10.29 | 11.99
2011-03-08 | 6.51 | 6.22 |  |  |  |  | 7.61 | 1.11 |  |  |  |  | 38 |  |  |  | 0 | 0.422 |  |  | 0.108 | 0.095 | [5 empty] | 44.4 |  |  |  |  | 88.8 |  | 31.4 |  | 12.2 | 0.044 |  | 3.4 | 51.19 | 0.45 |  |  |  |  | 15.251 | 14.46 | [6 empty] | 26.76 | 14.74 | 21.09
2011-03-09 | 6.61 | 6.65 |  |  |  |  | 8.24 | 1.02 |  |  |  |  | 32 |  |  |  | 0 | 0.387 |  |  | 0.113 | 0.102 | [5 empty] | 39.4 |  |  |  |  | 78.8 |  | 30.1 |  | 10.7 | 0.039 |  | 3.7 | 49.87 | 0.45 |  |  |  |  | 15.679 | 15.3 | [6 empty] | 33.31 | 13.58 | 19.56
2011-03-10 | 6.7 | 6.4 |  |  |  |  | 6.58 | 0.98 |  |  |  |  | 39 |  |  |  | 0 | 0.42 |  |  | 0.193 | 0.131 | [5 empty] | 45.5 |  |  |  |  | 91 |  | 31.7 |  | 13.7 | 0.068 |  | 3.5 | 46.3 | 0.44 |  |  |  |  | 15.102 | 14.762 | [6 empty] | 38.97 | 13.24 | 19.4
2011-03-11 | 6.71 | 6.65 |  |  |  |  | 7.9 | 0.85 |  |  |  |  | 38 |  |  |  | 0 | 0.432 |  |  | 0.162 | 0.087 | [5 empty] | 44 |  |  |  |  | 88 |  | 31.2 |  | 11.6 | 0.064 |  | 4.8 | 45 | 0.56 |  |  |  |  | 15.867 | 15.451 | [6 empty] | 35.02 | 13.24 | 19.4
2011-03-12 | 6.59 | 5.46 |  |  |  |  | 5.49 | 0.83 |  |  |  |  | 39 |  |  |  | 0 | 0.453 |  |  | 0.119 | 0.116 | [5 empty] | 30.8 |  |  |  |  | 61.6 |  | 30.7 |  | 7.3 | 0.114 |  | 3.4 | 45.42 | 0.55 |  |  |  |  | 15.76 | 14.84 | [6 empty] | 29.73 | 13.24 | 19.4
2011-03-13 | 6.245 | 5.65 |  |  |  |  | 5.535 | 0.99 |  |  |  |  | 42 |  |  |  | 0 | 0.466 |  |  | 0.159 | 0.348 | [5 empty] | 31.7 |  |  |  |  | 63.4 |  | 30.9 |  | 7.95 | 0.134 |  | 3.6 | 49.36 | 0.55 |  |  |  |  | 15.38 | 14.514 | [6 empty] | 35.335 | 13.24 | 19.4
2011-03-14 | 5.9 | 5.84 |  |  |  |  | 5.58 | 0.91 |  |  |  |  | 45 |  |  |  | 0 | 0.479 |  |  | 0.199 | 0.58 | [5 empty] | 32.6 |  |  |  |  | 65.2 |  | 31.1 |  | 8.6 | 0.154 |  | 3.8 | 50.42 | 0.65 |  |  |  |  | 15.043 | 14.618 | [6 empty] | 40.94 | 16.2 | 18.96
2011-03-15 | 6.14 | 6.16 |  |  |  |  | 7.27 | 0.72 |  |  |  |  | 44 |  |  |  | 0 | 0.479 |  |  | 0.24 | 0.22 | [5 empty] | 40.3 |  |  |  |  | 80.6 |  | 21.1 |  | 8.9 | 0.081 |  | 4.5 | 48.51 | 0.72 |  |  |  |  | 15.878 | 15.279 | [6 empty] | 31.49 | 14.32 | 12
2011-03-16 | 6.15 | 5.97 |  |  |  |  | 5.61 | 1.12 |  |  |  |  | 44 |  |  |  | 2 | 0.468 |  |  | 0.147 | 0.482 | [5 empty] | 32.2 |  |  |  |  | 64.4 |  | 20.1 |  | 8.4 | 0.102 |  | 3.4 | 60.13 | 0.65 |  |  |  |  | 15.267 | 15.397 | [6 empty] | 35.59 | 13.94 | 20.05
2011-03-17 | 5.93 | 6.45 |  |  |  |  | 8.08 | 1.13 |  |  |  |  | 37 |  |  |  | 0 | 0.462 |  |  | 0.164 | 0.127 | [5 empty] | 44.4 |  |  |  |  | 88.8 |  | 23.4 |  | 11.7 | 0.081 |  | 3.4 | 64.61 | 0.81 |  |  |  |  | 15.434 | 15.093 | [6 empty] | 39.49 | 13.73 | 19.48
2011-03-18 | 6.53 | 6.54 |  |  |  |  | 8.6 | 1.12 |  |  |  |  | 43 |  |  |  | 0 | 0.448 |  |  | 0.142 | 0.14 | [5 empty] | 42.9 |  |  |  |  | 85.9 |  | 21.3 |  | 13.9 | 0.042 |  | 3.7 | 57.3 | 0.61 |  |  |  |  | 16.2 | 15.038 | [6 empty] | 27.69 | 14.57 | 18.59
2011-03-19 | 6.66 | 6.39 |  |  |  |  | 8.18 | 1.24 |  |  |  |  | 41 |  |  |  | 0 | 0.429 |  |  | 0.153 | 0.122 | [5 empty] | 41.8 |  |  |  |  | 83.7 |  | 22 |  | 13.6 | 0.041 |  | 3.6 | 55.12 | 0.5 |  |  |  |  | 15.03 | 14.32 | [6 empty] | 29.11 | 17.52 | 19.06
2011-03-20 | 6.325 | 6.575 |  |  |  |  | 7.925 | 1.28 |  |  |  |  | 40 |  |  |  | 0 | 0.4175 |  |  | 0.1645 | 0.141 | [5 empty] | 40.15 |  |  |  |  | 76.85 |  | 22.65 |  | 11.35 | 0.0375 |  | 3.5 | 55.12 | 0.54 |  |  |  |  | 14.395 | 13.717 | [6 empty] | 29.11 | 17.52 | 19.06
2011-03-21 | 5.99 | 6.76 |  |  |  |  | 7.67 | 1.27 |  |  |  |  | 39 |  |  |  | 0 | 0.406 |  |  | 0.176 | 0.16 | [5 empty] | 38.5 |  |  |  |  | 70 |  | 23.3 |  | 9.1 | 0.034 |  | 3.4 | 60.13 | 0.62 |  |  |  |  | 15.569 | 14.38 | [6 empty] | 29.19 | 14.35 | 16.63
2011-03-22 | 6.65 | 6.57 |  |  |  |  | 8.08 | 1.17 |  |  |  |  | 39 |  |  |  | 0 | 0.377 |  |  | 0.153 | 0.114 | [5 empty] | 37.5 |  |  |  |  | 75 |  | 22.1 |  | 8.8 | 0.079 |  | 3.8 | 55.12 | 0.64 |  |  |  |  | 15.07 | 13.801 | [6 empty] | 27.56 | 14.76 | 14.45
2011-03-23 | 6.24 | 6.14 |  |  |  |  | 6.76 | 1.58 |  |  |  |  | 36 |  |  |  | 0 | 0.353 |  |  | 0.125 | 0.214 | [5 empty] | 42.5 |  |  |  |  | 85.2 |  | 24.4 |  | 9.8 | 0.033 |  | 3.8 | 54.33 | 0.11 |  |  |  |  | 15.638 | 14.537 | [6 empty] | 28.375 | 13.12 | 18.39
2011-03-24 | 6.04 | 6.12 |  |  |  |  | 7.29 | 1.24 |  |  |  |  | 37 |  |  |  | 0 | 0.341 |  |  | 0.129 | 0.227 | [5 empty] | 44.1 |  |  |  |  | 88.2 |  | 21.8 |  | 10.6 | 0.01 |  | 3.4 | 55.25 | 0.58 |  |  |  |  | 14.914 | 13.76 | [6 empty] | 27.9675 | 12.725 | 18.55
2011-03-25 | 6.79 | 5.97 |  |  |  |  | 7.1 | 1.21 |  |  |  |  | 29 |  |  |  | 0 | 0.312 |  |  | 0.127 | 0.231 | [5 empty] | 39.1 |  |  |  |  | 78.2 |  | 21.3 |  | 9.7 | 0 |  | 4 | 49.85 | 0.51 |  |  |  |  | 14.231 | 13.088 | [6 empty] | 28.1713 | 12.33 | 18.71
2011-03-26 | 6.23 | 6.36 |  |  |  |  | 7.46 | 1.07 |  |  |  |  | 30 |  |  |  | 0 | 0.338 |  |  | 0.201 | 0.279 | [5 empty] | 47.8 |  |  |  |  | 95.7 |  | 22 |  | 9.6 | 0.153 |  | 3.9 | 45.97 | 0.46 |  |  |  |  | 14.79 | 13.62 | [6 empty] | 28.0694 | 14.79 | 19.23
2011-03-27 | 6.145 | 6.315 |  |  |  |  | 7.33 | 1.05 |  |  |  |  | 30.5 |  |  |  | 0 | 0.325 |  |  | 0.1895 | 0.357 | [5 empty] | 47.25 |  |  |  |  | 94.6 |  | 22.5 |  | 9.6 | 0.0845 |  | 3.65 | 45.475 | 0.405 |  |  |  |  | 14.958 | 14.169 | [6 empty] | 28.1203 | 13.535 | 18.25
2011-03-28 | 6.06 | 6.27 |  |  |  |  | 7.2 | 1.03 |  |  |  |  | 31 |  |  |  | 0 | 0.312 |  |  | 0.178 | 0.435 | [5 empty] | 46.7 |  |  |  |  | 93.5 |  | 23 |  | 9.6 | 0.016 |  | 3.4 | 44.98 | 0.35 |  |  |  |  | 15.126 | 14.718 | [6 empty] | 28.0948 | 12.28 | 17.27
2011-03-29 | 6.02 | 6.11 |  |  |  |  | 7.44 | 1.06 |  |  |  |  | 37 |  |  |  | 0 | 0.32 |  |  | 0.335 | 0.466 | [5 empty] | 49.2 |  |  |  |  | 98.4 |  | 32.3 |  | 10.1 | 0.001 |  | 3.5 | 45.04 | 0.45 |  |  |  |  | 14.149 | 13.487 | [6 empty] | 28.1076 | 13.79 | 19.97
2011-03-30 | 6.89 | 7.2 |  |  |  |  | 8.29 | 1.03 |  |  |  |  | 35 |  |  |  | 0 | 0.31 |  |  | 0.167 | 0.126 | [5 empty] | 36.4 |  |  |  |  | 72.8 |  | 30.3 |  | 9.9 | 0.01 |  | 4.2 | 40.1 | 0.27 |  |  |  |  | 14.726 | 13.997 | [6 empty] | 28.1012 | 11.78 | 13.91
2011-03-31 | 6.25 | 6.47 |  |  |  |  | 7.12 | 0.92 |  |  |  |  | 30 |  |  |  | 0 | 0.299 |  |  | 0.36 | 0.343 | [5 empty] | 38.4 |  |  |  |  | 76.8 |  | 26.2 |  | 8.9 | 0.013 |  | 4.2 | 45 | 0.57 |  |  |  |  | 14.719 | 13.65 | [6 empty] | 42.95 | 11.96 | 13.67
2011-04-01 | 5.84 | 6.3 |  |  |  |  | 7.88 | 0.86 |  |  |  |  | 28 |  |  |  | 0 | 0.168 |  |  | 0.187 | 0.163 | [5 empty] | 39.9 |  |  |  |  | 79.8 |  | 25.9 |  | 8.7 | 0.018 |  | 4.5 | 39.06 | 0.45 |  |  |  |  | 14.726 | 13.641 | [6 empty] | 35.5256 | 13.08 | 11.89
2011-04-02 | 6.01 | 6.14 |  |  |  |  | 7.68 | 0.84 |  |  |  |  | 33 |  |  |  | 0 | 0.029 |  |  | 0.136 | 0.148 | [5 empty] | 40.9 |  |  |  |  | 81.8 |  | 26.6 |  | 9.6 | 0.031 |  | 4.1 | 44.98 | 0.68 |  |  |  |  | 14.22 | 13.39 | [6 empty] | 39.2378 | 14.14 | 14.38
2011-04-03 | 6.38 | 6.175 |  |  |  |  | 7.47 | 0.78 |  |  |  |  | 35 |  |  |  | 0 | 0.162 |  |  | 0.163 | 0.179 | [5 empty] | 40.75 |  |  |  |  | 81.5 |  | 27.55 |  | 9.7 | 0.0345 |  | 4.1 | 35.91 | 0.42 |  |  |  |  | 14.4165 | 13.4915 | [6 empty] | 37.3817 | 13.81 | 16.05
2011-04-04 | 6.75 | 6.21 |  |  |  |  | 7.26 | 0.83 |  |  |  |  | 37 |  |  |  | 0 | 0.295 |  |  | 0.19 | 0.21 | [5 empty] | 40.6 |  |  |  |  | 81.2 |  | 28.5 |  | 9.8 | 0.038 |  | 4.1 | 39.6 | 0.49 |  |  |  |  | 14.613 | 13.593 | [6 empty] | 38.3098 | 13.48 | 17.72
2011-04-05 | 5.98 | 6.64 |  |  |  |  | 7.32 | 0.85 |  |  |  |  | 40 |  |  |  | 0 | 0.266 |  |  | 0.099 | 0.086 | [5 empty] | 39.5 |  |  |  |  | 78.9 |  | 20 |  | 8.8 | 0.013 |  | 3.9 | 40.5 | 0.48 |  |  |  |  | 14.47 | 13.75 | [6 empty] | 37.8457 | 14 | 15.21
2011-04-06 | 6.15 | 6.65 |  |  |  |  | 7.99 | 0.79 |  |  |  |  | 34 |  |  |  | 0 | 0.261 |  |  | 0.103 | 0.09 | [5 empty] | 39 |  |  |  |  | 78 |  | 21.3 |  | 12.8 | 0.054 |  | 3.6 | 39.66 | 0.5 |  |  |  |  | 14.628 | 13.909 | [6 empty] | 38.0777 | 13.78 | 14.41
2011-04-07 | 6.71 | 6.38 |  |  |  |  | 8.39 | 0.79 |  |  |  |  | 33 |  |  |  | 0 | 0.261 |  |  | 0.123 | 0.09 | [5 empty] | 38.4 |  |  |  |  | 76.8 |  | 23.7 |  | 11.7 | 0.019 |  | 3.8 | 39.76 | 0.53 |  |  |  |  | 14.362 | 13.725 | [6 empty] | 37.9617 | 15.15 | 17.74
2011-04-08 | 6.25 | 6.43 |  |  |  |  | 6.9 | 0.82 |  |  |  |  | 31 |  |  |  | 0 | 0.307 |  |  | 0.121 | 0.119 | [5 empty] | 36.5 |  |  |  |  | 73.2 |  | 23.5 |  | 13.1 | 0.021 |  | 3.8 | 39.12 | 0.45 |  |  |  |  | 14.561 | 13.997 | [6 empty] | 38.0197 | 14.12 | 13.64
2011-04-09 | 6.4 | 6.1 |  |  |  |  | 6.98 | 1.18 |  |  |  |  | 31 |  |  |  | 0 | 0.328 |  |  | 0.113 | 0.086 | [5 empty] | 39.8 |  |  |  |  | 79.6 |  | 23.5 |  | 11.9 | 0.018 |  | 3.6 | 44.1 | 0.33 |  |  |  |  | 14.03 | 13.22 | [6 empty] | 37.9907 | 13.11 | 14.29
2011-04-10 | 6.215 | 6.145 |  |  |  |  | 7.21 | 0.75 |  |  |  |  | 37 |  |  |  | 0 | 0.333 |  |  | 0.135 | 0.2115 | [5 empty] | 38.55 |  |  |  |  | 77.1 |  | 24.05 |  | 10.25 | 0.024 |  | 3.6 | 44.09 | 0.71 |  |  |  |  | 14.439 | 13.641 | [6 empty] | 38.0052 | 13.11 | 14.29
2011-04-11 | 6.03 | 6.19 |  |  |  |  | 7.44 | 0.88 |  |  |  |  | 43 |  |  |  | 0 | 0.338 |  |  | 0.157 | 0.337 | [5 empty] | 37.3 |  |  |  |  | 74.6 |  | 24.6 |  | 8.6 | 0.03 |  | 3.6 | 40.5 | 0.47 |  |  |  |  | 15.293 | 13.561 | [6 empty] | 37.998 | 13.64 | 14.12
2011-04-12 | 6.01 | 6.46 |  |  |  |  | 7.24 | 0.72 |  |  |  |  | 44 |  |  |  | 1 | 0.338 |  |  | 0.121 | 0.086 | [5 empty] | 39.8 |  |  |  |  | 79.6 |  | 25.8 |  | 9.1 | 0.002 |  | 3.7 | 39.12 | 0.55 |  |  |  |  | 15.216 | 13.96 | [6 empty] | 38.0016 | 8.83 | 16.15
2011-04-13 | 6.6 | 6.25 |  |  |  |  | 7.64 | 0.85 |  |  |  |  | 38 |  |  |  | 0 | 0.323 |  |  | 0.105 | 0.079 | [5 empty] | 37.6 |  |  |  |  | 75.3 |  | 26.6 |  | 10.6 | 0.011 |  | 3.5 | 40.08 | 0.47 |  |  |  |  | 14.397 | 13.766 | [6 empty] | 37.9998 | 13.46 | 15.56
2011-04-14 | 6.13 | 6.34 |  |  |  |  | 7.63 | 1.1 |  |  |  |  | 37 |  |  |  | 0 | 0.328 |  |  | 0.112 | 0.095 | [5 empty] | 35.7 |  |  |  |  | 71.1 |  | 25.3 |  | 11.4 | 0.09 |  | 3.6 | 40.17 | 0.24 |  |  |  |  | 14.182 | 13.533 | [6 empty] | 38.0007 | 14.52 | 14.03
2011-04-15 | 6.33 | 6.34 |  |  |  |  | 7.71 | 1.09 |  |  |  |  | 32 |  |  |  | 0 | 0.329 |  |  | 0.099 | 0.107 | [5 empty] | 32.7 |  |  |  |  | 65.5 |  | 21.3 |  | 10.9 | 0.084 |  | 4.1 | 40.08 | 0.2 |  |  |  |  | 14.25 | 14.064 | [6 empty] | 38.0003 | 14.37 | 14.39
2011-04-16 | 6.29 | 6.08 |  |  |  |  | 7.48 | 1.19 |  |  |  |  | 32 |  |  |  | 0 | 0.319 |  |  | 0.101 | 0.092 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 20.7 |  | 10.7 | 0.086 |  | 3.9 | 40.09 | 0.16 |  |  |  |  | 14.26 | 13.5 | [6 empty] | 38.0005 | 13.03 | 14.29
2011-04-17 | 6.335 | 6.055 |  |  |  |  | 7.475 | 1.085 |  |  |  |  | 38 |  |  |  | 0 | 0.337 |  |  | 0.2295 | 0.1175 | [5 empty] | 33.15 |  |  |  |  | 66.3 |  | 27.2 |  | 12.3 | 0.0435 |  | 3.7 | 40.305 | 0.27 |  |  |  |  | 14.4035 | 13.508 | [6 empty] | 38.0004 | 13.555 | 15.8
2011-04-18 | 6.38 | 6.03 |  |  |  |  | 7.47 | 0.98 |  |  |  |  | 44 |  |  |  | 0 | 0.355 |  |  | 0.358 | 0.143 | [5 empty] | 37.1 |  |  |  |  | 74.2 |  | 33.7 |  | 13.9 | 0.001 |  | 3.5 | 40.52 | 0.38 |  |  |  |  | 14.547 | 13.516 | [6 empty] | 38.0004 | 14.08 | 17.31
2011-04-19 | 6.39 | 5.89 |  |  |  |  | 6.98 | 1.15 |  |  |  |  | 46 |  |  |  | 0 | 0.326 |  |  | 0.132 | 0.164 | [5 empty] | 37.5 |  |  |  |  | 75.1 |  | 28.9 |  | 13.1 | 0.057 |  | 3 | 49.85 | 0.43 |  |  |  |  | 15.056 | 14.267 | [6 empty] | 38.0004 | 13.33 | 15.95
2011-04-20 | 6.57 | 6.46 |  |  |  |  | 7.71 | 1.07 |  |  |  |  | 30 |  |  |  | 0 | 0.332 |  |  | 0.109 | 0.089 | [5 empty] | 34.1 |  |  |  |  | 68.2 |  | 28 |  | 12.4 | 0.037 |  | 3.7 | 55.25 | 0.67 |  |  |  |  | 14.915 | 14.382 | [6 empty] | 38.0004 | 13.52 | 18.17
2011-04-21 | 6.46 | 6.45 |  |  |  |  | 7.16 | 0.99 |  |  |  |  | 36 |  |  |  | 0 | 0.339 |  |  | 0.14 | 0.09 | [5 empty] | 34 |  |  |  |  | 68 |  | 22 |  | 9.7 | 0.089 |  | 3.7 | 44.91 | 0.55 |  |  |  |  | 14.839 | 13.208 | [6 empty] | 38.0004 | 14.7 | 14.58
2011-04-22 | 6.09 | 6.18 |  |  |  |  | 7.02 | 0.85 |  |  |  |  | 37 |  |  |  | 0 | 0.339 |  |  | 0.138 | 0.284 | [5 empty] | 34.5 |  |  |  |  | 69 |  | 23.3 |  | 9.4 | 0.075 |  | 3.9 | 40.08 | 0.49 |  |  |  |  | 14.716 | 13.548 | [6 empty] | 38.0004 | 14.34 | 14.72
2011-04-23 | 5.97 | 6.81 |  |  |  |  | 7.92 | 0.93 |  |  |  |  | 35 |  |  |  | 1 | 0.339 |  |  | 0.213 | 0.131 | [5 empty] | 32.6 |  |  |  |  | 65.2 |  | 22.3 |  | 10.8 | 0.053 |  | 3.9 | 44.98 | 0.55 |  |  |  |  | 14.32 | 13.73 | [6 empty] | 38.0004 | 13.52 | 15.77
2011-04-24 | 6.19 | 6.795 |  |  |  |  | 7.76 | 0.98 |  |  |  |  | 34.5 |  |  |  | 0.5 | 0.329 |  |  | 0.1585 | 0.222 | [5 empty] | 34.15 |  |  |  |  | 68.3 |  | 20.95 |  | 9.8 | 0.096 |  | 4 | 44.98 | 0.6 |  |  |  |  | 13.569 | 12.879 | [6 empty] | 38.0004 | 13.93 | 16.16
2011-04-25 | 6.41 | 6.78 |  |  |  |  | 7.6 | 0.94 |  |  |  |  | 34 |  |  |  | 0 | 0.319 |  |  | 0.104 | 0.313 | [5 empty] | 35.7 |  |  |  |  | 71.4 |  | 19.6 |  | 8.8 | 0.139 |  | 4.1 | 49.21 | 0.55 |  |  |  |  | 16.442 | 14.9 | [6 empty] | 38.0004 | 13.725 | 16.55
2011-04-26 | 6.18 | 6.42 |  |  |  |  | 7.13 | 0.97 |  |  |  |  | 39 |  |  |  | 0 | 0.296 |  |  | 0.121 | 0.338 | [5 empty] | 28.7 |  |  |  |  | 57.5 |  | 18.8 |  | 8.2 | 0.062 |  | 4.1 | 45.04 | 0.49 |  |  |  |  | 14.668 | 13.944 | [6 empty] | 38.0004 | 13.8275 | 13.91
2011-04-27 | 5.98 | 6.04 |  |  |  |  | 6.91 | 1.07 |  |  |  |  | 42 |  |  |  | 1 | 0.305 |  |  | 0.097 | 0.332 | [5 empty] | 32.2 |  |  |  |  | 64.4 |  | 20.1 |  | 6.8 | 0.012 |  | 4.1 | 54.57 | 0.57 |  |  |  |  | 15.665 | 15.083 | [6 empty] | 38.0004 | 13.7763 | 14.35
2011-04-28 | 5.74 | 6.12 |  |  |  |  | 7.34 | 1.03 |  |  |  |  | 41 |  |  |  | 0 | 0.314 |  |  | 0.087 | 0.06 | [5 empty] | 32.6 |  |  |  |  | 65.2 |  | 21.6 |  | 9.2 | 0.011 |  | 4.8 | 40.09 | 0.39 |  |  |  |  | 13.694 | 12.801 | [6 empty] | 38.0004 | 13.38 | 17.85
2011-04-29 | 6.28 | 6.11 |  |  |  |  | 7.3 | 1.1 |  |  |  |  | 38 |  |  |  | 0 | 0.31 |  |  | 0.077 | 0.088 | [5 empty] | 33.4 |  |  |  |  | 66.9 |  | 23.6 |  | 15.7 | 0.032 |  | 4.1 | 44.98 | 0.52 |  |  |  |  | 14.162 | 12.629 | [6 empty] | 38.0004 | 13.91 | 13.8
2011-04-30 | 6.3 | 6.16 |  |  |  |  | 6.93 | 1.19 |  |  |  |  | 38 |  |  |  | 0 | 0.302 |  |  | 0.089 | 0.161 | [5 empty] | 33.6 |  |  |  |  | 67.2 |  | 22 |  | 13.3 | 0.054 |  | 4.3 | 44.98 | 0.34 |  |  |  |  | 13.48 | 13.36 | [6 empty] | 38.0004 | 11.91 | 11.66
2011-05-01 | 6.09 | 6.385 |  |  |  |  | 7.255 | 1.06 |  |  |  |  | 41 |  |  |  | 0 | 0.335 |  |  | 0.0875 | 0.113 | [5 empty] | 33.15 |  |  |  |  | 66.3 |  | 22.65 |  | 10.65 | 0.0335 |  | 4.35 | 44.98 | 0.5 |  |  |  |  | 12.837 | 11.304 | [6 empty] | 38.0004 | 12.715 | 12.415
2011-05-02 | 5.88 | 6.61 |  |  |  |  | 7.58 | 0.93 |  |  |  |  | 44 |  |  |  | 0 | 0.368 |  |  | 0.086 | 0.065 | [5 empty] | 32.7 |  |  |  |  | 65.4 |  | 23.3 |  | 8 | 0.013 |  | 4.4 | 44.98 | 0.66 |  |  |  |  | 14.32 | 12.856 | [6 empty] | 38.0004 | 13.52 | 13.17
2011-05-03 | 5.94 | 6.79 |  |  |  |  | 7.69 | 0.91 |  |  |  |  | 38 |  |  |  | 0 | 0.337 |  |  | 0.083 | 0.288 | [5 empty] | 31.6 |  |  |  |  | 63.2 |  | 22.3 |  | 12.25 | 0 |  | 4.5 | 39.6 | 0.39 |  |  |  |  | 14.399 | 13.799 | [6 empty] | 38.0004 | 11.95 | 15.6
2011-05-04 | 6.37 | 6.27 |  |  |  |  | 6.89 | 0.99 |  |  |  |  | 36 |  |  |  | 0 | 0.321 |  |  | 0.108 | 0.25 | [5 empty] | 32.1 |  |  |  |  | 64.3 |  | 24.1 |  | 16.5 | 0.014 |  | 4.6 | 39.67 | 0.37 |  |  |  |  | 13.58 | 13.205 | [6 empty] | 38.0004 | 14.01 | 11.28
2011-05-05 | 6.36 | 6.21 |  |  |  |  | 7.19 | 1.18 |  |  |  |  | 34 |  |  |  | 0 | 0.383 |  |  | 0.196 | 0.197 | [5 empty] | 29.6 |  |  |  |  | 59.1 |  | 25.6 |  | 15.8 | 0.016 |  | 4.8 | 40.15 | 0.28 |  |  |  |  | 13.634 | 12.898 | [6 empty] | 38.0004 | 12.88 | 11.25
2011-05-06 | 6.24 | 6.5 |  |  |  |  | 7.63 | 1.53 |  |  |  |  | 39 |  |  |  | 0 | 0.373 |  |  | 0.088 | 0.183 | [5 empty] | 31.5 |  |  |  |  | 63.1 |  | 26.3 |  | 14.4 | 0.096 |  | 5.4 | 44.98 | 0.12 |  |  |  |  | 13.416 | 12.67 | [6 empty] | 38.0004 | 20 | 13.01
2011-05-07 | 6.16 | 6.12 |  |  |  |  | 7.2 | 1.36 |  |  |  |  | 30 |  |  |  | 0 | 0.399 |  |  | 0.099 | 0.206 | [5 empty] | 34.1 |  |  |  |  | 68.3 |  | 19.6 |  | 8.7 | 0.101 |  | 5.2 | 40.18 | 0.005 |  |  |  |  | 13.37 | 12.9 | [6 empty] | 38.0004 | 16.8 | 14.95
2011-05-08 | 6.58 | 6.285 |  |  |  |  | 7.3 | 1.21 |  |  |  |  | 33 |  |  |  | 0 | 0.4945 |  |  | 0.095 | 0.207 | [5 empty] | 33.45 |  |  |  |  | 67 |  | 24 |  | 8.2 | 0.0995 |  | 5.7 | 40.345 | 0.2075 |  |  |  |  | 13.7595 | 12.69 | [6 empty] | 38.0004 | 15.035 | 13.03
2011-05-09 | 7 | 6.45 |  |  |  |  | 7.4 | 1.06 |  |  |  |  | 36 |  |  |  | 0 | 0.59 |  |  | 0.091 | 0.208 | [5 empty] | 32.8 |  |  |  |  | 65.7 |  | 28.4 |  | 7.7 | 0.098 |  | 6.2 | 40.51 | 0.41 |  |  |  |  | 14.149 | 12.48 | [6 empty] | 38.0004 | 13.27 | 11.11
2011-05-10 | 6.55 | 6.61 |  |  |  |  | 7 | 0.95 |  |  |  |  | 35 |  |  |  | 0 | 0.544 |  |  | 0.089 | 0.199 | [5 empty] | 29.5 |  |  |  |  | 59 |  | 26.5 |  | 8.4 | 0.103 |  | 6.6 | 45.47 | 0.81 |  |  |  |  | 13.428 | 11.743 | [6 empty] | 38.0004 | 12.76 | 10.12
2011-05-11 | 6.4 | 5.97 |  |  |  |  | 6.88 | 0.93 |  |  |  |  | 34 |  |  |  | 0 | 0.57 |  |  | 0.104 | 0.266 | [5 empty] | 30.1 |  |  |  |  | 60.2 |  | 26.2 |  | 10.1 | 0.112 |  | 7.9 | 39.45 | 0.72 |  |  |  |  | 12.525 | 10.824 | [6 empty] | 38.0004 | 11.82 | 14.17
2011-05-12 | 6.49 | 6.68 |  |  |  |  | 7.92 | 0.87 |  |  |  |  | 40 |  |  |  | 0 | 0.638 |  |  | 0.1 | 0.073 | [5 empty] | 30 |  |  |  |  | 60 |  | 26.9 |  | 8.6 | 0.051 |  | 7.4 | 35.19 | 0.43 |  |  |  |  | 13.17 | 12.282 | [6 empty] | 38.0004 | 7.96 | 10.79
2011-05-13 | 6.48 | 6.76 |  |  |  |  | 8.09 | 0.94 |  |  |  |  | 43 |  |  |  | 0 | 0.614 |  |  | 0.103 | 0.079 | [5 empty] | 34 |  |  |  |  | 68 |  | 24.6 |  | 9.7 | 0.094 |  | 7.5 | 44.98 | 0.62 |  |  |  |  | 13.9 | 13.05 | [6 empty] | 38.0004 | 5.21 | 13.92
2011-05-14 | 6.485 | 6.72 |  |  |  |  | 8.005 | 0.905 |  |  |  |  | 41.5 |  |  |  | 0 | 0.626 |  |  | 0.1015 | 0.076 | [5 empty] | 32 |  |  |  |  | 64 |  | 25.75 |  | 9.15 | 0.0725 |  | 7.45 | 42.535 | 0.64 |  |  |  |  | 13.61 | 13.51 | [6 empty] | 38.0004 | 6.585 | 12.355
2011-05-15 | 6.4825 | 6.74 |  |  |  |  | 8.0475 | 0.9225 |  |  |  |  | 42.25 |  |  |  | 0 | 0.62 |  |  | 0.10225 | 0.0775 | [5 empty] | 33 |  |  |  |  | 66 |  | 25.175 |  | 9.425 | 0.08325 |  | 7.475 | 40.09 | 0.66 |  |  |  |  | 12.274 | 11.371 | [6 empty] | 38.0004 | 5.8975 | 13.1375
2011-05-16 | 6.48 | 5.93 |  |  |  |  | 7.84 | 0.963 |  |  |  |  | 30 |  |  |  | 0 | 0.73 |  |  | 0.113 | 0.129 | [5 empty] | 30.2 |  |  |  |  | 60.4 |  | 20.9 |  | 9.2 | 0.109 |  | 7.4 | 44.98 | 0.72 |  |  |  |  | 14.032 | 12.408 | [6 empty] | 38.0004 | 12.29 | 13.92
2011-05-17 | 6.26 | 6.57 |  |  |  |  | 7.25 | 0.99 |  |  |  |  | 34 |  |  |  | 0 | 0.663 |  |  | 0.097 | 0.166 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 19.6 |  | 8.6 | 0.042 |  | 7.8 | 44.98 | 0.83 |  |  |  |  | 12.92 | 11.198 | [6 empty] | 38.0004 | 13.26 | 15.62
2011-05-18 | 6.39 | 6.04 |  |  |  |  | 7.13 | 0.92 |  |  |  |  | 30 |  |  |  | 0 | 0.621 |  |  | 0.094 | 0.089 | [5 empty] | 29.1 |  |  |  |  | 58.2 |  | 21.9 |  | 8.7 | 0.079 |  | 8.3 | 39.4 | 0.71 |  |  |  |  | 12.659 | 10.963 | [6 empty] | 38.0004 | 15.26 | 16.16
2011-05-19 | 6.21 | 6.53 |  |  |  |  | 7.39 | 0.86 |  |  |  |  | 29 |  |  |  | 0 | 0.693 |  |  | 0.092 | 0.104 | [5 empty] | 28.8 |  |  |  |  | 57.6 |  | 22.9 |  | 8.9 | 0.073 |  | 8.1 | 45.4 | 0.79 |  |  |  |  | 13.42 | 12.51 | [6 empty] | 38.0004 | 14.69 | 14.41
2011-05-20 | 6.56 | 5.97 |  |  |  |  | 6.46 | 0.91 |  |  |  |  | 33 |  |  |  | 0 | 0.96 |  |  | 0.102 | 0.178 | [5 empty] | 29.1 |  |  |  |  | 58.3 |  | 22 |  | 9.3 | 0.061 |  | 8.2 | 40.09 | 0.6 |  |  |  |  | 12.892 | 12.031 | [6 empty] | 38.0004 | 11.26 | 10.78
2011-05-21 | 6.39 | 6.04 |  |  |  |  | 7.77 | 0.86 |  |  |  |  | 34 |  |  |  | 0 | 0.927 |  |  | 0.092 | 0.086 | [5 empty] | 27.7 |  |  |  |  | 55.3 |  | 21.7 |  | 9.2 | 0.054 |  | 9.1 | 39.6 | 0.6 |  |  |  |  | 12.37 | 12.29 | [6 empty] | 38.0004 | 8.59 | 11.29
2011-05-22 | 6.32 | 6.235 |  |  |  |  | 7.77 | 0.94 |  |  |  |  | 34 |  |  |  | 0 | 0.9335 |  |  | 0.0975 | 0.085 | [5 empty] | 29 |  |  |  |  | 57.95 |  | 20.9 |  | 7.65 | 0.0765 |  | 8.55 | 35.19 | 0.52 |  |  |  |  | 11.832 | 10.913 | [6 empty] | 38.0004 | 8.59 | 11.29
2011-05-23 | 6.25 | 6.43 |  |  |  |  | 7.77 | 0.83 |  |  |  |  | 34 |  |  |  | 0 | 0.94 |  |  | 0.103 | 0.084 | [5 empty] | 30.3 |  |  |  |  | 60.6 |  | 20.1 |  | 6.1 | 0.099 |  | 8 | 40.11 | 0.66 |  |  |  |  | 13.842 | 12.195 | [6 empty] | 38.0004 | 10.15 | 12.56
2011-05-24 | 6.5 | 6.69 |  |  |  |  | 8.13 | 0.76 |  |  |  |  | 36 |  |  |  | 0 | 0.826 |  |  | 0.088 | 0.088 | [5 empty] | 28.4 |  |  |  |  | 57.8 |  | 21.1 |  | 6 | 0.129 |  | 8.4 | 40.09 | 0.79 |  |  |  |  | 13.477 | 11.764 | [6 empty] | 38.0004 | 8.99 | 12.76
2011-05-25 | 6.43 | 5.94 |  |  |  |  | 6.55 | 0.75 |  |  |  |  | 35 |  |  |  | 0 | 1.913 |  |  | 0.102 | 0.185 | [5 empty] | 28.1 |  |  |  |  | 57.1 |  | 22 |  | 5.2 | 0.112 |  | 8.8 | 36.16 | 0.74 |  |  |  |  | 12.679 | 11.004 | [6 empty] | 38.0004 | 9.44 | 10.67
2011-05-26 | 6.28 | 6.48 |  |  |  |  | 7.9 | 0.68 |  |  |  |  | 41 |  |  |  | 0 | 1.103 |  |  | 0.091 | 0.123 | [5 empty] | 28.6 |  |  |  |  | 57.2 |  | 24.7 |  | 7.7 | 0.056 |  | 8.8 | 35.21 | 0.61 |  |  |  |  | 13.329 | 12.434 | [6 empty] | 38.0004 | 10.42 | 10.35
2011-05-27 | 6.39 | 6.34 |  |  |  |  | 7.44 | 0.86 |  |  |  |  | 37 |  |  |  | 0 | 1.074 |  |  | 0.084 | 0.137 | [5 empty] | 27.2 |  |  |  |  | 54.4 |  | 26.3 |  | 8.2 | 0.067 |  | 9.9 | 60.13 | 1.15 |  |  |  |  | 14.411 | 13.558 | [6 empty] | 38.0004 | 14 | 14.26
2011-05-28 | 6.21 | 6.26 |  |  |  |  | 6.63 | 0.96 |  |  |  |  | 35 |  |  |  | 0 | 0.866 |  |  | 0.098 | 0.176 | [5 empty] | 26.3 |  |  |  |  | 52.6 |  | 25.5 |  | 5 | 0.059 |  | 15 | 59.54 | 1.2 |  |  |  |  | 12.99 | 12.5 | [6 empty] | 38.0004 | 13.87 | 12.64
2011-05-29 | 6.34 | 6.905 |  |  |  |  | 7.34 | 0.865 |  |  |  |  | 37 |  |  |  | 0 | 0.865 |  |  | 0.0975 | 0.13 | [5 empty] | 27.15 |  |  |  |  | 54.3 |  | 25 |  | 5.95 | 0.06 |  | 12.85 | 52.56 | 1.055 |  |  |  |  | 13.0715 | 12.395 | [6 empty] | 38.0004 | 13.87 | 12.64
2011-05-30 | 6.47 | 7.55 |  |  |  |  | 8.05 | 0.77 |  |  |  |  | 39 |  |  |  | 0 | 0.864 |  |  | 0.097 | 0.084 | [5 empty] | 28 |  |  |  |  | 56 |  | 24.5 |  | 6.9 | 0.061 |  | 10.7 | 45.58 | 0.91 |  |  |  |  | 13.153 | 12.29 | [6 empty] | 38.0004 | 13.87 | 12.64
2011-05-31 | 6.46 | 6.42 |  |  |  |  | 7.23 | 0.96 |  |  |  |  | 36 |  |  |  | 0 | 0.806 |  |  | 0.091 | 0.074 | [5 empty] | 27 |  |  |  |  | 54 |  | 23.3 |  | 6.5 | 0.042 |  | 10.6 | 49.56 | 1.03 |  |  |  |  | 13.593 | 12.696 | [6 empty] | 38.0004 | 10.81 | 10.215
2011-06-01 | 6.7 | 6.07 |  |  |  |  | 6.82 | 1.01 |  |  |  |  | 30 |  |  |  | 0 | 0.755 |  |  | 0.119 | 0.213 | [5 empty] | 26 |  |  |  |  | 52 |  | 25 |  | 7.1 | 0.059 |  | 11.2 | 53.54 | 0.96 |  |  |  |  | 13.271 | 12.338 | [6 empty] | 38.0004 | 7.75 | 7.79
2011-06-02 | 6.21 | 6.23 |  |  |  |  | 6.76 | 0.84 |  |  |  |  | 49 |  |  |  | 0 | 0.893 |  |  | 0.118 | 0.367 | [5 empty] | 28.3 |  |  |  |  | 56.6 |  | 23.2 |  | 7.1 | 0.108 |  | 10.6 | 49.37 | 1.05 |  |  |  |  | 12.739 | 11.833 | [6 empty] | 38.0004 | 10.5 | 10.02
2011-06-03 | 6.18 | 6.44 |  |  |  |  | 8.5 | 0.98 |  |  |  |  | 47 |  |  |  | 0 | 1.164 |  |  | 0.086 | 0.127 | [5 empty] | 31 |  |  |  |  | 62 |  | 24.5 |  | 8.3 | 0.097 |  | 10.7 | 55.26 | 1.06 |  |  |  |  | 13.556 | 12.313 | [6 empty] | 38.0004 | 14.33 | 13.19
2011-06-04 | 6.44 | 6.65 |  |  |  |  | 7.79 | 1.05 |  |  |  |  | 45 |  |  |  | 0 | 0.914 |  |  | 0.101 | 0.097 | [5 empty] | 30.6 |  |  |  |  | 61.2 |  | 23.1 |  | 7.6 | 0.101 |  | 10.2 | 54.75 | 0.81 |  |  |  |  | 13.85 | 13.33 | [6 empty] | 38.0004 | 12.04 | 9.15
2011-06-05 | 6.49 | 6.525 |  |  |  |  | 7.44 | 0.96 |  |  |  |  | 39 |  |  |  | 0 | 0.8435 |  |  | 0.0975 | 0.082 | [5 empty] | 30.35 |  |  |  |  | 60.7 |  | 24.4 |  | 7.65 | 0.096 |  | 10.45 | 55.26 | 0.98 |  |  |  |  | 13.097 | 13.613 | [6 empty] | 38.0004 | 11.43 | 8.905
2011-06-06 | 6.54 | 6.4 |  |  |  |  | 7.09 | 0.87 |  |  |  |  | 33 |  |  |  | 0 | 0.773 |  |  | 0.094 | 0.067 | [5 empty] | 30.1 |  |  |  |  | 60.2 |  | 25.7 |  | 7.7 | 0.091 |  | 10.7 | 49.88 | 0.91 |  |  |  |  | 13.244 | 12.76 | [6 empty] | 38.0004 | 10.82 | 8.66
2011-06-07 | 6.36 | 6.58 |  |  |  |  | 7.28 | 0.96 |  |  |  |  | 40 |  |  |  | 0 | 0.679 |  |  | 0.099 | 0.068 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 23.2 |  | 7.4 | 0.089 |  | 11.9 | 55.24 | 1.07 |  |  |  |  | 13.967 | 12.346 | [6 empty] | 38.0004 | 11.55 | 9.99
2011-06-08 | 6.51 | 6.73 |  |  |  |  | 7.45 | 0.92 |  |  |  |  | 43 |  |  |  | 0 | 0.638 |  |  | 0.096 | 0.084 | [5 empty] | 30.5 |  |  |  |  | 61 |  | 24.3 |  | 7.7 | 0.087 |  | 10.4 | 54.77 | 1.18 |  |  |  |  | 13.483 | 11.838 | [6 empty] | 38.0004 | 14.28 | 10.71
2011-06-09 | 6.55 | 6.79 |  |  |  |  | 7.1 | 0.83 |  |  |  |  | 44 |  |  |  | 0 | 0.637 |  |  | 0.088 | 0.135 | [5 empty] | 30.9 |  |  |  |  | 61.8 |  | 22.7 |  | 7.1 | 0.032 |  | 12.1 | 54.6 | 1.3 |  |  |  |  | 13.362 | 11.655 | [6 empty] | 38.0004 | 9.72 | 10.73
2011-06-10 | 6.44 | 6.44 |  |  |  |  | 7.34 | 0.83 |  |  |  |  | 42 |  |  |  | 0 | 0.918 |  |  | 0.097 | 0.076 | [5 empty] | 30.1 |  |  |  |  | 60.2 |  | 24.2 |  | 7.6 | 0.048 |  | 12.9 | 49.88 | 0.98 |  |  |  |  | 13.452 | 12.489 | [6 empty] | 38.0004 | 10.68 | 11.36
2011-06-11 | 6.59 | 6.74 |  |  |  |  | 7.18 | 1.19 |  |  |  |  | 45 |  |  |  | 0 | 1.022 |  |  | 0.072 | 0.09 | [5 empty] | 30.1 |  |  |  |  | 60.3 |  | 22.5 |  | 8.1 | 0.044 |  | 13.4 | 71.02 | 1.39 |  |  |  |  | 13.53 | 12.51 | [6 empty] | 38.0004 | 11.64 | 11.99
2011-06-12 | 6.5 | 6.395 |  |  |  |  | 7.03 | 1.23 |  |  |  |  | 46 |  |  |  | 0 | 1.009 |  |  | 0.078 | 0.113 | [5 empty] | 30.3 |  |  |  |  | 60.65 |  | 22.8 |  | 7.65 | 0.05 |  | 12.55 | 59.54 | 1.13 |  |  |  |  | 12.666 | 11.474 | [6 empty] | 38.0004 | 11.64 | 11.99
2011-06-13 | 6.41 | 6.05 |  |  |  |  | 6.88 | 1.11 |  |  |  |  | 47 |  |  |  | 0 | 0.996 |  |  | 0.084 | 0.136 | [5 empty] | 30.5 |  |  |  |  | 61 |  | 23.1 |  | 7.2 | 0.056 |  | 11.7 | 50.3 | 0.77 |  |  |  |  | 12.678 | 12.168 | [6 empty] | 38.0004 | 11.75 | 12.28
2011-06-14 | 6.24 | 6.16 |  |  |  |  | 8.02 | 1.08 |  |  |  |  | 32 |  |  |  | 0 | 1.714 |  |  | 0.096 | 0.084 | [5 empty] | 30.8 |  |  |  |  | 61.6 |  | 22.1 |  | 7.9 | 0.041 |  | 11.8 | 60.13 | 0.99 |  |  |  |  | 14.56 | 13.18 | [6 empty] | 38.0004 | 13.72 | 12.39
2011-06-15 | 6.37 | 6.34 |  |  |  |  | 7.64 | 1.01 |  |  |  |  | 50 |  |  |  | 0 | 0.607 |  |  | 0.102 | 0.13 | [5 empty] | 28.8 |  |  |  |  | 57.6 |  | 24.1 |  | 7.7 | 0.067 |  | 12.7 | 61.74 | 1.28 |  |  |  |  | 13.655 | 12.251 | [6 empty] | 38.0004 | 13.72 | 12.39
2011-06-16 | 6.39 | 6.26 |  |  |  |  | 6.97 | 0.97 |  |  |  |  | 46 |  |  |  | 0 | 0.916 |  |  | 0.087 | 0.083 | [5 empty] | 27.5 |  |  |  |  | 55 |  | 23.4 |  | 7.9 | 0.051 |  | 12.4 | 48.51 | 0.86 |  |  |  |  | 12.539 | 12.016 | [6 empty] | 38.0004 | 13.72 | 12.39
2011-06-17 | 6.08 | 6.25 |  |  |  |  | 7.26 | 1.07 |  |  |  |  | 39 |  |  |  | 0 | 1.236 |  |  | 0.079 | 0.176 | [5 empty] | 29.8 |  |  |  |  | 59.6 |  | 25.1 |  | 8 | 0.092 |  | 12.4 | 50.36 | 0.82 |  |  |  |  | 12.599 | 12.081 | [6 empty] | 38.0004 | 12.79 | 11.54
2011-06-18 | 6.04 | 6.2 |  |  |  |  | 7.2 | 1.13 |  |  |  |  | 39 |  |  |  | 0 | 1.95 |  |  | 0.101 | 0.209 | [5 empty] | 26.4 |  |  |  |  | 52.8 |  | 25.1 |  | 8.1 | 0.067 |  | 12.6 | 54.27 | 0.49 |  |  |  |  | 15.02 | 15.19 | [6 empty] | 38.0004 | 12.56 | 11.36
2011-06-19 | 6.19 | 6.095 |  |  |  |  | 7.26 | 1.055 |  |  |  |  | 37.5 |  |  |  | 0 | 1.409 |  |  | 0.095 | 0.183 | [5 empty] | 26.7 |  |  |  |  | 53.45 |  | 25.85 |  | 8.2 | 0.059 |  | 12.5 | 52.075 | 0.715 |  |  |  |  | 13.8885 | 13.4975 | [6 empty] | 38.0004 | 13.015 | 11.06
2011-06-20 | 6.34 | 5.99 |  |  |  |  | 7.32 | 0.98 |  |  |  |  | 36 |  |  |  | 0 | 0.868 |  |  | 0.089 | 0.157 | [5 empty] | 27 |  |  |  |  | 54.1 |  | 26.6 |  | 8.3 | 0.051 |  | 12.4 | 49.88 | 0.94 |  |  |  |  | 12.757 | 11.805 | [6 empty] | 38.0004 | 13.47 | 10.76
2011-06-21 | 6.72 | 6.31 |  |  |  |  | 7.54 | 0.93 |  |  |  |  | 35 |  |  |  | 0 | 0.418 |  |  | 0.1 | 0.092 | [5 empty] | 31.9 |  |  |  |  | 63.9 |  | 23 |  | 7.3 | 0.059 |  | 10.8 | 54.92 | 1.14 |  |  |  |  | 13.038 | 12.034 | [6 empty] | 38.0004 | 14.23 | 11.2
2011-06-22 | 6.19 | 5.74 |  |  |  |  | 6.33 | 0.93 |  |  |  |  | 36 |  |  |  | 0 | 2.209 |  |  | 0.117 | 0.313 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 24.4 |  | 7.9 | 0.071 |  | 11.2 | 50.54 | 1 |  |  |  |  | 12.901 | 11.885 | [6 empty] | 35.26 | 12.62 | 11.72
2011-06-23 | 6.07 | 6.49 |  |  |  |  | 7.57 | 1.19 |  |  |  |  | 40 |  |  |  | 0 | 2.067 |  |  | 0.104 | 0.079 | [5 empty] | 29.7 |  |  |  |  | 59.5 |  | 21.9 |  | 7.1 | 0.066 |  | 11.2 | 64.47 | 1.12 |  |  |  |  | 13.724 | 12.656 | [6 empty] | 31.57 | 14.16 | 10.75
2011-06-24 | 5.52 | 6.29 |  |  |  |  | 7.29 | 1.16 |  |  |  |  | 44 |  |  |  | 0 | 3.536 |  |  | 0.092 | 0.114 | [5 empty] | 29.1 |  |  |  |  | 58.2 |  | 22.9 |  | 7.3 | 0.061 |  | 10.3 | 65.47 | 1.14 |  |  |  |  | 13.888 | 12.912 | [6 empty] | 34.68 | 13.34 | 10.75
2011-06-25 | 6.06 | 6.18 |  |  |  |  | 7.48 | 1.16 |  |  |  |  | 43 |  |  |  | 0 | 3.146 |  |  | 0.097 | 0.093 | [5 empty] | 32 |  |  |  |  | 64 |  | 23.5 |  | 7.2 | 0.058 |  | 10.9 | 60.22 | 1.11 |  |  |  |  | 12.565 | 12.02 | [6 empty] | 33.31 | 13.38 | 12.5
2011-06-26 | 6.255 | 6.28 |  |  |  |  | 7.725 | 1.15 |  |  |  |  | 46 |  |  |  | 0 | 3.2965 |  |  | 0.1005 | 0.1545 | [5 empty] | 31.5 |  |  |  |  | 63 |  | 22.1 |  | 7.3 | 0.063 |  | 11.35 | 60.13 | 1.07 |  |  |  |  | 12.814 | 12.26 | [6 empty] | 31.955 | 13.02 | 14.64
2011-06-27 | 6.45 | 6.38 |  |  |  |  | 7.97 | 1.14 |  |  |  |  | 49 |  |  |  | 0 | 3.447 |  |  | 0.104 | 0.216 | [5 empty] | 31 |  |  |  |  | 62 |  | 20.7 |  | 7.4 | 0.068 |  | 11.8 | 60.13 | 1.05 |  |  |  |  | 13.018 | 12.483 | [6 empty] | 30.6 | 12.66 | 16.78
2011-06-28 | 6.19 | 6.52 |  |  |  |  | 7.23 | 1.14 |  |  |  |  | 44 |  |  |  | 0 | 2.697 |  |  | 0.123 | 0.297 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 24.9 |  | 6.8 | 0.071 |  | 11.7 | 65.05 | 1.18 |  |  |  |  | 14.075 | 12.708 | [6 empty] | 31.93 | 13.98 | 10.24
2011-06-29 | 6.29 | 6.92 |  |  |  |  | 7.49 | 1.04 |  |  |  |  | 44 |  |  |  | 0 | 2.802 |  |  | 0.099 | 0.254 | [5 empty] | 31.1 |  |  |  |  | 62.3 |  | 24.3 |  | 7.4 | 0.079 |  | 12.2 | 60.79 | 1.21 |  |  |  |  | 13.648 | 12.271 | [6 empty] | 29.78 | 13.17 | 11.2
2011-06-30 | 6.49 | 6.98 |  |  |  |  | 7.91 | 1.12 |  |  |  |  | 46 |  |  |  | 0 | 2.743 |  |  | 0.114 | 0.343 | [5 empty] | 30.1 |  |  |  |  | 60.2 |  | 23.5 |  | 8.8 | 0.112 |  | 12 | 65.33 | 0.96 |  |  |  |  | 14.783 | 14.277 | [6 empty] | 31.67 | 12.7 | 11.39
2011-07-01 | 6.68 | 6.19 |  |  |  |  | 7.37 | 1.03 |  |  |  |  | 44 |  |  |  | 0 | 3.812 |  |  | 0.087 | 0.165 | [5 empty] | 31.2 |  |  |  |  | 62.5 |  | 21.5 |  | 9.2 | 0.098 |  | 12.4 | 60.13 | 1.23 |  |  |  |  | 13.02 | 12.091 | [6 empty] | 28.17 | 9.45 | 12.65
2011-07-02 | 6.58 | 6.21 |  |  |  |  | 6.7 | 0.85 |  |  |  |  | 42 |  |  |  | 0 | 0.509 |  |  | 0.082 | 0.078 | [5 empty] | 32.1 |  |  |  |  | 64.3 |  | 23.5 |  | 9.6 | 0.104 |  | 12.5 | 60.13 | 1.18 |  |  |  |  | 13.9 | 13.43 | [6 empty] | 28.64 | 10.02 | 10.2
2011-07-03 | 6.495 | 6.37 |  |  |  |  | 7.29 | 0.96 |  |  |  |  | 43 |  |  |  | 0 | 0.676 |  |  | 0.0865 | 0.097 | [5 empty] | 30.5 |  |  |  |  | 61.05 |  | 23.15 |  | 9.45 | 0.0955 |  | 13.15 | 60.12 | 1.13 |  |  |  |  | 14.312 | 13.785 | [6 empty] | 28.64 | 10.02 | 10.2
2011-07-04 | 6.41 | 6.53 |  |  |  |  | 7.88 | 1.07 |  |  |  |  | 44 |  |  |  | 0 | 0.843 |  |  | 0.091 | 0.116 | [5 empty] | 28.9 |  |  |  |  | 57.8 |  | 22.8 |  | 9.3 | 0.087 |  | 13.8 | 74.82 | 1.36 |  |  |  |  | 14.878 | 13.988 | [6 empty] | 24.83 | 9.84 | 10.5
2011-07-05 | 6.22 | 6.47 |  |  |  |  | 7.74 | 1.11 |  |  |  |  | 47 |  |  |  | 0 | 1.411 |  |  | 0.108 | 0.141 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 23.8 |  | 8.6 | 0.073 |  | 14 | 74.89 | 1.34 |  |  |  |  | 14.785 | 13.851 | [6 empty] | 25.61 | 10.54 | 11.37
2011-07-06 | 6.58 | 6.11 |  |  |  |  | 7.48 | 1.04 |  |  |  |  | 43 |  |  |  | 0 | 1.367 |  |  | 0.089 | 0.145 | [5 empty] | 30.1 |  |  |  |  | 60.1 |  | 26.5 |  | 9.2 | 0.045 |  | 14.2 | 69.89 | 1.12 |  |  |  |  | 15.597 | 14.707 | [6 empty] | 29.57 | 8.56 | 11.76
2011-07-07 | 6.62 | 6.29 |  |  |  |  | 7.11 | 1.09 |  |  |  |  | 43 |  |  |  | 0 | 1.334 |  |  | 0.091 | 0.098 | [5 empty] | 30.6 |  |  |  |  | 61.1 |  | 23.3 |  | 9.3 | 0.062 |  | 14.4 | 79.02 | 1.35 |  |  |  |  | 15.68 | 14.717 | [6 empty] | 28.64 | 8.58 | 12.01
2011-07-08 | 6.31 | 6.55 |  |  |  |  | 7.32 | 1.1 |  |  |  |  | 45 |  |  |  | 0 | 1.167 |  |  | 0.111 | 0.112 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 23.7 |  | 9.6 | 0.071 |  | 15.4 | 80.13 | 1.43 |  |  |  |  | 15.43 | 14.4 | [6 empty] | 27.94 | 8.62 | 11.03
2011-07-09 | 6.465 | 6.42 |  |  |  |  | 7.215 | 1.095 |  |  |  |  | 44 |  |  |  | 0 | 1.2505 |  |  | 0.101 | 0.105 | [5 empty] | 29.9 |  |  |  |  | 59.75 |  | 23.5 |  | 9.45 | 0.0665 |  | 14.9 | 79.575 | 1.39 |  |  |  |  | 15.555 | 14.5585 | [6 empty] | 28.29 | 8.6 | 11.52
2011-07-10 | 6.3875 | 6.485 |  |  |  |  | 7.2675 | 1.0975 |  |  |  |  | 44.5 |  |  |  | 0 | 1.2088 |  |  | 0.106 | 0.1085 | [5 empty] | 29.55 |  |  |  |  | 59.075 |  | 23.6 |  | 9.525 | 0.06875 |  | 15.15 | 79.8525 | 1.41 |  |  |  |  | 15.4925 | 14.4793 | [6 empty] | 28.115 | 8.61 | 11.275
2011-07-11 | 7.01 | 6.57 |  |  |  |  | 7.19 | 1.15 |  |  |  |  | 38 |  |  |  | 0 | 2.021 |  |  | 0.09 | 0.138 | [5 empty] | 28.8 |  |  |  |  | 57.7 |  | 25.4 |  | 6.5 | 0.059 |  | 15.3 | 80.61 | 1.23 |  |  |  |  | 15.86 | 15.346 | [6 empty] | 26.76 | 7.28 | 12
2011-07-12 | 6.57 | 6.32 |  |  |  |  | 7.48 | 0.96 |  |  |  |  | 38 |  |  |  | 0 | 2.794 |  |  | 0.087 | 0.103 | [5 empty] | 28.9 |  |  |  |  | 57.8 |  | 25.8 |  | 7.2 | 0.061 |  | 15.4 | 50.45 | 1.235 |  |  |  |  | 13.704 | 12.969 | [6 empty] | 26.76 | 5.62 | 11.99
2011-07-13 | 6.42 | 5.97 |  |  |  |  | 7.02 | 1.15 |  |  |  |  | 37 |  |  |  | 0 | 1.387 |  |  | 0.097 | 0.154 | [5 empty] | 29.8 |  |  |  |  | 59.6 |  | 24.4 |  | 7 | 0.073 |  | 15.5 | 69.92 | 1.24 |  |  |  |  | 13.92 | 13.299 | [6 empty] | 26.76 | 5.62 | 11.99
2011-07-14 | 6.48 | 6.22 |  |  |  |  | 7.23 | 1.09 |  |  |  |  | 41.5 |  |  |  | 0 | 1.515 |  |  | 0.0875 | 0.114 | [5 empty] | 29.85 |  |  |  |  | 59.7 |  | 23.75 |  | 6.9 | 0.0625 |  | 15.35 | 70.82 | 1.33 |  |  |  |  | 14.334 | 13.27 | [6 empty] | 26.76 | 5.62 | 11.99
2011-07-15 | 6.54 | 6.47 |  |  |  |  | 7.44 | 1.29 |  |  |  |  | 46 |  |  |  | 0 | 1.643 |  |  | 0.078 | 0.074 | [5 empty] | 29.9 |  |  |  |  | 59.8 |  | 23.1 |  | 6.8 | 0.052 |  | 15.2 | 74.82 | 1.42 |  |  |  |  | 13.139 | 12.525 | [6 empty] | 30.48 | 4.52 | 10.17
2011-07-16 | 6.52 | 6.46 |  |  |  |  | 6.5 | 0.91 |  |  |  |  | 38 |  |  |  | 0 | 1.845 |  |  | 0.096 | 0.574 | [5 empty] | 27.7 |  |  |  |  | 54 |  | 19.2 |  | 6.1 | 0.005 |  | 14.7 | 70.41 | 1.71 |  |  |  |  | 12.838 | 12.191 | [6 empty] | 31.52 | 5.07 | 10.4
2011-07-17 | 6.715 | 6.675 |  |  |  |  | 7.16 | 0.68 |  |  |  |  | 38 |  |  |  | 0 | 1.741 |  |  | 0.1575 | 0.3435 | [5 empty] | 24.85 |  |  |  |  | 49 |  | 20.35 |  | 6.05 | 0.1015 |  | 14.8 | 79.69 | 2.22 |  |  |  |  | 13.553 | 12.47 | [6 empty] | 27.355 | 4.795 | 11.565
2011-07-18 | 6.91 | 6.89 |  |  |  |  | 7.82 | 1.25 |  |  |  |  | 38 |  |  |  | 0 | 1.637 |  |  | 0.219 | 0.113 | [5 empty] | 22 |  |  |  |  | 44 |  | 21.5 |  | 6 | 0.198 |  | 14.9 | 100.24 | 2.09 |  |  |  |  | 14.352 | 13.629 | [6 empty] | 23.19 | 4.9325 | 12.73
2011-07-19 | 6.89 | 6.42 |  |  |  |  | 7.17 | 1.25 |  |  |  |  | 41 |  |  |  | 0 | 1.692 |  |  | 0.241 | 0.206 | [5 empty] | 26.7 |  |  |  |  | 53.4 |  | 19.7 |  | 6.1 | 0.154 |  | 15.3 | 100.28 | 2.24 |  |  |  |  | 14.251 | 13.05 | [6 empty] | 25.01 | 4.8637 | 13.64
2011-07-20 | 6.58 | 6.21 |  |  |  |  | 7.1 | 0.92 |  |  |  |  | 40 |  |  |  | 0 | 2.407 |  |  | 0.152 | 0.372 | [5 empty] | 32.1 |  |  |  |  | 64.2 |  | 22.2 |  | 7.3 | 0.192 |  | 15.5 | 89.96 | 2.25 |  |  |  |  | 13.953 | 12.095 | [6 empty] | 24.21 | 4.8981 | 15.02
2011-07-21 | 6.49 | 6.39 |  |  |  |  | 7.26 | 1.1 |  |  |  |  | 45 |  |  |  | 0 | 1.602 |  |  | 0.14 | 0.331 | [5 empty] | 33.5 |  |  |  |  | 67 |  | 24.3 |  | 7.9 | 0.114 |  | 15.4 | 100.24 | 2.23 |  |  |  |  | 14.681 | 13.653 | [6 empty] | 24.5 | 4.8809 | 15.26
2011-07-22 | 6.535 | 6.29 |  |  |  |  | 7.38 | 1.01 |  |  |  |  | 42.5 |  |  |  | 0 | 1.693 |  |  | 0.146 | 0.3515 | [5 empty] | 32.8 |  |  |  |  | 65.6 |  | 23.25 |  | 7.6 | 0.153 |  | 15.45 | 95.1 | 2.24 |  |  |  |  | 13.474 | 12.403 | [6 empty] | 24.355 | 4.8895 | 15.14
2011-07-23 | 6.5125 | 6.34 |  |  |  |  | 7.32 | 1.055 |  |  |  |  | 43.75 |  |  |  | 0 | 1.6475 |  |  | 0.143 | 0.34125 | [5 empty] | 33.15 |  |  |  |  | 66.3 |  | 23.775 |  | 7.75 | 0.1335 |  | 15.425 | 103.04 | 2.495 |  |  |  |  | 14.0415 | 12.922 | [6 empty] | 24.4275 | 4.8852 | 15.2
2011-07-24 | 6.5237 | 6.41 |  |  |  |  | 7.35 | 1.0325 |  |  |  |  | 43.125 |  |  |  | 0 | 2.1383 |  |  | 0.1445 | 0.34638 | [5 empty] | 32.975 |  |  |  |  | 65.95 |  | 23.5125 |  | 7.675 | 0.14325 |  | 15.4375 | 110.98 | 2.75 |  |  |  |  | 14.609 | 13.441 | [6 empty] | 24.3912 | 4.8874 | 15.17
2011-07-25 | 6.45 | 6.48 |  |  |  |  | 6.62 | 1.09 |  |  |  |  | 47 |  |  |  | 2 | 2.629 |  |  | 0.196 | 0.873 | [5 empty] | 26.5 |  |  |  |  | 53 |  | 24.8 |  | 7.4 | 0.21 |  | 15.8 | 114.42 | 2.17 |  |  |  |  | 17.357 | 15.942 | [6 empty] | 24.4094 | 4.8863 | 15.185
2011-07-26 | 6.32 | 6.31 |  |  |  |  | 6.34 | 1.34 |  |  |  |  | 40 |  |  |  | 1 | 1.584 |  |  | 0.127 | 1.14 | [5 empty] | 28.5 |  |  |  |  | 57 |  | 20.9 |  | 6.8 | 0.22 |  | 16 | 135.92 | 2.9 |  |  |  |  | 16.001 | 14.564 | [6 empty] | 20.25 | 2.99 | 12.02
2011-07-27 | 6.41 | 6.13 |  |  |  |  | 5.06 | 1.13 |  |  |  |  | 42 |  |  |  | 0 | 1.496 |  |  | 0.114 | 0.993 | [5 empty] | 28.5 |  |  |  |  | 57.1 |  | 14.7 |  | 7.35 | 0.183 |  | 16.1 | 110 | 2.59 |  |  |  |  | 14.409 | 13.435 | [6 empty] | 30.98 | 6.68 | 11.95
2011-07-28 | 6.39 | 5.76 |  |  |  |  | 8.63 | 1.32 |  |  |  |  | 41 |  |  |  | 0 | 0.905 |  |  | 0.096 | 0.227 | [5 empty] | 35.5 |  |  |  |  | 71 |  | 20.2 |  | 7.9 | 0.184 |  | 16.5 | 100.83 | 2.38 |  |  |  |  | 13.287 | 12.361 | [6 empty] | 29.1 | 4.835 | 16.03
2011-07-29 | 6.44 | 6.11 |  |  |  |  | 7.51 | 1.57 |  |  |  |  | 40 |  |  |  | 0 | 0.639 |  |  | 0.094 | 0.151 | [5 empty] | 32.6 |  |  |  |  | 65.2 |  | 22.7 |  | 8.4 | 0.12 |  | 16.1 | 114.97 | 2.3 |  |  |  |  | 14.653 | 13.476 | [6 empty] | 27.63 | 5.7575 | 14.04
2011-07-30 | 6.47 | 6.7 |  |  |  |  | 6.72 | 1.37 |  |  |  |  | 41 |  |  |  | 0 | 0.729 |  |  | 0.097 | 0.396 | [5 empty] | 31.1 |  |  |  |  | 62.2 |  | 24.6 |  | 8.7 | 0.14 |  | 16.5 | 99.73 | 2.23 |  |  |  |  | 13.112 | 12.576 | [6 empty] | 27.79 | 5.2963 | 13.12
2011-07-31 | 6.415 | 6.79 |  |  |  |  | 6.97 | 1.24 |  |  |  |  | 39.5 |  |  |  | 1 | 0.7235 |  |  | 0.12 | 0.51 | [5 empty] | 30.2 |  |  |  |  | 60.4 |  | 23.65 |  | 7.6 | 0.12 |  | 16.7 | 95.41 | 2 |  |  |  |  | 12.9 | 12.88 | [6 empty] | 27.79 | 5.5269 | 13.12
2011-08-01 | 6.36 | 6.88 |  |  |  |  | 7.22 | 0.94 |  |  |  |  | 38 |  |  |  | 2 | 0.718 |  |  | 0.143 | 0.624 | [5 empty] | 29.3 |  |  |  |  | 58.6 |  | 22.7 |  | 6.5 | 0.1 |  | 16.9 | 110.01 | 2.54 |  |  |  |  | 15.332 | 14.34 | [6 empty] | 32.66 | 5.4116 | 13.29
2011-08-02 | 6.37 | 6.49 |  |  |  |  | 6.85 | 1.1 |  |  |  |  | 39 |  |  |  | 0 | 0.837 |  |  | 0.131 | 0.298 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 23.7 |  | 7.4 | 0.097 |  | 17 | 120.28 | 2.97 |  |  |  |  | 14.42 | 13.414 | [6 empty] | 32.66 | 5.4692 | 12.955
2011-08-03 | 6.35 | 6.25 |  |  |  |  | 7.19 | 1.16 |  |  |  |  | 37 |  |  |  | 0 | 0.834 |  |  | 0.117 | 0.287 | [5 empty] | 25.4 |  |  |  |  | 50.9 |  | 25.5 |  | 7 | 0.084 |  | 18.1 | 74.37 | 1.36 |  |  |  |  | 13.971 | 13.401 | [6 empty] | 30.65 | 5.4404 | 12.62
2011-08-04 | 6.48 | 5.82 |  |  |  |  | 7.64 | 1.23 |  |  |  |  | 45 |  |  |  | 1 | 0.834 |  |  | 0.132 | 0.249 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 23.7 |  | 8.5 | 0.151 |  | 17.2 | 115.45 | 2.76 |  |  |  |  | 13.71 | 13.142 | [6 empty] | 26.72 | 5.4548 | 13.3
2011-08-05 | 5.95 | 6.34 |  |  |  |  | 8.6 | 1.3 |  |  |  |  | 44 |  |  |  | 2 | 0.837 |  |  | 0.261 | 0.274 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 23.5 |  | 8.8 | 0.192 |  | 17.2 | 130.05 | 3.41 |  |  |  |  | 14.072 | 12.529 | [6 empty] | 35.09 | 5.4476 | 14.35
2011-08-06 | 6.4 | 6.5 |  |  |  |  | 7.5 | 1.33 |  |  |  |  | 43 |  |  |  | 0 | 0.773 |  |  | 0.114 | 0.178 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 23.3 |  | 7.4 | 0.098 |  | 17.2 | 110.49 | 2.7 |  |  |  |  | 13.06 | 12.45 | [6 empty] | 23.87 | 5.4512 | 10.62
2011-08-07 | 6.535 | 6.375 |  |  |  |  | 7.235 | 1.18 |  |  |  |  | 43 |  |  |  | 0 | 0.899 |  |  | 0.1205 | 0.273 | [5 empty] | 27.85 |  |  |  |  | 55.7 |  | 22.25 |  | 7.5 | 0.0895 |  | 16.9 | 105.07 | 2.63 |  |  |  |  | 13.121 | 12.536 | [6 empty] | 23.93 | 5.4494 | 10.975
2011-08-08 | 6.67 | 6.25 |  |  |  |  | 6.97 | 1.35 |  |  |  |  | 43 |  |  |  | 0 | 1.025 |  |  | 0.127 | 0.368 | [5 empty] | 27.3 |  |  |  |  | 54.6 |  | 21.2 |  | 7.6 | 0.081 |  | 16.6 | 130.47 | 3.26 |  |  |  |  | 14.931 | 12.85 | [6 empty] | 23.99 | 5.4503 | 11.33
2011-08-09 | 6.41 | 6.34 |  |  |  |  | 7.5 | 1.25 |  |  |  |  | 41 |  |  |  | 0 | 1.019 |  |  | 0.131 | 0.236 | [5 empty] | 29.5 |  |  |  |  | 59 |  | 21.6 |  | 7.4 | 0.095 |  | 16.5 | 115.39 | 3.45 |  |  |  |  | 13.361 | 11.152 | [6 empty] | 24.13 | 5.4498 | 11.55
2011-08-10 | 5.99 | 6.07 |  |  |  |  | 6.92 | 1.49 |  |  |  |  | 37 |  |  |  | 1 | 1.031 |  |  | 0.122 | 0.489 | [5 empty] | 25.8 |  |  |  |  | 51.6 |  | 22 |  | 7.2 | 0.04 |  | 16.6 | 126.06 | 3.14 |  |  |  |  | 14.069 | 12.368 | [6 empty] | 24.87 | 5.4501 | 11.24
2011-08-11 | 6.52 | 6.13 |  |  |  |  | 8.01 | 1.42 |  |  |  |  | 37 |  |  |  | 1 | 0.93 |  |  | 0.225 | 0.171 | [5 empty] | 32 |  |  |  |  | 64 |  | 21.3 |  | 6.2 | 0.162 |  | 16.2 | 110.25 | 2.42 |  |  |  |  | 13.607 | 13.047 | [6 empty] | 25.01 | 4.77 | 13.1
2011-08-12 | 6.5 | 6.27 |  |  |  |  | 7.19 | 1.58 |  |  |  |  | 37 |  |  |  | 0 | 0.72 |  |  | 0.168 | 0.121 | [5 empty] | 31.4 |  |  |  |  | 62.8 |  | 23.5 |  | 7.4 | 0.139 |  | 16.5 | 90.45 | 1.75 |  |  |  |  | 13.481 | 12.345 | [6 empty] | 29.14 | 9.51 | 14.53
2011-08-13 | 6.53 | 6.19 |  |  |  |  | 7.38 | 1.39 |  |  |  |  | 38 |  |  |  | 0 | 1.036 |  |  | 0.136 | 0.134 | [5 empty] | 32.2 |  |  |  |  | 64.4 |  | 23.1 |  | 7.2 | 0.097 |  | 16.2 | 75.23 | 1.38 |  |  |  |  | 13.007 | 12.326 | [6 empty] | 32.92 | 7.14 | 13.815
2011-08-14 | 6.5 | 6.355 |  |  |  |  | 7.25 | 1.22 |  |  |  |  | 36 |  |  |  | 0 | 1.0095 |  |  | 0.137 | 0.134 | [5 empty] | 32.15 |  |  |  |  | 64.3 |  | 23.8 |  | 7.15 | 0.079 |  | 16.3 | 84.16 | 1.64 |  |  |  |  | 13.869 | 13.352 | [6 empty] | 33.79 | 8.325 | 14.1725
2011-08-15 | 6.47 | 6.52 |  |  |  |  | 7.12 | 1.24 |  |  |  |  | 34 |  |  |  | 0 | 0.983 |  |  | 0.138 | 0.134 | [5 empty] | 32.1 |  |  |  |  | 64.2 |  | 24.5 |  | 7.1 | 0.061 |  | 16.4 | 90.32 | 1.89 |  |  |  |  | 14.142 | 13.107 | [6 empty] | 34.66 | 9.19 | 17.59
2011-08-16 | 6.52 | 6.62 |  |  |  |  | 6.5 | 1.12 |  |  |  |  | 38 |  |  |  | 0 | 1.702 |  |  | 0.121 | 0.172 | [5 empty] | 28.6 |  |  |  |  | 57.2 |  | 23.7 |  | 6.4 | 0.089 |  | 16.7 | 85.56 | 1.92 |  |  |  |  | 13.795 | 12.78 | [6 empty] | 32.99 | 8.7575 | 11.36
2011-08-17 | 6.5 | 5.92 |  |  |  |  | 5.1 | 1.12 |  |  |  |  | 32 |  |  |  | 0 | 1.002 |  |  | 0.092 | 0.063 | [5 empty] | 21.7 |  |  |  |  | 43.4 |  | 24.1 |  | 5.7 | 0.134 |  | 17.4 | 90.37 | 2.07 |  |  |  |  | 13.949 | 12.872 | [6 empty] | 33.7 | 8.9737 | 11.26
2011-08-18 | 6.61 | 6.49 |  |  |  |  | 7.78 | 1.38 |  |  |  |  | 38 |  |  |  | 0 | 1.055 |  |  | 0.113 | 0.191 | [5 empty] | 29.4 |  |  |  |  | 58.8 |  | 25.6 |  | 7.3 | 0.086 |  | 16.9 | 114.13 | 2.44 |  |  |  |  | 14.653 | 13.581 | [6 empty] | 32.89 | 8.8656 | 11.26
2011-08-19 | 6.6 | 6.58 |  |  |  |  | 7.35 | 1.5 |  |  |  |  | 37 |  |  |  | 0 | 1.5295 |  |  | 0.131 | 0.176 | [5 empty] | 29.3 |  |  |  |  | 58.6 |  | 25.3 |  | 7.2 | 0.066 |  | 16.9 | 110.98 | 2.46 |  |  |  |  | 13.805 | 12.708 | [6 empty] | 32.89 | 8.9197 | 11.26
2011-08-20 | 6.605 | 6.535 |  |  |  |  | 7.565 | 1.44 |  |  |  |  | 37.5 |  |  |  | 0 | 1.2923 |  |  | 0.122 | 0.1835 | [5 empty] | 29.35 |  |  |  |  | 58.7 |  | 25.45 |  | 7.25 | 0.076 |  | 16.9 | 112.555 | 2.45 |  |  |  |  | 14.229 | 13.1445 | [6 empty] | 32.89 | 8.8927 | 11.26
2011-08-21 | 6.6025 | 6.5575 |  |  |  |  | 7.4575 | 1.47 |  |  |  |  | 37.25 |  |  |  | 0 | 1.4109 |  |  | 0.1265 | 0.17975 | [5 empty] | 29.325 |  |  |  |  | 58.65 |  | 25.375 |  | 7.225 | 0.071 |  | 16.9 | 111.7675 | 2.455 |  |  |  |  | 14.017 | 12.9262 | [6 empty] | 32.89 | 8.9062 | 11.26
2011-08-22 | 6.55 | 6.55 |  |  |  |  | 6.95 | 1.11 |  |  |  |  | 36 |  |  |  | 0 | 0.985 |  |  | 0.12425 | 0.383 | [5 empty] | 28.1 |  |  |  |  | 56.3 |  | 23.7 |  | 6 | 0.042 |  | 17.2 | 116.87 | 2.75 |  |  |  |  | 15.46 | 13.757 | [6 empty] | 27.23 | 8.8994 | 12.21
2011-08-23 | 6.73 | 6.37 |  |  |  |  | 6.37 | 1.19 |  |  |  |  | 36 |  |  |  | 0 | 1.089 |  |  | 0.12538 | 0.607 | [5 empty] | 30.2 |  |  |  |  | 60.4 |  | 21.6 |  | 5.5 | 0.02 |  | 17.7 | 110.49 | 2.69 |  |  |  |  | 14.937 | 12.925 | [6 empty] | 29.1 | 8.9028 | 12.28
2011-08-24 | 6.38 | 5.88 |  |  |  |  | 7.13 | 1.2 |  |  |  |  | 34 |  |  |  | 0 | 0.917 |  |  | 0.12481 | 0.499 | [5 empty] | 31.2 |  |  |  |  | 62.4 |  | 25.7 |  | 6.9 | 0.054 |  | 18.1 | 105.6 | 2.43 |  |  |  |  | 16.582 | 13.2 | [6 empty] | 34.59 | 8.9011 | 13.85
2011-08-25 | 6.48 | 6.22 |  |  |  |  | 6.08 | 1.2 |  |  |  |  | 41 |  |  |  | 0 | 1.003 |  |  | 0.12509 | 0.691 | [5 empty] | 27.8 |  |  |  |  | 55.7 |  | 22.6 |  | 6 | 0.159 |  | 18.1 | 105.875 | 2.64 |  |  |  |  | 14.829 | 14.083 | [6 empty] | 34.96 | 8.9019 | 15.195
2011-08-26 | 6.55 | 6.13 |  |  |  |  | 6.67 | 1.33 |  |  |  |  | 34 |  |  |  | 1 | 1.073 |  |  | 0.121 | 0.756 | [5 empty] | 32.3 |  |  |  |  | 64.6 |  | 23.7 |  | 6.1 | 0.024 |  | 17.9 | 106.15 | 2.52 |  |  |  |  | 13.707 | 12.507 | [6 empty] | 34.91 | 8.9015 | 16.54
2011-08-27 | 6.34 | 6.05 |  |  |  |  | 7.39 | 1.6 |  |  |  |  | 39 |  |  |  | 1 | 1.186 |  |  | 0.117 | 0.264 | [5 empty] | 35.1 |  |  |  |  | 70.2 |  | 24.6 |  | 6.9 | 0.084 |  | 18 | 110.49 | 2.29 |  |  |  |  | 14.02 | 12.89 | [6 empty] | 42.9 | 8.9017 | 18.06
2011-08-28 | 6.365 | 5.93 |  |  |  |  | 7.235 | 1.605 |  |  |  |  | 38 |  |  |  | 0.5 | 1.016 |  |  | 0.168 | 0.2345 | [5 empty] | 35.05 |  |  |  |  | 70.1 |  | 27.95 |  | 8.15 | 0.0685 |  | 18.05 | 75.01 | 1.17 |  |  |  |  | 13.415 | 12.276 | [6 empty] | 35.35 | 8.9016 | 15.15
2011-08-29 | 6.39 | 5.81 |  |  |  |  | 7.08 | 1.61 |  |  |  |  | 37 |  |  |  | 0 | 0.846 |  |  | 0.219 | 0.205 | [5 empty] | 35 |  |  |  |  | 70 |  | 31.3 |  | 9.4 | 0.053 |  | 18.1 | 99.73 | 1.69 |  |  |  |  | 15.007 | 13.733 | [6 empty] | 27.8 | 10.45 | 12.24
2011-08-30 | 6.46 | 5.93 |  |  |  |  | 7.06 | 1.41 |  |  |  |  | 38 |  |  |  | 0 | 1.29 |  |  | 0.114 | 0.158 | [5 empty] | 34.5 |  |  |  |  | 69 |  | 24.5 |  | 8.4 | 0.024 |  | 18.2 | 95.32 | 1.91 |  |  |  |  | 14.151 | 13.032 | [6 empty] | 40.41 | 11.61 | 12.14
2011-08-31 | 6.25 | 5.75 |  |  |  |  | 7.39 | 1.361 |  |  |  |  | 42 |  |  |  | 0 | 1.252 |  |  | 0.118 | 0.109 | [5 empty] | 35.1 |  |  |  |  | 70.2 |  | 23.8 |  | 8.1 | 0.116 |  | 18.1 | 85.07 | 1.83 |  |  |  |  | 13.52 | 12.304 | [6 empty] | 38.31 | 12.86 | 11.92
2011-09-01 | 6.67 | 5.96 |  |  |  |  | 7.31 | 1.36 |  |  |  |  | 43 |  |  |  | 0 | 1.236 |  |  | 0.12 | 0.087 | [5 empty] | 31.6 |  |  |  |  | 63.2 |  | 24.3 |  | 7.3 | 0.07 |  | 18 | 89.99 | 1.83 |  |  |  |  | 13.899 | 12.791 | [6 empty] | 37.23 | 13.32 | 12.29
2011-09-02 | 6.54 | 5.86 |  |  |  |  | 6.24 | 1.33 |  |  |  |  | 41 |  |  |  | 0 | 1.24 |  |  | 0.099 | 0.079 | [5 empty] | 29.4 |  |  |  |  | 58.8 |  | 24.9 |  | 7 | 0.064 |  | 17.9 | 85.25 | 1.84 |  |  |  |  | 13.381 | 12.256 | [6 empty] | 36.87 | 13.37 | 12.26
2011-09-03 | 6.67 | 6.08 |  |  |  |  | 8.64 | 1.15 |  |  |  |  | 35 |  |  |  | 0 | 1.139 |  |  | 0.123 | 0.224 | [5 empty] | 40.8 |  |  |  |  | 82.1 |  | 26.4 |  | 8.2 | 0.059 |  | 18.2 | 100.22 | 2.56 |  |  |  |  | 13.37 | 12.28 | [6 empty] | 28.17 | 13.16 | 14.72
2011-09-04 | 6.47 | 6.005 |  |  |  |  | 7.865 | 1.125 |  |  |  |  | 38.5 |  |  |  | 0 | 1.052 |  |  | 0.12 | 0.1595 | [5 empty] | 39.05 |  |  |  |  | 78.35 |  | 26.2 |  | 8.05 | 0.074 |  | 18.1 | 79.29 | 2.23 |  |  |  |  | 13.304 | 11.803 | [6 empty] | 28.17 | 13.16 | 14.72
2011-09-05 | 6.27 | 5.93 |  |  |  |  | 7.09 | 1.1 |  |  |  |  | 42 |  |  |  | 0 | 0.965 |  |  | 0.117 | 0.095 | [5 empty] | 37.3 |  |  |  |  | 74.6 |  | 26 |  | 7.9 | 0.089 |  | 18 | 100.22 | 2.46 |  |  |  |  | 13.894 | 12.774 | [6 empty] | 41.49 | 12.35 | 13.68
2011-09-06 | 6.46 | 6.08 |  |  |  |  | 7.32 | 1.1 |  |  |  |  | 32 |  |  |  | 0 | 0.943 |  |  | 0.136 | 0.081 | [5 empty] | 31.7 |  |  |  |  | 63.4 |  | 26.3 |  | 7.7 | 0.05 |  | 18.1 | 100.24 | 2.76 |  |  |  |  | 13.13 | 11.775 | [6 empty] | 38.15 | 12.84 | 12.99
2011-09-07 | 6.39 | 5.92 |  |  |  |  | 7.06 | 1.19 |  |  |  |  | 34 |  |  |  | 0 | 1.012 |  |  | 0.14 | 0.085 | [5 empty] | 32 |  |  |  |  | 64 |  | 25 |  | 7.1 | 0.054 |  | 18 | 104.14 | 2.6 |  |  |  |  | 13.865 | 12.462 | [6 empty] | 38.27 | 12.99 | 13.84
2011-09-08 | 6.78 | 6.22 |  |  |  |  | 7.23 | 1.18 |  |  |  |  | 32 |  |  |  | 0 | 0.86 |  |  | 0.132 | 0.101 | [5 empty] | 34.4 |  |  |  |  | 69.4 |  | 22 |  | 7.6 | 0.053 |  | 17.4 | 85.58 | 2.06 |  |  |  |  | 13.197 | 12.007 | [6 empty] | 33.33 | 11.69 | 13.17
2011-09-09 | 6.68 | 6.26 |  |  |  |  | 7.5 | 0.98 |  |  |  |  | 33 |  |  |  | 0 | 0.884 |  |  | 0.146 | 0.07 | [5 empty] | 31.7 |  |  |  |  | 63.4 |  | 22.3 |  | 7.4 | 0.074 |  | 17 | 73.56 | 1.71 |  |  |  |  | 14.273 | 12.414 | [6 empty] | 33.66 | 11.67 | 13.774
2011-09-10 | 6.54 | 6.13 |  |  |  |  | 7.37 | 1.15 |  |  |  |  | 39 |  |  |  | 0 | 1.11 |  |  | 0.127 | 0.087 | [5 empty] | 28.7 |  |  |  |  | 57.4 |  | 23.5 |  | 7.7 | 0.07 |  | 16.7 | 85.07 | 2.18 |  |  |  |  | 12.46 | 11.6 | [6 empty] | 30.72 | 12.2 | 12.8
2011-09-11 | 6.595 | 6.14 |  |  |  |  | 7.19 | 1.055 |  |  |  |  | 35 |  |  |  | 0 | 1.0065 |  |  | 0.14 | 0.0935 | [5 empty] | 29.75 |  |  |  |  | 59.5 |  | 23.7 |  | 7.6 | 0.064 |  | 16.4 | 90.38 | 2.395 |  |  |  |  | 13.0565 | 11.8855 | [6 empty] | 30.38 | 12.31 | 11.77
2011-09-12 | 6.65 | 6.15 |  |  |  |  | 7.01 | 0.96 |  |  |  |  | 31 |  |  |  | 0 | 0.903 |  |  | 0.153 | 0.1 | [5 empty] | 30.8 |  |  |  |  | 61.6 |  | 23.9 |  | 7.5 | 0.058 |  | 16.1 | 95.69 | 2.61 |  |  |  |  | 13.653 | 12.171 | [6 empty] | 30.04 | 12.42 | 10.74
2011-09-13 | 6.77 | 6.26 |  |  |  |  | 7.4 | 1.31 |  |  |  |  | 32 |  |  |  | 0 | 0.918 |  |  | 0.147 | 0.093 | [5 empty] | 29.2 |  |  |  |  | 38.4 |  | 27 |  | 7.3 | 0.064 |  | 15.8 | 79.69 | 1.61 |  |  |  |  | 13.803 | 12.404 | [6 empty] | 30.5 | 12.17 | 10.5
2011-09-14 | 6.79 | 6.37 |  |  |  |  | 7.65 | 1.07 |  |  |  |  | 38 |  |  |  | 0 | 0.99 |  |  | 0.138 | 0.09 | [5 empty] | 33.5 |  |  |  |  | 67 |  | 22.2 |  | 8.3 | 0.055 |  | 15.9 | 75.3 | 1.77 |  |  |  |  | 13.46 | 12.019 | [6 empty] | 35.24 | 11.07 | 11.99
2011-09-15 | 6.72 | 6.4 |  |  |  |  | 7.25 | 1.22 |  |  |  |  | 49 |  |  |  | 0 | 1.079 |  |  | 0.199 | 0.083 | [5 empty] | 31.7 |  |  |  |  | 63.5 |  | 22.95 |  | 6.3 | 0.034 |  | 16.1 | 69.5 | 1.42 |  |  |  |  | 13.319 | 11.936 | [6 empty] | 33.61 | 11.03 | 12.5
2011-09-16 | 6.03 | 6.61 |  |  |  |  | 7.95 | 1.03 |  |  |  |  | 31 |  |  |  | 0 | 1.121 |  |  | 0.153 | 0.087 | [5 empty] | 31 |  |  |  |  | 62 |  | 23.7 |  | 7 | 0.047 |  | 16.1 | 75.34 | 1.72 |  |  |  |  | 13.714 | 12.455 | [6 empty] | 36.62 | 13.96 | 11.97
2011-09-17 | 6.23 | 6.03 |  |  |  |  | 7.06 | 1.25 |  |  |  |  | 33 |  |  |  | 0 | 1.214 |  |  | 0.157 | 0.089 | [5 empty] | 31.1 |  |  |  |  | 62.2 |  | 24.4 |  | 6.7 | 0.039 |  | 15.9 | 70.32 | 1.42 |  |  |  |  | 12.8 | 11.96 | [6 empty] | 35.6 | 12.16 | 12.87
2011-09-18 | 6.25 | 6.08 |  |  |  |  | 7.085 | 1.25 |  |  |  |  | 32.5 |  |  |  | 0 | 1.486 |  |  | 0.133 | 0.0895 | [5 empty] | 31.3 |  |  |  |  | 62.6 |  | 24 |  | 7.05 | 0.039 |  | 15.6 | 60.57 | 1.06 |  |  |  |  | 12.77 | 11.893 | [6 empty] | 33.945 | 11.915 | 12.57
2011-09-19 | 6.27 | 6.13 |  |  |  |  | 7.11 | 1.21 |  |  |  |  | 32 |  |  |  | 0 | 1.758 |  |  | 0.109 | 0.09 | [5 empty] | 31.5 |  |  |  |  | 63 |  | 23.6 |  | 7.4 | 0.039 |  | 15.3 | 74.79 | 1.48 |  |  |  |  | 13.87 | 12.607 | [6 empty] | 32.29 | 11.67 | 12.27
2011-09-20 | 6.49 | 6.25 |  |  |  |  | 7.31 | 1.31 |  |  |  |  | 37 |  |  |  | 0 | 1.622 |  |  | 0.14 | 0.109 | [5 empty] | 30.2 |  |  |  |  | 60.4 |  | 25.5 |  | 8.3 | 0.065 |  | 15.2 | 74.82 | 1.56 |  |  |  |  | 13.114 | 11.819 | [6 empty] | 32.36 | 11.8 | 12.69
2011-09-21 | 5.86 | 6.25 |  |  |  |  | 7.6 | 1.07 |  |  |  |  | 35 |  |  |  | 0 | 1.69 |  |  | 0.154 | 0.116 | [5 empty] | 31.4 |  |  |  |  | 62.8 |  | 24.6 |  | 8.1 | 0.066 |  | 15 | 75.3 | 1.55 |  |  |  |  | 14.285 | 13.029 | [6 empty] | 36.19 | 12.01 | 12.86
2011-09-22 | 6.34 | 6.07 |  |  |  |  | 7.45 | 1.02 |  |  |  |  | 37 |  |  |  | 0 | 1.656 |  |  | 0.173 | 0.124 | [5 empty] | 31.3 |  |  |  |  | 62.6 |  | 23.6 |  | 8.2 | 0.067 |  | 15 | 65.2 | 1.31 |  |  |  |  | 13.503 | 12.693 | [6 empty] | 31.43 | 13.03 | 11.02
2011-09-23 | 6.27 | 6.43 |  |  |  |  | 7.02 | 0.99 |  |  |  |  | 36 |  |  |  | 0 | 1.732 |  |  | 0.146 | 0.091 | [5 empty] | 31 |  |  |  |  | 62 |  | 23.9 |  | 7.8 | 0.079 |  | 14.9 | 60.64 | 1.32 |  |  |  |  | 13.242 | 11.916 | [6 empty] | 31.43 | 13.03 | 11.01
2011-09-24 | 6.24 | 6.26 |  |  |  |  | 6.8 | 1.08 |  |  |  |  | 35 |  |  |  | 0 | 1.0065 |  |  | 0.137 | 0.106 | [5 empty] | 30.9 |  |  |  |  | 61.8 |  | 25 |  | 8.3 | 0.062 |  | 14.8 | 64.96 | 1.33 |  |  |  |  | 13.03 | 12.26 | [6 empty] | 31.43 | 13.03 | 11.02
2011-09-25 | 6.1 | 6.275 |  |  |  |  | 7.29 | 1.09 |  |  |  |  | 32 |  |  |  | 0 | 0.4665 |  |  | 0.1525 | 0.115 | [5 empty] | 31.35 |  |  |  |  | 62.7 |  | 24.4 |  | 8.45 | 0.0565 |  | 14.85 | 60.06 | 1.22 |  |  |  |  | 12.617 | 11.828 | [6 empty] | 31.43 | 13.03 | 11.02
2011-09-26 | 5.96 | 6.29 |  |  |  |  | 7.78 | 1.06 |  |  |  |  | 29 |  |  |  | 0 | 0.933 |  |  | 0.168 | 0.124 | [5 empty] | 31.8 |  |  |  |  | 63.6 |  | 23.8 |  | 8.6 | 0.051 |  | 14.9 | 80.2 | 1.89 |  |  |  |  | 14.519 | 12.323 | [6 empty] | 40.1 | 11.2 | 11.89
2011-09-27 | 6.37 | 6.43 |  |  |  |  | 7.58 | 1.18 |  |  |  |  | 34 |  |  |  | 1 | 0.9875 |  |  | 0.977 | 0.201 | [5 empty] | 32.6 |  |  |  |  | 63.2 |  | 24.4 |  | 8.9 | 0.177 |  | 14.7 | 79.46 | 2.15 |  |  |  |  | 13.2 | 10.826 | [6 empty] | 31.91 | 10.21 | 12.31
2011-09-28 | 6.31 | 6.12 |  |  |  |  | 7.16 | 1.43 |  |  |  |  | 31 |  |  |  | 0 | 1.042 |  |  | 0.141 | 0.086 | [5 empty] | 31.2 |  |  |  |  | 62.5 |  | 21.8 |  | 9.1 | 0.056 |  | 14.7 | 75.36 | 1.36 |  |  |  |  | 13.022 | 12.262 | [6 empty] | 33.33 | 9.27 | 14.98
2011-09-29 | 6.84 | 6.23 |  |  |  |  | 6.03 | 1.23 |  |  |  |  | 41 |  |  |  | 0 | 1.039 |  |  | 0.144 | 0.395 | [5 empty] | 29.3 |  |  |  |  | 58.5 |  | 26.2 |  | 9.6 | 0.047 |  | 14.3 | 74.86 | 1.4 |  |  |  |  | 14.358 | 12.536 | [6 empty] | 35.68 | 10.48 | 14.78
2011-09-30 | 6.22 | 6.37 |  |  |  |  | 6.86 | 1.13 |  |  |  |  | 34 |  |  |  | 0 | 0.649 |  |  | 0.151 | 0.156 | [5 empty] | 33.1 |  |  |  |  | 66.2 |  | 22.8 |  | 6.8 | 0.052 |  | 14.5 | 60.15 | 1.15 |  |  |  |  | 12.657 | 11.991 | [6 empty] | 33.33 | 9.27 | 14.48
2011-10-01 | 6.15 | 5.46 |  |  |  |  | 6.7 | 1.42 |  |  |  |  | 34 |  |  |  | 0 | 0.753 |  |  | 0.148 | 0.264 | [5 empty] | 33 |  |  |  |  | 66 |  | 24.3 |  | 7.2 | 0.067 |  | 14.6 | 80.17 | 1.66 |  |  |  |  | 12.633 | 11.817 | [6 empty] | 38.985 | 7.35 | 14.805
2011-10-02 | 6.34 | 6.14 |  |  |  |  | 6.67 | 2.02 |  |  |  |  | 54 |  |  |  | 1 | 0.857 |  |  | 0.318 | 0.257 | [5 empty] | 34.3 |  |  |  |  | 68.6 |  | 23.4 |  | 6.3 | 0.157 |  | 8.7 | 80.17 | 0.94 |  |  |  |  | 13.636 | 12.282 | [6 empty] | 44.64 | 5.43 | 15.13
2011-10-03 | 6.58 | 6.35 |  |  |  |  | 7.2 | 1.432 |  |  |  |  | 58 |  |  |  | 0 | 0.616 |  |  | 0.137 | 0.107 | [5 empty] | 36.4 |  |  |  |  | 72.8 |  | 24 |  | 7.4 | 0.051 |  | 14.3 | 85.07 | 1.81 |  |  |  |  | 14.045 | 11.945 | [6 empty] | 36.17 | 13.22 | 14.25
2011-10-04 | 6.18 | 5.65 |  |  |  |  | 7.78 | 1.34 |  |  |  |  | 42 |  |  |  | 0 | 0.598 |  |  | 0.139 | 0.124 | [5 empty] | 35 |  |  |  |  | 70 |  | 22.2 |  | 8.2 | 0.047 |  | 14.1 | 79.69 | 1.94 |  |  |  |  | 13.259 | 11.032 | [6 empty] | 32.86 | 14.19 | 14.28
2011-10-05 | 6.74 | 6.05 |  |  |  |  | 7.37 | 1.16 |  |  |  |  | 59 |  |  |  | 0 | 0.592 |  |  | 0.124 | 0.11 | [5 empty] | 35 |  |  |  |  | 70 |  | 22.4 |  | 7.7 | 0.104 |  | 14.1 | 70.41 | 1.84 |  |  |  |  | 12.897 | 10.673 | [6 empty] | 30.95 | 12.36 | 13.54
2011-10-06 | 6.59 | 6.42 |  |  |  |  | 6.49 | 1.16 |  |  |  |  | 54 |  |  |  | 0 | 0.648 |  |  | 0.139 | 0.082 | [5 empty] | 33.8 |  |  |  |  | 67.6 |  | 25.5 |  | 7.4 | 0.112 |  | 13.4 | 100.24 | 2.52 |  |  |  |  | 14.776 | 12.243 | [6 empty] | 30.37 | 12.22 | 14.13
2011-10-07 | 6.67 | 6.495 |  |  |  |  | 6.725 | 1.22 |  |  |  |  | 47.5 |  |  |  | 0 | 0.661 |  |  | 0.1415 | 0.0905 | [5 empty] | 32.95 |  |  |  |  | 65.9 |  | 23.85 |  | 7.25 | 0.1105 |  | 13.2 | 87.385 | 2.115 |  |  |  |  | 13.458 | 11.7725 | [6 empty] | 30.66 | 12.29 | 13.835
2011-10-08 | 6.75 | 6.57 |  |  |  |  | 6.96 | 1.28 |  |  |  |  | 41 |  |  |  | 0 | 0.674 |  |  | 0.144 | 0.099 | [5 empty] | 32.1 |  |  |  |  | 64.2 |  | 22.2 |  | 7.1 | 0.109 |  | 13 | 74.53 | 1.71 |  |  |  |  | 12.14 | 11.302 | [6 empty] | 30.515 | 12.255 | 13.9825
2011-10-09 | 6.72 | 6.345 |  |  |  |  | 6.73 | 1.21 |  |  |  |  | 44 |  |  |  | 0 | 0.6815 |  |  | 0.1965 | 0.254 | [5 empty] | 31.75 |  |  |  |  | 63.5 |  | 21.2 |  | 7.1 | 0.133 |  | 13 | 65.09 | 1.48 |  |  |  |  | 12.163 | 11.333 | [6 empty] | 30.5875 | 12.2725 | 13.9088
2011-10-10 | 6.69 | 6.12 |  |  |  |  | 6.5 | 1.14 |  |  |  |  | 47 |  |  |  | 0 | 0.689 |  |  | 0.249 | 0.409 | [5 empty] | 31.4 |  |  |  |  | 62.8 |  | 20.2 |  | 7.1 | 0.157 |  | 13 | 101.21 | 2.4 |  |  |  |  | 14.754 | 12.99 | [6 empty] | 31.13 | 12.2637 | 12.99
2011-10-11 | 6.48 | 5.96 |  |  |  |  | 7.09 | 0.98 |  |  |  |  | 53 |  |  |  | 0 | 0.687 |  |  | 0.242 | 0.732 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 21.4 |  | 7.1 | 0.194 |  | 12.5 | 89.92 | 2.51 |  |  |  |  | 12.613 | 11.674 | [6 empty] | 30.4 | 12.2681 | 12.51
2011-10-12 | 6.23 | 6.42 |  |  |  |  | 7.31 | 1.07 |  |  |  |  | 35 |  |  |  | 0 | 0.641 |  |  | 0.171 | 0.279 | [5 empty] | 26.9 |  |  |  |  | 53.8 |  | 22.2 |  | 5.3 | 0.033 |  | 12 | 95.63 | 2.64 |  |  |  |  | 13.49 | 11.705 | [6 empty] | 31.96 | 12.2659 | 13.11
2011-10-13 | 6.46 | 5.91 |  |  |  |  | 6.27 | 0.91 |  |  |  |  | 38 |  |  |  | 0 | 0.662 |  |  | 0.143 | 0.13 | [5 empty] | 24.9 |  |  |  |  | 49.8 |  | 23.6 |  | 7.4 | 0.041 |  | 11.8 | 70.89 | 1.83 |  |  |  |  | 13.097 | 11.749 | [6 empty] | 30.94 | 3.21 | 11.43
2011-10-14 | 6.59 | 5.93 |  |  |  |  | 7.065 | 1.16 |  |  |  |  | 35 |  |  |  | 0 | 0.659 |  |  | 0.1535 | 0.1115 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 24.45 |  | 7.6 | 0.0665 |  | 11.8 | 89.48 | 2.3 |  |  |  |  | 13.064 | 11.757 | [6 empty] | 28.85 | 6.285 | 11.2
2011-10-15 | 6.72 | 5.95 |  |  |  |  | 7.86 | 1.15 |  |  |  |  | 32 |  |  |  | 0 | 0.656 |  |  | 0.164 | 0.093 | [5 empty] | 31.3 |  |  |  |  | 62.6 |  | 25.3 |  | 7.8 | 0.092 |  | 11.8 | 75.09 | 1.73 |  |  |  |  | 12.38 | 11.93 | [6 empty] | 26.76 | 9.36 | 10.97
2011-10-16 | 6.48 | 6.14 |  |  |  |  | 7.885 | 1.32 |  |  |  |  | 32.5 |  |  |  | 0 | 0.632 |  |  | 0.1605 | 0.103 | [5 empty] | 31.25 |  |  |  |  | 62.5 |  | 24.95 |  | 7.7 | 0.083 |  | 11.9 | 74.33 | 1.48 |  |  |  |  | 12.49 | 12.05 | [6 empty] | 26.76 | 9.36 | 10.97
2011-10-17 | 6.24 | 6.33 |  |  |  |  | 7.91 | 1.43 |  |  |  |  | 33 |  |  |  | 0 | 0.608 |  |  | 0.157 | 0.113 | [5 empty] | 31.2 |  |  |  |  | 62.4 |  | 24.6 |  | 7.6 | 0.074 |  | 12 | 94.86 | 2.13 |  |  |  |  | 14.294 | 12.085 | [6 empty] | 27.74 | 9.44 | 10.67
2011-10-18 | 6.59 | 6.62 |  |  |  |  | 7.55 | 1.22 |  |  |  |  | 46 |  |  |  | 1 | 0.6525 |  |  | 0.174 | 0.121 | [5 empty] | 30.9 |  |  |  |  | 61.8 |  | 25.5 |  | 6.3 | 0.077 |  | 12.1 | 74.79 | 2.02 |  |  |  |  | 12.781 | 10.493 | [6 empty] | 28.35 | 10.58 | 10.68
2011-10-19 | 6.41 | 6.27 |  |  |  |  | 6.97 | 1.66 |  |  |  |  | 42 |  |  |  | 0 | 0.697 |  |  | 0.171 | 0.082 | [5 empty] | 29.7 |  |  |  |  | 59.4 |  | 24.6 |  | 7 | 0.097 |  | 12.3 | 90.51 | 1.94 |  |  |  |  | 13.21 | 11.402 | [6 empty] | 28.495 | 12.09 | 10.515
2011-10-20 | 6.49 | 6.25 |  |  |  |  | 7.44 | 1.07 |  |  |  |  | 43 |  |  |  | 0 | 0.657 |  |  | 0.152 | 0.094 | [5 empty] | 30.8 |  |  |  |  | 61.7 |  | 26.8 |  | 7.2 | 0.069 |  | 12 | 74.82 | 1.72 |  |  |  |  | 13.09 | 12.195 | [6 empty] | 28.64 | 13.6 | 10.35
2011-10-21 | 6.46 | 6.25 |  |  |  |  | 7.49 | 1.1 |  |  |  |  | 45 |  |  |  | 0 | 0.638 |  |  | 0.161 | 0.093 | [5 empty] | 30.6 |  |  |  |  | 29.3 |  | 58.6 |  | 7.05 | 0.0665 |  | 10.1 | 80.2 | 1.96 |  |  |  |  | 12.927 | 12.018 | [6 empty] | 29.97 | 13.4 | 10.795
2011-10-22 | 6.52 | 6.25 |  |  |  |  | 7.17 | 1.17 |  |  |  |  | 48 |  |  |  | 0 | 0.694 |  |  | 0.159 | 0.109 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 24.4 |  | 6.9 | 0.064 |  | 11.9 | 85.58 | 2.2 |  |  |  |  | 13.13 | 11.54 | [6 empty] | 31.3 | 13.2 | 11.24
2011-10-23 | 6.525 | 6.17 |  |  |  |  | 6.895 | 1.04 |  |  |  |  | 45.5 |  |  |  | 0 | 0.6405 |  |  | 0.1965 | 0.243 | [5 empty] | 29.55 |  |  |  |  | 59.05 |  | 24.85 |  | 7.05 | 0.0715 |  | 11.85 | 82.875 | 2.21 |  |  |  |  | 13.5525 | 11.5915 | [6 empty] | 30.085 | 13.56 | 10.565
2011-10-24 | 6.53 | 6.09 |  |  |  |  | 6.62 | 0.91 |  |  |  |  | 43 |  |  |  | 0 | 0.587 |  |  | 0.234 | 0.377 | [5 empty] | 28.7 |  |  |  |  | 57.3 |  | 25.3 |  | 7.2 | 0.079 |  | 11.8 | 80.17 | 2.22 |  |  |  |  | 13.975 | 11.643 | [6 empty] | 28.87 | 13.92 | 9.89
2011-10-25 | 6.83 | 6.2 |  |  |  |  | 7.61 | 1.18 |  |  |  |  | 41 |  |  |  | 0 | 0.594 |  |  | 0.189 | 0.094 | [5 empty] | 31.9 |  |  |  |  | 63.9 |  | 26.8 |  | 7.3 | 0.069 |  | 12 | 69.92 | 1.89 |  |  |  |  | 12.653 | 10.334 | [6 empty] | 29.11 | 14.17 | 10.59
2011-10-26 | 6.645 | 6.29 |  |  |  |  | 7.72 | 0.88 |  |  |  |  | 45.5 |  |  |  | 0 | 0.9495 |  |  | 0.2025 | 0.471 | [5 empty] | 29.75 |  |  |  |  | 59.55 |  | 26.85 |  | 7.15 | 0.095 |  | 11.2 | 57.45 | 1.485 |  |  |  |  | 13.3075 | 11.3305 | [6 empty] | 28.835 | 13.19 | 10.61
2011-10-27 | 6.46 | 6.38 |  |  |  |  | 7.83 | 0.58 |  |  |  |  | 50 |  |  |  | 0 | 1.305 |  |  | 0.216 | 0.848 | [5 empty] | 27.6 |  |  |  |  | 55.2 |  | 26.9 |  | 7 | 0.121 |  | 10.4 | 44.98 | 1.08 |  |  |  |  | 13.962 | 12.327 | [6 empty] | 28.56 | 12.21 | 10.63
2011-10-28 | 6.44 | 6.17 |  |  |  |  | 7.94 | 0.9 |  |  |  |  | 48 |  |  |  | 0 | 0.997 |  |  | 0.18 | 0.171 | [5 empty] | 30.6 |  |  |  |  | 61.2 |  | 25.8 |  | 7.4 | 0.137 |  | 10 | 60.77 | 1.38 |  |  |  |  | 13.513 | 12.112 | [6 empty] | 31.89 | 10.73 | 12.39
2011-10-29 | 6.32 | 6.47 |  |  |  |  | 7.31 | 1.3 |  |  |  |  | 49 |  |  |  | 0 | 0.743 |  |  | 0.214 | 0.098 | [5 empty] | 30.7 |  |  |  |  | 61.4 |  | 24.9 |  | 6.9 | 0.091 |  | 9.6 | 44.98 | 0.5 |  |  |  |  | 12.765 | 11.341 | [6 empty] | 29.77 | 13.69 | 10.01
2011-10-30 | 6.675 | 6.59 |  |  |  |  | 7.315 | 1.41 |  |  |  |  | 61.5 |  |  |  | 2 | 0.7535 |  |  | 0.28 | 0.1025 | [5 empty] | 31.05 |  |  |  |  | 62.1 |  | 23.55 |  | 6.7 | 0.1385 |  | 9.5 | 51.27 | 0.64 |  |  |  |  | 12.292 | 11.38 | [6 empty] | 30.635 | 10.645 | 11.23
2011-10-31 | 7.03 | 6.71 |  |  |  |  | 7.32 | 1.82 |  |  |  |  | 74 |  |  |  | 4 | 0.764 |  |  | 0.346 | 0.107 | [5 empty] | 31.4 |  |  |  |  | 62.8 |  | 22.2 |  | 6.5 | 0.186 |  | 9.4 | 69.92 | 0.79 |  |  |  |  | 13.575 | 12.177 | [6 empty] | 31.5 | 7.6 | 12.45
2011-11-01 | 6.94 | 6.59 |  |  |  |  | 7.02 | 1.97 |  |  |  |  | 51 |  |  |  | 0 | 0.925 |  |  | 0.219 | 0.239 | [5 empty] | 32.3 |  |  |  |  | 64.6 |  | 22.5 |  | 7.4 | 0.144 |  | 8.7 | 80.19 | 1.08 |  |  |  |  | 13.318 | 11.947 | [6 empty] | 33.23 | 5.18 | 13.89
2011-11-02 | 6.985 | 6.65 |  |  |  |  | 7.17 | 1.895 |  |  |  |  | 62.5 |  |  |  | 0 | 0.8445 |  |  | 0.2825 | 0.173 | [5 empty] | 31.85 |  |  |  |  | 63.7 |  | 22.35 |  | 6.95 | 0.165 |  | 9.05 | 75.055 | 0.935 |  |  |  |  | 13.4465 | 12.062 | [6 empty] | 32.365 | 6.39 | 13.17
2011-11-03 | 6.9625 | 6.62 |  |  |  |  | 7.095 | 1.9325 |  |  |  |  | 56.75 |  |  |  | 0 | 0.88475 |  |  | 0.25075 | 0.206 | [5 empty] | 32.075 |  |  |  |  | 64.15 |  | 22.425 |  | 7.175 | 0.1545 |  | 8.875 | 77.6225 | 1.0075 |  |  |  |  | 13.3822 | 12.0045 | [6 empty] | 32.7975 | 5.785 | 13.53
2011-11-04 | 6.9463 | 6.56 |  |  |  |  | 7.97 | 1.71 |  |  |  |  | 45 |  |  |  | 0 | 0.732 |  |  | 0.201 | 0.154 | [5 empty] | 33 |  |  |  |  | 66 |  | 22 |  | 7.1 | 0.086 |  | 8 | 74.85 | 1.08 |  |  |  |  | 13.127 | 12.192 | [6 empty] | 36.15 | 8.34 | 15.91
2011-11-05 | 6.93 | 6.59 |  |  |  |  | 7.02 | 1.93 |  |  |  |  | 44 |  |  |  | 0 | 0.661 |  |  | 0.743 | 0.178 | [5 empty] | 29.6 |  |  |  |  | 59.3 |  | 22 |  | 7.3 | 0.086 |  | 7.9 | 70.41 | 0.72 |  |  |  |  | 13.47 | 12.08 | [6 empty] | 29.11 | 7.89 | 15.73
2011-11-06 | 6.625 | 6.49 |  |  |  |  | 6.825 | 2.04 |  |  |  |  | 54 |  |  |  | 1 | 0.6995 |  |  | 0.849 | 0.373 | [5 empty] | 32.75 |  |  |  |  | 65.55 |  | 22.2 |  | 6.85 | 0.0535 |  | 7.9 | 69.92 | 0.77 |  |  |  |  | 12.708 | 11.314 | [6 empty] | 29.11 | 7.89 | 15.73
2011-11-07 | 6.32 | 6.39 |  |  |  |  | 6.63 | 1.63 |  |  |  |  | 64 |  |  |  | 2 | 0.738 |  |  | 0.955 | 0.568 | [5 empty] | 35.9 |  |  |  |  | 71.8 |  | 22.4 |  | 6.4 | 0.021 |  | 7.9 | 75.37 | 1.27 |  |  |  |  | 14.044 | 11.792 | [6 empty] | 38.88 | 9.13 | 14.28
2011-11-08 | 6.44 | 6.69 |  |  |  |  | 7.61 | 1.57 |  |  |  |  | 66 |  |  |  | 2 | 0.709 |  |  | 0.286 | 0.23 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 23.7 |  | 7.1 | 0.047 |  | 7.8 | 66.77 | 1.26 |  |  |  |  | 13.026 | 10.729 | [6 empty] | 30.02 | 7.51 | 12.65
2011-11-09 | 6.77 | 6.09 |  |  |  |  | 7.14 | 1.7 |  |  |  |  | 42 |  |  |  | 0 | 0.693 |  |  | 0.663 | 0.394 | [5 empty] | 30.6 |  |  |  |  | 61.2 |  | 21.5 |  | 7.7 | 0.025 |  | 7.7 | 73.74 | 1.24 |  |  |  |  | 13.799 | 11.41 | [6 empty] | 30.98 | 8.32 | 13.02
2011-11-10 | 6.76 | 6.3 |  |  |  |  | 7.66 | 1.87 |  |  |  |  | 41 |  |  |  | 0 | 0.692 |  |  | 0.16 | 0.127 | [5 empty] | 31.5 |  |  |  |  | 62.9 |  | 26.8 |  | 8.1 | 0.091 |  | 7.6 | 70.41 | 0.79 |  |  |  |  | 13.06 | 12.011 | [6 empty] | 27.7 | 7.915 | 13.47
2011-11-11 | 6.64 | 6.29 |  |  |  |  | 7.44 | 1.79 |  |  |  |  | 34 |  |  |  | 0 | 0.624 |  |  | 0.172 | 0.529 | [5 empty] | 30.1 |  |  |  |  | 60.3 |  | 22.8 |  | 7.3 | 0.087 |  | 7.3 | 74.82 | 1.01 |  |  |  |  | 13.264 | 12.149 | [6 empty] | 27.82 | 8.1175 | 13.64
2011-11-12 | 6.72 | 7.08 |  |  |  |  | 7.38 | 1.59 |  |  |  |  | 58 |  |  |  | 2 | 0.658 |  |  | 0.0942 | 0.342 | [5 empty] | 28.7 |  |  |  |  | 57.4 |  | 22.5 |  | 6.4 | 0.171 |  | 7.6 | 70.41 | 1.71 |  |  |  |  | 11.099 | 9.683 | [6 empty] | 27.74 | 8.0162 | 12.59
2011-11-13 | 6.66 | 6.85 |  |  |  |  | 7.48 | 1.74 |  |  |  |  | 49.5 |  |  |  | 1 | 1.006 |  |  | 0.2841 | 0.2905 | [5 empty] | 28.35 |  |  |  |  | 56.7 |  | 22.7 |  | 6.65 | 0.1165 |  | 7.5 | 75.29 | 1.48 |  |  |  |  | 12.377 | 10.64 | [6 empty] | 24.9 | 8.0669 | 13.07
2011-11-14 | 6.6 | 6.62 |  |  |  |  | 7.58 | 1.89 |  |  |  |  | 41 |  |  |  | 0 | 1.354 |  |  | 0.474 | 0.239 | [5 empty] | 28 |  |  |  |  | 56 |  | 22.9 |  | 6.9 | 0.062 |  | 7.4 | 80.17 | 1.25 |  |  |  |  | 13.655 | 11.597 | [6 empty] | 22.06 | 8.0416 | 13.55
2011-11-15 | 7.07 | 6.48 |  |  |  |  | 7.7 | 2 |  |  |  |  | 28 |  |  |  | 0 | 1.424 |  |  | 0.411 | 0.165 | [5 empty] | 29.8 |  |  |  |  | 59.6 |  | 24.1 |  | 6.6 | 0.165 |  | 7.8 | 70.91 | 0.63 |  |  |  |  | 13.215 | 12.23 | [6 empty] | 24.41 | 8.0542 | 13.13
2011-11-16 | 6.9 | 6.27 |  |  |  |  | 7.1 | 1.89 |  |  |  |  | 34 |  |  |  | 0 | 1.141 |  |  | 0.287 | 0.374 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 24.8 |  | 6.2 | 0.142 |  | 7.7 | 80.2 | 1.29 |  |  |  |  | 13.956 | 11.433 | [6 empty] | 29.14 | 8.0479 | 13.09
2011-11-17 | 7.01 | 6.59 |  |  |  |  | 7.38 | 1.82 |  |  |  |  | 29 |  |  |  | 0 | 1.179 |  |  | 0.137 | 0.164 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 26.7 |  | 6.8 | 0.094 |  | 7.3 | 69.92 | 0.87 |  |  |  |  | 12.849 | 11.812 | [6 empty] | 30.44 | 8.0511 | 15.33
2011-11-18 | 6.5 | 6.51 |  |  |  |  | 6.9 | 1.17 |  |  |  |  | 74 |  |  |  | 0 | 1.178 |  |  | 0.211 | 0.346 | [5 empty] | 26.9 |  |  |  |  | 53.8 |  | 25.9 |  | 6.6 | 0.071 |  | 8.2 | 80.17 | 1.92 |  |  |  |  | 13.771 | 11.765 | [6 empty] | 27.12 | 8.0495 | 11.04
2011-11-19 | 6.58 | 6.23 |  |  |  |  | 7.28 | 1.86 |  |  |  |  | 44 |  |  |  | 0 | 0.97 |  |  | 0.138 | 0.415 | [5 empty] | 27.1 |  |  |  |  | 54.2 |  | 24.8 |  | 6.9 | 0.094 |  | 7.4 | 70.89 | 0.96 |  |  |  |  | 12.983 | 11.416 | [6 empty] | 30.07 | 8.0503 | 10.64
2011-11-20 | 6.49 | 6.125 |  |  |  |  | 7.235 | 1.68 |  |  |  |  | 50.5 |  |  |  | 0 | 0.9885 |  |  | 0.131 | 0.2735 | [5 empty] | 27.05 |  |  |  |  | 54.1 |  | 24.55 |  | 6.95 | 0.1015 |  | 7.3 | 69.92 | 1.25 |  |  |  |  | 12.383 | 10.845 | [6 empty] | 30.785 | 8.0499 | 10.84
2011-11-21 | 6.4 | 6.02 |  |  |  |  | 7.19 | 1.77 |  |  |  |  | 57 |  |  |  | 0 | 1.007 |  |  | 0.124 | 0.132 | [5 empty] | 27 |  |  |  |  | 54 |  | 24.3 |  | 7 | 0.109 |  | 7.2 | 75.17 | 1.21 |  |  |  |  | 14.014 | 11.456 | [6 empty] | 31.5 | 8.0501 | 10.74
2011-11-22 | 6.45 | 6.095 |  |  |  |  | 7.15 | 1.815 |  |  |  |  | 60 |  |  |  | 0 | 0.9605 |  |  | 0.1675 | 0.124 | [5 empty] | 27.025 |  |  |  |  | 54.05 |  | 24.05 |  | 6.975 | 0.10525 |  | 7.25 | 75.235 | 1.11 |  |  |  |  | 13.683 | 11.6735 | [6 empty] | 31.36 | 8.05 | 10.79
2011-11-23 | 6.5 | 6.17 |  |  |  |  | 7.11 | 1.86 |  |  |  |  | 63 |  |  |  | 0 | 0.914 |  |  | 0.211 | 0.116 | [5 empty] | 27.0125 |  |  |  |  | 54.025 |  | 23.8 |  | 6.9875 | 0.10712 |  | 7.225 | 75.3 | 1.01 |  |  |  |  | 13.352 | 11.891 | [6 empty] | 31.22 | 8.05 | 10.37
2011-11-24 | 6.49 | 6.17 |  |  |  |  | 7.05 | 2.08 |  |  |  |  | 60 |  |  |  | 0 | 0.897 |  |  | 0.226 | 0.114 | [5 empty] | 27.0187 |  |  |  |  | 54.0375 |  | 24.65 |  | 6.9812 | 0.10619 |  | 7.2375 | 74.31 | 0.79 |  |  |  |  | 13.197 | 11.742 | [6 empty] | 30.89 | 6.88 | 12.16
2011-11-25 | 7.03 | 6.18 |  |  |  |  | 7.02 | 2.09 |  |  |  |  | 44 |  |  |  | 0 | 0.92 |  |  | 0.256 | 0.112 | [5 empty] | 27.0156 |  |  |  |  | 54.0312 |  | 24.95 |  | 6.9844 | 0.10666 |  | 7.2312 | 75.3 | 0.8 |  |  |  |  | 13.276 | 11.797 | [6 empty] | 25.35 | 7.75 | 13.13
2011-11-26 | 6.9 | 6.56 |  |  |  |  | 7.72 | 2.1 |  |  |  |  | 41 |  |  |  | 0 | 0.856 |  |  | 0.384 | 0.604 | [5 empty] | 30.7 |  |  |  |  | 61.4 |  | 25.5 |  | 7.6 | 0.162 |  | 3.5 | 69.92 | 0.59 |  |  |  |  | 13.26 | 11.81 | [6 empty] | 26.29 | 6.95 | 18.56
2011-11-27 | 6.615 | 6.49 |  |  |  |  | 7.615 | 2.07 |  |  |  |  | 52.5 |  |  |  | 0.5 | 0.8365 |  |  | 0.4725 | 0.528 | [5 empty] | 30.85 |  |  |  |  | 61.7 |  | 25.25 |  | 7.45 | 0.1375 |  | 3.55 | 70.82 | 0.6 |  |  |  |  | 12.56 | 12.06 | [6 empty] | 26.29 | 6.95 | 18.56
2011-11-28 | 6.33 | 6.42 |  |  |  |  | 7.51 | 2.04 |  |  |  |  | 64 |  |  |  | 1 | 0.817 |  |  | 0.561 | 0.452 | [5 empty] | 31 |  |  |  |  | 62 |  | 25 |  | 7.3 | 0.113 |  | 3.6 | 79.27 | 1.1 |  |  |  |  | 13.789 | 11.444 | [6 empty] | 29.99 | 7.3 | 9.91
2011-11-29 | 6.55 | 6.27 |  |  |  |  | 7.29 | 2.08 |  |  |  |  | 66 |  |  |  | 0 | 0.796 |  |  | 0.256 | 0.163 | [5 empty] | 30.8 |  |  |  |  | 61.6 |  | 25.5 |  | 6.9 | 0.087 |  | 3.5 | 70.41 | 0.56 |  |  |  |  | 13.094 | 12.125 | [6 empty] | 32.12 | 8.68 | 9.39
2011-11-30 | 6.78 | 6.07 |  |  |  |  | 7.59 | 1.96 |  |  |  |  | 44 |  |  |  | 0 | 0.818 |  |  | 0.543 | 0.299 | [5 empty] | 32 |  |  |  |  | 64 |  | 24.5 |  | 7.4 | 0.136 |  | 3.5 | 76.06 | 0.94 |  |  |  |  | 13.902 | 11.906 | [6 empty] | 25.82 | 13.29 | 10.55
2011-12-01 | 6.58 | 6.31 |  |  |  |  | 7.47 | 1.8 |  |  |  |  | 38 |  |  |  | 0 | 0.748 |  |  | 0.415 | 0.131 | [5 empty] | 31.5 |  |  |  |  | 63 |  | 26.6 |  | 7.2 | 0.113 |  | 3.5 | 65.03 | 0.69 |  |  |  |  | 12.78 | 11.854 | [6 empty] | 25.82 | 12.83 | 10.81
2011-12-02 | 6.55 | 6.37 |  |  |  |  | 7.79 | 1.81 |  |  |  |  | 33 |  |  |  | 0 | 0.891 |  |  | 0.273 | 0.139 | [5 empty] | 30.7 |  |  |  |  | 61.4 |  | 27.4 |  | 6.9 | 0.101 |  | 4.3 | 65.51 | 0.71 |  |  |  |  | 13.325 | 11.821 | [6 empty] | 26.81 | 13.72 | 10.49
2011-12-03 | 6.62 | 6.28 |  |  |  |  | 7.26 | 1.82 |  |  |  |  | 27 |  |  |  | 0 | 0.729 |  |  | 0.123 | 0.327 | [5 empty] | 31.7 |  |  |  |  | 63.5 |  | 25 |  | 7 | 0.094 |  | 4.2 | 65.09 | 0.63 |  |  |  |  | 13.12 | 12.04 | [6 empty] | 29.51 | 13.275 | 12.62
2011-12-04 | 6.675 | 6.33 |  |  |  |  | 7.145 | 1.81 |  |  |  |  | 33.5 |  |  |  | 0 | 0.732 |  |  | 0.228 | 0.3455 | [5 empty] | 29.7 |  |  |  |  | 59.4 |  | 24.45 |  | 6.55 | 0.0755 |  | 3.85 | 64.815 | 0.62 |  |  |  |  | 13.4835 | 12.108 | [6 empty] | 26.725 | 13.4975 | 11.21
2011-12-05 | 6.73 | 6.38 |  |  |  |  | 7.03 | 1.8 |  |  |  |  | 40 |  |  |  | 0 | 0.735 |  |  | 0.333 | 0.364 | [5 empty] | 27.7 |  |  |  |  | 55.3 |  | 23.9 |  | 6.1 | 0.057 |  | 3.5 | 64.54 | 0.61 |  |  |  |  | 13.847 | 12.176 | [6 empty] | 23.94 | 13.3863 | 9.8
2011-12-06 | 6.4 | 6.16 |  |  |  |  | 7.22 | 1.86 |  |  |  |  | 39 |  |  |  | 0 | 0.729 |  |  | 0.175 | 0.178 | [5 empty] | 31.7 |  |  |  |  | 63.2 |  | 26.8 |  | 6.5 | 0.044 |  | 7 | 70.41 | 0.79 |  |  |  |  | 14.078 | 12.081 | [6 empty] | 24.41 | 13.4419 | 11.43
2011-12-07 | 6.48 | 6.15 |  |  |  |  | 7.42 | 1.89 |  |  |  |  | 30 |  |  |  | 0 | 0.678 |  |  | 0.137 | 0.239 | [5 empty] | 32 |  |  |  |  | 64 |  | 27.5 |  | 6.2 | 0.071 |  | 6.7 | 69.92 | 0.61 |  |  |  |  | 14.096 | 12.705 | [6 empty] | 25.65 | 13.4141 | 10.11
2011-12-08 | 6.26 | 6.11 |  |  |  |  | 7.09 | 1.92 |  |  |  |  | 54 |  |  |  | 0 | 0.743 |  |  | 0.113 | 0.252 | [5 empty] | 28.8 |  |  |  |  | 57.6 |  | 23.8 |  | 5.7 | 0.073 |  | 3.7 | 65.03 | 0.57 |  |  |  |  | 12.798 | 11.875 | [6 empty] | 26.55 | 12.84 | 14.53
2011-12-09 | 6.13 | 6.26 |  |  |  |  | 7.4 | 1.99 |  |  |  |  | 72 |  |  |  | 0 | 0.7105 |  |  | 0.214 | 0.138 | [5 empty] | 27.9 |  |  |  |  | 55.8 |  | 24.2 |  | 6.7 | 0.086 |  | 3.2 | 75.79 | 0.78 |  |  |  |  | 14.215 | 12.431 | [6 empty] | 33.82 | 11.59 | 11.13
2011-12-10 | 5.94 | 5.98 |  |  |  |  | 7.64 | 2.05 |  |  |  |  | 81 |  |  |  | 0 | 0.72675 |  |  | 0.146 | 0.113 | [5 empty] | 30.2 |  |  |  |  | 60.4 |  | 23.8 |  | 7.2 | 0.094 |  | 2.7 | 65.03 | 0.37 |  |  |  |  | 13.08 | 12.22 | [6 empty] | 33.87 | 12.76 | 10.58
2011-12-11 | 6.155 | 5.975 |  |  |  |  | 7.47 | 2.03 |  |  |  |  | 64.5 |  |  |  | 0 | 0.71863 |  |  | 0.1365 | 0.1115 | [5 empty] | 30.8 |  |  |  |  | 61.6 |  | 24.15 |  | 7.05 | 0.1185 |  | 2.85 | 70.41 | 0.72 |  |  |  |  | 12.481 | 11.607 | [6 empty] | 32.03 | 12.36 | 11.61
2011-12-12 | 6.37 | 5.97 |  |  |  |  | 7.3 | 1.94 |  |  |  |  | 48 |  |  |  | 0 | 0.72269 |  |  | 0.127 | 0.11 | [5 empty] | 31.4 |  |  |  |  | 62.8 |  | 24.5 |  | 6.9 | 0.143 |  | 3 | 74.82 | 1.01 |  |  |  |  | 13.695 | 11.501 | [6 empty] | 30.19 | 11.96 | 12.64
2011-12-13 | 6.19 | 5.75 |  |  |  |  | 7.75 | 1.95 |  |  |  |  | 57 |  |  |  | 0 | 0.72066 |  |  | 0.146 | 0.147 | [5 empty] | 32 |  |  |  |  | 64 |  | 21.6 |  | 7 | 0.124 |  | 2.5 | 66.1 | 0.86 |  |  |  |  | 12.964 | 10.679 | [6 empty] | 33.2 | 11.75 | 13.9
2011-12-14 | 6.05 | 6.52 |  |  |  |  | 7.14 | 1.9 |  |  |  |  | 65.5 |  |  |  | 0 | 0.72167 |  |  | 0.193 | 0.151 | [5 empty] | 29.9 |  |  |  |  | 59.8 |  | 21.9 |  | 6.8 | 0.131 |  | 2.7 | 55.3 | 0.25 |  |  |  |  | 12.541 | 11.668 | [6 empty] | 32.92 | 11.49 | 10.48
2011-12-15 | 6.15 | 5.88 |  |  |  |  | 8.11 | 1.95 |  |  |  |  | 74 |  |  |  | 1 | 0.72116 |  |  | 0.236 | 0.138 | [5 empty] | 28.9 |  |  |  |  | 57.8 |  | 24.8 |  | 7.1 | 0.148 |  | 3.4 | 74.33 | 0.82 |  |  |  |  | 14.001 | 12.196 | [6 empty] | 29.01 | 12.19 | 13.12
2011-12-16 | 6.53 | 6.19 |  |  |  |  | 8.46 | 1.92 |  |  |  |  | 70 |  |  |  | 0 | 0.72142 |  |  | 0.25 | 0.123 | [5 empty] | 32.8 |  |  |  |  | 65.7 |  | 23.8 |  | 8.4 | 0.114 |  | 3.5 | 65.51 | 0.56 |  |  |  |  | 12.836 | 11.966 | [6 empty] | 27.23 | 12.28 | 13.65
2011-12-17 | 6.7 | 5.98 |  |  |  |  | 8.3 | 1.89 |  |  |  |  | 68 |  |  |  | 0 | 0.72129 |  |  | 0.516 | 0.135 | [5 empty] | 33.1 |  |  |  |  | 66.3 |  | 25.2 |  | 7.8 | 0.126 |  | 3.4 | 64.95 | 0.4 |  |  |  |  | 13.78 | 12.9 | [6 empty] | 29.11 | 13.34 | 15.26
2011-12-18 | 6.32 | 6.055 |  |  |  |  | 8.455 | 1.95 |  |  |  |  | 71 |  |  |  | 0 | 0.72135 |  |  | 0.3645 | 0.1305 | [5 empty] | 34.15 |  |  |  |  | 68.35 |  | 25.55 |  | 7.85 | 0.1365 |  | 3.5 | 64.94 | 0.51 |  |  |  |  | 12.839 | 11.989 | [6 empty] | 29.11 | 13.34 | 15.26
2011-12-19 | 5.94 | 6.13 |  |  |  |  | 8.61 | 1.89 |  |  |  |  | 74 |  |  |  | 0 | 0.72132 |  |  | 0.213 | 0.126 | [5 empty] | 35.2 |  |  |  |  | 70.4 |  | 25.9 |  | 7.9 | 0.147 |  | 3.6 | 74.86 | 1.01 |  |  |  |  | 13.967 | 11.736 | [6 empty] | 36.79 | 13.14 | 14.87
2011-12-20 | 6.09 | 6.21 |  |  |  |  | 8.68 | 1.76 |  |  |  |  | 68 |  |  |  | 0 | 0.687 |  |  | 0.342 | 0.124 | [5 empty] | 33.4 |  |  |  |  | 66.8 |  | 24.6 |  | 7.2 | 0.137 |  | 3.6 | 64.94 | 1.01 |  |  |  |  | 12.937 | 10.63 | [6 empty] | 35.22 | 12.73 | 14.08
2011-12-21 | 6.47 | 6.5 |  |  |  |  | 8.12 | 1.85 |  |  |  |  | 60 |  |  |  | 0 | 0.70416 |  |  | 0.216 | 0.082 | [5 empty] | 33.6 |  |  |  |  | 67.3 |  | 25.7 |  | 7.8 | 0.131 |  | 3.7 | 60.15 | 0.48 |  |  |  |  | 12.56 | 11.714 | [6 empty] | 27.23 | 13.2 | 13.78
2011-12-22 | 6.74 | 6.49 |  |  |  |  | 7.79 | 1.9 |  |  |  |  | 68 |  |  |  | 0 | 0.69558 |  |  | 0.241 | 0.086 | [5 empty] | 33.6 |  |  |  |  | 67.3 |  | 23.9 |  | 7.8 | 0.112 |  | 3.7 | 69.92 | 0.75 |  |  |  |  | 13.724 | 11.973 | [6 empty] | 27.23 | 13.45 | 13.66
2011-12-23 | 6.71 | 6.38 |  |  |  |  | 7.38 | 1.9 |  |  |  |  | 57 |  |  |  | 0 | 0.69987 |  |  | 0.172 | 0.102 | [5 empty] | 32.1 |  |  |  |  | 64.2 |  | 26.3 |  | 7.7 | 0.128 |  | 3.7 | 60.13 | 0.66 |  |  |  |  | 12.451 | 10.65 | [6 empty] | 29.25 | 13.68 | 13.87
2011-12-24 | 6.77 | 6.42 |  |  |  |  | 6.94 | 1.87 |  |  |  |  | 69 |  |  |  | 0 | 0.69773 |  |  | 0.107 | 0.092 | [5 empty] | 30.7 |  |  |  |  | 61.4 |  | 23.1 |  | 6.4 | 0.099 |  | 4.1 | 65.31 | 0.74 |  |  |  |  | 12.74 | 11.38 | [6 empty] | 30.23 | 13.2 | 14.5
2011-12-25 | 6.59 | 6.455 |  |  |  |  | 6.685 | 1.85 |  |  |  |  | 68.5 |  |  |  | 0 | 0.6988 |  |  | 0.135 | 0.2 | [5 empty] | 29.85 |  |  |  |  | 59.75 |  | 24.4 |  | 6.6 | 0.0625 |  | 3.9 | 59.79 | 0.605 |  |  |  |  | 12.487 | 11.0565 | [6 empty] | 28.73 | 13.44 | 13.745
2011-12-26 | 6.41 | 6.49 |  |  |  |  | 6.43 | 1.83 |  |  |  |  | 68 |  |  |  | 0 | 0.69826 |  |  | 0.163 | 0.308 | [5 empty] | 29 |  |  |  |  | 58.1 |  | 25.7 |  | 6.8 | 0.026 |  | 3.7 | 54.27 | 0.47 |  |  |  |  | 12.234 | 10.733 | [6 empty] | 27.23 | 13.32 | 12.99
2011-12-27 | 7.14 | 6.3 |  |  |  |  | 6.79 | 1.81 |  |  |  |  | 65 |  |  |  | 0 | 0.69853 |  |  | 0.189 | 0.328 | [5 empty] | 30.1 |  |  |  |  | 60.2 |  | 23.6 |  | 6.3 | 0.036 |  | 3.7 | 65.03 | 0.73 |  |  |  |  | 13.066 | 11.639 | [6 empty] | 26.76 | 13.38 | 11.6
2011-12-28 | 6.74 | 6.37 |  |  |  |  | 7.3 | 1.72 |  |  |  |  | 60 |  |  |  | 0 | 0.6984 |  |  | 0.092 | 0.309 | [5 empty] | 30 |  |  |  |  | 60 |  | 22.1 |  | 6.9 | 0.048 |  | 3.7 | 55.26 | 0.55 |  |  |  |  | 12.492 | 11.057 | [6 empty] | 28.33 | 13.35 | 11.42
2011-12-29 | 6.59 | 6.22 |  |  |  |  | 7.31 | 1.7 |  |  |  |  | 59 |  |  |  | 0 | 0.69846 |  |  | 0.117 | 0.467 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 25 |  | 6.1 | 0.102 |  | 3.8 | 60.13 | 0.71 |  |  |  |  | 13.216 | 11.343 | [6 empty] | 27.23 | 10.77 | 11.66
2011-12-30 | 6.35 | 6.4 |  |  |  |  | 7.35 | 1.81 |  |  |  |  | 58 |  |  |  | 0 | 0.69843 |  |  | 0.326 | 0.304 | [5 empty] | 29.4 |  |  |  |  | 58.8 |  | 24.7 |  | 6.3 | 0.098 |  | 3.4 | 60.13 | 0.36 |  |  |  |  | 13.473 | 12.578 | [6 empty] | 35.22 | 12.21 | 10.68
2011-12-31 | 6.08 | 6.25 |  |  |  |  | 6.97 | 1.82 |  |  |  |  | 59 |  |  |  | 0 | 0.69845 |  |  | 0.197 | 0.308 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 25.3 |  | 6.1 | 0.087 |  | 3.3 | 58.38 | 0.41 |  |  |  |  | 13.25 | 11.9 | [6 empty] | 27.78 | 11.12 | 10.95

## 2012
All of the data presented below was copied verbatim from spreadsheets transcribed by Debbie Rideout, Town PLO
| pH | [6 empty] | Chlorine |  |  |  | Colour | [5 empty] | Turbidity | [5 empty] | Total Dissolved Solids |  |  |  |  | Conductivity |  |  |  |  | Hardness |  | Alkalinity |  | Aluminum | Temperature |  | Cl Used | Cl Demand | UVT |  | UVA |  | Flows within plant |  |  |  | Flows from plant |  |  | Chemical Dosages |  |  |  | Dennis Penney
Date | Raw | PTC | PTC (OL) | SWC | Filter | Finish (OL) | Finish | Free | Total | Sample | Analyzer | Raw A | Raw T | SWC A | Filter A | Finish A | Finish T | Raw | Raw (OL) | SWC | Filter | Finish | Finish (OL) | Raw | PTC | SWC | Filter | Finish | Raw | PTC | SWC | Filter | Finish | Raw | Finish | Raw | Finish | Finish (Free) | Raw | Finish |  |  | Raw | Filter | Raw | Filter | Raw | Finish | Filter | Backwash | Bishop's | Botwood | GFW | Chlorine | Alum | Limestone | Lime | Jerry Loveless
2012-01-01 | 6.58 | 6.1 |  |  |  |  | 7.105 | 1.82 |  |  |  |  | 39.5 |  |  |  | 0 | 1.244 |  |  | 0.162 | 0.3265 | [5 empty] | 32.1 |  |  |  |  | 64.2 |  | 22.9 |  | 6.3 | 0.068 |  | 3.25 | 61.25 | 0.6 |  |  |  |  | 12.881 | 11.49 | [6 empty] | 27.52 | 12.28 | 11.905 | Noland Simms
2012-01-02 | 6.62 | 6.15 |  |  |  |  | 7.09 | 1.86 |  |  |  |  | 55 |  |  |  | 0 | 1.277 |  |  | 0.129 | 0.337 | [5 empty] | 30.7 |  |  |  |  | 61.4 |  | 25 |  | 6.2 | 0.08 |  | 3.4 | 69.99 | 0.63 |  |  |  |  | 14.11 | 12.769 | [6 empty] | 26.11 | 11.27 | 12.9
2012-01-03 | 6.54 | 6.05 |  |  |  |  | 7.12 | 1.87 |  |  |  |  | 24 |  |  |  | 0 | 1.211 |  |  | 0.195 | 0.316 | [5 empty] | 33.5 |  |  |  |  | 67 |  | 20.8 |  | 6.4 | 0.056 |  | 3.1 | 69.89 | 0.64 |  |  |  |  | 14.023 | 12.648 | [6 empty] | 28.93 | 13.29 | 10.91
2012-01-04 | 5.75 | 5.75 |  |  |  |  | 7.43 | 1.87 |  |  |  |  | 54 |  |  |  | 1 | 1.235 |  |  | 0.208 | 0.267 | [5 empty] | 32.4 |  |  |  |  | 65 |  | 21.3 |  | 6.1 | 0.067 |  | 3 | 65.47 | 0.53 |  |  |  |  | 13.722 | 12.383 | [6 empty] | 36.37 | 1.63 | 10.89 | Continuous
2012-01-05 | 6.11 | 5.91 |  |  |  |  | 7.24 | 1.93 |  |  |  |  | 53 |  |  |  | 0 | 1.227 |  |  | 0.196 | 0.154 | [5 empty] | 33.1 |  |  |  |  | 66.2 |  | 22 |  | 6.3 | 0.086 |  | 3.1 | 65.09 | 0.43 |  |  |  |  | 13.511 | 12.534 | [6 empty] | 33.51 | 11.02 | 14.02 | Grab
2012-01-06 | 7.02 | 6.37 |  |  |  |  | 7.36 | 1.99 |  |  |  |  | 48 |  |  |  | 0 | 1.146 |  |  | 0.288 | 0.17 | [5 empty] | 33.8 |  |  |  |  | 67.5 |  | 21 |  | 7.3 | 0.092 |  | 3 | 75.27 | 0.78 |  |  |  |  | 14.152 | 12.346 | [6 empty] | 25.35 | 13.24 | 12.11 | ^ Stuff for form dropdown menus
2012-01-07 | 5.86 | 5.91 |  |  |  |  | 7.2 | 1.97 |  |  |  |  | 51 |  |  |  | 0 | 1.183 |  |  | 0.297 | 0.256 | [5 empty] | 32.2 |  |  |  |  | 64.4 |  | 21.5 |  | 7.1 | 0.087 |  | 3.1 | 69.92 | 0.57 |  |  |  |  | 12.99 | 12.52 | [6 empty] | 25.35 | 13.24 | 12.11
2012-01-08 | 5.96 | 5.945 |  |  |  |  | 7.1 | 1.97 |  |  |  |  | 62.5 |  |  |  | 0 | 1.1395 |  |  | 0.254 | 0.3415 | [5 empty] | 32.5 |  |  |  |  | 65 |  | 21.35 |  | 6.9 | 0.084 |  | 3.25 | 65.03 | 0.84 |  |  |  |  | 12.368 | 10.516 | [6 empty] | 25.35 | 13.24 | 12.11
2012-01-09 | 6.06 | 5.98 |  |  |  |  | 7 | 2.03 |  |  |  |  | 74 |  |  |  | 0 | 1.096 |  |  | 0.211 | 0.427 | [5 empty] | 32.8 |  |  |  |  | 65.6 |  | 21.2 |  | 6.7 | 0.081 |  | 3.4 | 75.37 | 0.87 |  |  |  |  | 14.126 | 11.795 | [6 empty] | 28.74 | 13.15 | 10.84
2012-01-10 | 6.14 | 5.98 |  |  |  |  | 7.03 | 2.05 |  |  |  |  | 73 |  |  |  | 0 | 1.068 |  |  | 0.198 | 0.196 | [5 empty] | 33.2 |  |  |  |  | 66.4 |  | 23.5 |  | 6.4 | 0.076 |  | 3 | 69.92 | 0.94 |  |  |  |  | 12.977 | 10.618 | [6 empty] | 29.43 | 13.28 | 10.95
2012-01-11 | 6.86 | 6.16 |  |  |  |  | 7.17 | 2.07 |  |  |  |  | 46 |  |  |  | 0 | 1.033 |  |  | 0.164 | 0.213 | [5 empty] | 34.8 |  |  |  |  | 69.4 |  | 21.9 |  | 7.1 | 0.071 |  | 3.1 | 70.33 | 0.68 |  |  |  |  | 12.998 | 11.623 | [6 empty] | 23.47 | 12.357 | 12.68
2012-01-12 | 7 | 6.49 |  |  |  |  | 7.18 | 2.06 |  |  |  |  | 42 |  |  |  | 0 | 1.036 |  |  | 0.218 | 0.257 | [5 empty] | 34.2 |  |  |  |  | 68.5 |  | 30.1 |  | 12.2 | 0.11 |  | 3.1 | 75.3 | 0.72 |  |  |  |  | 13.574 | 12.293 | [6 empty] | 23.94 | 12.29 | 13.45
2012-01-13 | 6.94 | 6.71 |  |  |  |  | 7.29 | 1.98 |  |  |  |  | 39 |  |  |  | 0 | 0.961 |  |  | 0.173 | 0.151 | [5 empty] | 34.7 |  |  |  |  | 69.4 |  | 25.8 |  | 7.8 | 0.094 |  | 3 | 69.99 | 0.7 |  |  |  |  | 13.158 | 11.863 | [6 empty] | 25.44 | 12.69 | 13.06
2012-01-14 | 6.79 | 6.61 |  |  |  |  | 7.28 | 1.9 |  |  |  |  | 44 |  |  |  | 0 | 0.998 |  |  | 0.094 | 0.131 | [5 empty] | 32.7 |  |  |  |  | 65.4 |  | 26.3 |  | 6.2 | 0.107 |  | 3 | 65.03 | 0.62 |  |  |  |  | 13.09 | 11.7 | [6 empty] | 24.48 | 8.16 | 14.59
2012-01-15 | 7.27 | 7.14 |  |  |  |  | 7.14 | 1.91 |  |  |  |  | 39 |  |  |  | 0 | 0.968 |  |  | 0.494 | 0.472 | [5 empty] | 33.1 |  |  |  |  | 66.3 |  | 25.3 |  | 11.3 | 0.084 |  | 3 | 69.92 | 0.81 |  |  |  |  | 13.557 | 11.656 | [6 empty] | 23 | 5.61 | 12.25
2012-01-16 | 7.02 | 6.73 |  |  |  |  | 7.395 | 1.89 |  |  |  |  | 38.5 |  |  |  | 0 | 0.9335 |  |  | 0.427 | 0.345 | [5 empty] | 32.95 |  |  |  |  | 66 |  | 25.9 |  | 10.75 | 0.0786 |  | 3 | 69.68 | 0.725 |  |  |  |  | 13.773 | 12.1165 | [6 empty] | 23.47 | 7.345 | 11.215
2012-01-17 | 6.77 | 6.32 |  |  |  |  | 7.65 | 1.87 |  |  |  |  | 38 |  |  |  | 0 | 0.899 |  |  | 0.36 | 0.218 | [5 empty] | 32.8 |  |  |  |  | 65.7 |  | 26.5 |  | 10.2 | 0.0732 |  | 3 | 69.44 | 0.64 |  |  |  |  | 13.989 | 12.577 | [6 empty] | 23.94 | 9.08 | 10.18
2012-01-18 | 6.69 | 6.39 |  |  |  |  | 7.35 | 1.8 |  |  |  |  | 36 |  |  |  | 0 | 0.842 |  |  | 0.217 | 0.35 | [5 empty] | 32.9 |  |  |  |  | 65.8 |  | 26.1 |  | 9.9 | 0.061 |  | 2.7 | 65.03 | 0.7 |  |  |  |  | 13.343 | 11.792 | [6 empty] | 24.5 | 9.27 | 11.12
2012-01-19 | 6.69 | 6.48 |  |  |  |  | 7.47 | 1.79 |  |  |  |  | 34 |  |  |  | 0 | 0.861 |  |  | 0.243 | 0.273 | [5 empty] | 33.4 |  |  |  |  | 66.8 |  | 26.8 |  | 7.6 | 0.109 |  | 2.8 | 65.03 | 0.63 |  |  |  |  | 13.185 | 12.204 | [6 empty] | 25.78 | 10.05 | 12.38
2012-01-20 | 5.43 | 6.53 |  |  |  |  | 7.18 | 1.72 |  |  |  |  | 37 |  |  |  | 6 | 0.816 |  |  | 1.36 | 0.496 | [5 empty] | 32.6 |  |  |  |  | 65.2 |  | 25.8 |  | 7.1 | 0.114 |  | 3.1 | 70.47 | 1.04 |  |  |  |  | 13.619 | 11.574 | [6 empty] | 26.13 | 9.39 | 11.87
2012-01-21 | 6.09 | 6.2 |  |  |  |  | 7.35 | 1.84 |  |  |  |  | 35 |  |  |  | 0 | 0.847 |  |  | 0.217 | 0.394 | [5 empty] | 34.2 |  |  |  |  | 68.4 |  | 24.6 |  | 7.4 | 0.083 |  | 3.1 | 60.2 | 0.57 |  |  |  |  | 12.33 | 11.36 | [6 empty] | 29.99 | 12.36 | 11.41
2012-01-22 | 6.225 | 6.07 |  |  |  |  | 7.225 | 1.85 |  |  |  |  | 41 |  |  |  | 0 | 0.834 |  |  | 0.319 | 0.4075 | [5 empty] | 35.4 |  |  |  |  | 70.8 |  | 25.2 |  | 7.4 | 0.096 |  | 3.25 | 65.09 | 0.69 |  |  |  |  | 12.596 | 11.636 | [6 empty] | 30.075 | 12.385 | 12.325
2012-01-23 | 6.36 | 5.94 |  |  |  |  | 7.1 | 1.76 |  |  |  |  | 47 |  |  |  | 0 | 0.821 |  |  | 0.421 | 0.421 | [5 empty] | 36.6 |  |  |  |  | 73.2 |  | 25.8 |  | 7.4 | 0.109 |  | 3.4 | 69.92 | 0.96 |  |  |  |  | 14.047 | 11.739 | [6 empty] | 30.16 | 12.41 | 13.24
2012-01-24 | 6.59 | 5.97 |  |  |  |  | 7.65 | 1.72 |  |  |  |  | 41 |  |  |  | 0 | 0.819 |  |  | 0.192 | 0.171 | [5 empty] | 35.9 |  |  |  |  | 71.8 |  | 26.5 |  | 7.4 | 0.114 |  | 3.2 | 59.64 | 0.9 |  |  |  |  | 12.716 | 10.347 | [6 empty] | 28.16 | 11.6 | 13.71
2012-01-25 | 5.42 | 6.25 |  |  |  |  | 7.48 | 1.63 |  |  |  |  | 38 |  |  |  | 0 | 0.795 |  |  | 0.579 | 0.243 | [5 empty] | 35.2 |  |  |  |  | 70.4 |  | 25.7 |  | 7.1 | 0.103 |  | 3.4 | 65.69 | 0.92 |  |  |  |  | 13.98 | 11.706 | [6 empty] | 28.84 | 11.3 | 14.18
2012-01-26 | 5.86 | 6.16 |  |  |  |  | 7.53 | 1.71 |  |  |  |  | 39 |  |  |  | 0 | 0.796 |  |  | 0.211 | 0.153 | [5 empty] | 37.4 |  |  |  |  | 74.8 |  | 23.8 |  | 7.8 | 0.064 |  | 3.3 | 59.64 | 0.45 |  |  |  |  | 13.03 | 12.56 | [6 empty] | 28.43 | 14.07 | 11.84
2012-01-27 | 7.16 | 6 |  |  |  |  | 6.98 | 1.67 |  |  |  |  | 38 |  |  |  | 0 | 0.775 |  |  | 0.277 | 0.175 | [5 empty] | 38.9 |  |  |  |  | 7.8 |  | 23.5 |  | 7.9 | 0.058 |  | 3.2 | 65.03 | 0.9 |  |  |  |  | 12.849 | 11.475 | [6 empty] | 25.11 | 12.26 | 16.1
2012-01-28 | 6.56 | 6.09 |  |  |  |  | 7.63 | 1.68 |  |  |  |  | 37 |  |  |  | 0 | 0.768 |  |  | 0.32 | 0.183 | [5 empty] | 39.6 |  |  |  |  | 79.2 |  | 25.4 |  | 8.2 | 0.044 |  | 3.3 | 65.03 | 0.75 |  |  |  |  | 13.49 | 12.13 | [6 empty] | 16.76 | 12.29 | 16.62
2012-01-29 | 6.12 | 6.11 |  |  |  |  | 7.14 | 1.55 |  |  |  |  | 42.5 |  |  |  | 1.5 | 0.7535 |  |  | 0.345 | 0.1735 | [5 empty] | 38.85 |  |  |  |  | 77.7 |  | 25 |  | 8.05 | 0.05 |  | 3.35 | 46.31 | 0.37 |  |  |  |  | 12.944 | 11.544 | [6 empty] | 26.76 | 12.29 | 16.62
2012-01-30 | 5.68 | 6.13 |  |  |  |  | 6.65 | 1.42 |  |  |  |  | 48 |  |  |  | 3 | 0.739 |  |  | 0.37 | 0.164 | [5 empty] | 38.1 |  |  |  |  | 76.2 |  | 24.6 |  | 7.9 | 0.056 |  | 3.4 | 54.77 | 0.63 |  |  |  |  | 14.452 | 12.144 | [6 empty] | 28.48 | 12.72 | 12.07
2012-01-31 | 6.11 | 6.01 |  |  |  |  | 7.13 | 1.48 |  |  |  |  | 46 |  |  |  | 2 | 0.756 |  |  | 0.214 | 0.143 | [5 empty] | 38.8 |  |  |  |  | 77.6 |  | 25.4 |  | 6.7 | 0.061 |  | 3.2 | 65.03 | 0.68 |  |  |  |  | 14.1 | 13.64 | [6 empty] | 29.78 | 13.49 | 14.13
2012-02-01 | 5.895 | 6.12 |  |  |  |  | 6.89 | 1.45 |  |  |  |  | 47 |  |  |  | 2.5 | 0.7475 |  |  | 0.292 | 0.1535 | [5 empty] | 38.45 |  |  |  |  | 76.9 |  | 25 |  | 7.3 | 0.0585 |  | 3.3 | 59.9 | 0.655 |  |  |  |  | 13.698 | 11.844 | [6 empty] | 29.13 | 13.105 | 13.1
2012-02-02 | 6.0025 | 6.07 |  |  |  |  | 7.01 | 1.465 |  |  |  |  | 46.5 |  |  |  | 2.25 | 0.75175 |  |  | 0.253 | 0.14825 | [5 empty] | 38.625 |  |  |  |  | 77.25 |  | 25.2 |  | 7 | 0.05975 |  | 3.25 | 62.465 | 0.6675 |  |  |  |  | 14.276 | 12.892 | [6 empty] | 29.455 | 13.2975 | 13.615
2012-02-03 | 6.11 | 5.85 |  |  |  |  | 7.27 | 1.45 |  |  |  |  | 31 |  |  |  | 0 | 0.747 |  |  | 0.211 | 0.159 | [5 empty] | 37.8 |  |  |  |  | 75.6 |  | 26.8 |  | 7.5 | 0.104 |  | 3.4 | 55.32 | 0.63 |  |  |  |  | 13.45 | 12.052 | [6 empty] | 26.06 | 12.12 | 11.36
2012-02-04 | 6.05 | 5.96 |  |  |  |  | 7.63 | 1.48 |  |  |  |  | 30 |  |  |  | 0 | 0.654 |  |  | 0.312 | 0.197 | [5 empty] | 36.7 |  |  |  |  | 73.4 |  | 25.5 |  | 7 | 0.11 |  | 3.4 | 65.03 | 0.89 |  |  |  |  | 14.74 | 12.46 | [6 empty] | 26.25 | 11.9 | 10.91
2012-02-05 | 6.08 | 5.96 |  |  |  |  | 7.45 | 1.465 |  |  |  |  | 30.5 |  |  |  | 0 | 0.7005 |  |  | 0.2615 | 0.178 | [5 empty] | 37.25 |  |  |  |  | 74.5 |  | 26.15 |  | 7.25 | 0.107 |  | 3.4 | 60.175 | 0.76 |  |  |  |  | 13.863 | 12.472 | [6 empty] | 26.155 | 12.01 | 11.135
2012-02-06 | 6.53 | 5.98 |  |  |  |  | 6.58 | 1.38 |  |  |  |  | 33 |  |  |  | 0 | 0.749 |  |  | 0.697 | 0.363 | [5 empty] | 35.4 |  |  |  |  | 70.8 |  | 24 |  | 9.2 | 0.114 |  | 3.2 | 59.16 | 0.75 |  |  |  |  | 13.975 | 12.602 | [6 empty] | 25.35 | 11.53 | 16.17
2012-02-07 | 6.53 | 6.25 |  |  |  |  | 7.39 | 1.46 |  |  |  |  | 29 |  |  |  | 0 | 0.743 |  |  | 1.03 | 0.441 | [5 empty] | 34.7 |  |  |  |  | 69.2 |  | 24.7 |  | 8.7 | 0.106 |  | 3.5 | 60.13 | 0.62 |  |  |  |  | 14.52 | 13.138 | [6 empty] | 25.82 | 11.77 | 16.67
2012-02-08 | 6.65 | 6.24 |  |  |  |  | 7.23 | 1.47 |  |  |  |  | 28 |  |  |  | 0 | 0.734 |  |  | 0.591 | 0.305 | [5 empty] | 34.9 |  |  |  |  | 69.8 |  | 24 |  | 8.2 | 0.087 |  | 3.6 | 65.03 | 0.84 |  |  |  |  | 14.121 | 12.77 | [6 empty] | 26.22 | 11.65 | 14.23
2012-02-09 | 6.54 | 5.87 |  |  |  |  | 7.46 | 1.5 |  |  |  |  | 32 |  |  |  | 0 | 0.723 |  |  | 0.39 | 0.429 | [5 empty] | 34.1 |  |  |  |  | 68.2 |  | 26.8 |  | 7 | 0.079 |  | 3.3 | 60.13 | 0.67 |  |  |  |  | 14.01 | 12.605 | [6 empty] | 26.72 | 11.71 | 14.72
2012-02-10 | 6.16 | 6.09 |  |  |  |  | 7.8 | 1.48 |  |  |  |  | 33 |  |  |  | 2 | 0.736 |  |  | 0.506 | 0.365 | [5 empty] | 32.9 |  |  |  |  | 65.8 |  | 25.8 |  | 7.3 | 0.096 |  | 4 | 60.15 | 0.75 |  |  |  |  | 13.596 | 12.259 | [6 empty] | 28.76 | 11.68 | 15.11
2012-02-11 | 6.71 | 6.07 |  |  |  |  | 7.63 | 1.51 |  |  |  |  | 42 |  |  |  | 1 | 0.728 |  |  | 0.317 | 0.197 | [5 empty] | 33.5 |  |  |  |  | 67 |  | 25.1 |  | 6.9 | 0.0875 |  | 3.65 | 60.13 | 0.73 |  |  |  |  | 13.581 | 12.182 | [6 empty] | 29.1 | 11.695 | 13
2012-02-12 | 6.435 | 5.98 |  |  |  |  | 7.715 | 1.43 |  |  |  |  | 37.5 |  |  |  | 1.5 | 0.732 |  |  | 0.4115 | 0.281 | [5 empty] | 33.2 |  |  |  |  | 66.4 |  | 25.45 |  | 7.1 | 0.09175 |  | 3.825 | 54.75 | 0.67 |  |  |  |  | 13.209 | 11.828 | [6 empty] | 28.93 | 11.6875 | 14.055
2012-02-13 | 6.63 | 6.17 |  |  |  |  | 7.6725 | 1.42 |  |  |  |  | 42 |  |  |  | 1.25 | 0.674 |  |  | 0.345 | 0.239 | [5 empty] | 33.35 |  |  |  |  | 66.7 |  | 25.275 |  | 7 | 0.089625 |  | 3.7375 | 65.09 | 1.01 |  |  |  |  | 14.422 | 12.145 | [6 empty] | 26.8 | 11.6913 | 11.75
2012-02-14 | 6.4 | 6.17 |  |  |  |  | 7.6937 | 1.41 |  |  |  |  | 33 |  |  |  | 1.375 | 0.783 |  |  | 0.582 | 0.26 | [5 empty] | 33.275 |  |  |  |  | 66.55 |  | 25.3625 |  | 7.05 | 0.090688 |  | 3.7812 | 55.26 | 0.87 |  |  |  |  | 13.302 | 10.979 | [6 empty] | 31.2 | 11.6894 | 15.64
2012-02-15 | 5.75 | 6.32 |  |  |  |  | 7.76 | 1.3 |  |  |  |  | 46 |  |  |  | 3 | 0.856 |  |  | 1.13 | 0.476 | [5 empty] | 35.8 |  |  |  |  | 71.6 |  | 23.6 |  | 12.3 | 0.053 |  | 3.7594 | 59.65 | 0.98 |  |  |  |  | 13.655 | 11.858 | [6 empty] | 27.82 | 10.11 | 13.84
2012-02-16 | 6.28 | 6.09 |  |  |  |  | 7.39 | 1.45 |  |  |  |  | 47 |  |  |  | 0 | 0.837 |  |  | 0.768 | 0.293 | [5 empty] | 38.6 |  |  |  |  | 77.2 |  | 23.7 |  | 9.7 | 0.068 |  | 3.1 | 60.15 | 0.69 |  |  |  |  | 13.646 | 12.756 | [6 empty] | 29.66 | 6.26 | 7.88
2012-02-17 | 6.47 | 6.41 |  |  |  |  | 7.95 | 1.4 |  |  |  |  | 44 |  |  |  | 0 | 0.82 |  |  | 0.544 | 0.408 | [5 empty] | 38.6 |  |  |  |  | 77.3 |  | 21.8 |  | 12.3 | 0.104 |  | 2.8 | 60.13 | 0.81 |  |  |  |  | 13.614 | 12.319 | [6 empty] | 25.35 | 12.21 | 14.15
2012-02-18 | 6.375 | 6.205 |  |  |  |  | 7.67 | 1.42 |  |  |  |  | 41 |  |  |  | 0 | 0.799 |  |  | 0.583 | 0.294 | [5 empty] | 37.3 |  |  |  |  | 74.6 |  | 25.5 |  | 1.2 | 0.13 |  | 2.8 | 60.13 | 0.73 |  |  |  |  | 13.5 | 12.67 | [6 empty] | 25.35 | 13.32 | 14.87
2012-02-19 | 6.4225 | 6.25 |  |  |  |  | 7.81 | 1.41 |  |  |  |  | 42.5 |  |  |  | 0 | 0.8095 |  |  | 0.5635 | 0.351 | [5 empty] | 37.95 |  |  |  |  | 75.95 |  | 23.65 |  | 6.75 | 0.117 |  | 2.8 | 54.77 | 0.51 |  |  |  |  | 13.36 | 12.96 | [6 empty] | 25.35 | 13.32 | 14.87
2012-02-20 | 6.25 | 6.17 |  |  |  |  | 7.33 | 1.38 |  |  |  |  | 47 |  |  |  | 1 | 0.756 |  |  | 0.906 | 0.812 | [5 empty] | 35.2 |  |  |  |  | 70.4 |  | 25.1 |  | 7.5 | 0.054 |  | 2.7 | 60.13 | 0.82 |  |  |  |  | 14.667 | 12.414 | [6 empty] | 24.66 | 13.46 | 13.98
2012-02-21 | 6.29 | 6.15 |  |  |  |  | 7.69 | 1.49 |  |  |  |  | 37 |  |  |  | 0 | 0.603 |  |  | 0.316 | 0.176 | [5 empty] | 36.4 |  |  |  |  | 72.8 |  | 25.7 |  | 11.5 | 0.053 |  | 2.8 | 55.92 | 0.5 |  |  |  |  | 14.02 | 12.721 | [6 empty] | 31.43 | 12.18 | 11.93
2012-02-22 | 6.52 | 6.3 |  |  |  |  | 8.05 | 1.41 |  |  |  |  | 34 |  |  |  | 0 | 0.653 |  |  | 0.155 | 0.269 | [5 empty] | 35.5 |  |  |  |  | 71.2 |  | 33.9 |  | 11.5 | 0.133 |  | 2.9 | 62.07 | 0.73 |  |  |  |  | 14.847 | 13.14 | [6 empty] | 25.82 | 13.05 | 18
2012-02-23 | 6.65 | 5.88 |  |  |  |  | 7.5 | 1.42 |  |  |  |  | 36 |  |  |  | 0 | 0.563 |  |  | 0.105 | 0.225 | [5 empty] | 35.1 |  |  |  |  | 70.3 |  | 29.6 |  | 11.3 | 0.083 |  | 3 | 60.15 | 0.66 |  |  |  |  | 14.451 | 13.119 | [6 empty] | 26.29 | 13.46 | 12.56
2012-02-24 | 6.54 | 6.1 |  |  |  |  | 6.67 | 1.46 |  |  |  |  | 44 |  |  |  | 0 | 0.577 |  |  | 0.097 | 0.339 | [5 empty] | 33.1 |  |  |  |  | 66.2 |  | 28.6 |  | 12.1 | 0.089 |  | 3.1 | 60.13 | 0.65 |  |  |  |  | 14.292 | 12.923 | [6 empty] | 27.06 | 13.5 | 11.64
2012-02-25 | 6.71 | 6.09 |  |  |  |  | 7.44 | 1.47 |  |  |  |  | 30 |  |  |  | 0 | 0.594 |  |  | 0.074 | 0.315 | [5 empty] | 34.5 |  |  |  |  | 69 |  | 27.3 |  | 10.5 | 0.102 |  | 3.2 | 60.13 | 0.79 |  |  |  |  | 13.46 | 12.08 | [6 empty] | 26.77 | 14.07 | 12.62
2012-02-26 | 6.625 | 5.99 |  |  |  |  | 7.055 | 1.465 |  |  |  |  | 37 |  |  |  | 0 | 0.5855 |  |  | 0.0855 | 0.327 | [5 empty] | 33.8 |  |  |  |  | 67.6 |  | 27.95 |  | 11.3 | 0.0955 |  | 3.15 | 60.13 | 0.72 |  |  |  |  | 14.3715 | 13.021 | [6 empty] | 26.915 | 13.785 | 12.13
2012-02-27 | 6.73 | 6.17 |  |  |  |  | 7.3 | 1.4 |  |  |  |  | 37 |  |  |  | 0 | 0.661 |  |  | 0.113 | 0.322 | [5 empty] | 34.5 |  |  |  |  | 67.8 |  | 29 |  | 10.3 | 0.052 |  | 2.9 | 55.3 | 0.64 |  |  |  |  | 13.667 | 12.303 | [6 empty] | 26.29 | 13.23 | 12.56
2012-02-28 | 6.7 | 6.06 |  |  |  |  | 7.6 | 1.35 |  |  |  |  | 38 |  |  |  | 0 | 0.576 |  |  | 0.144 | 0.184 | [5 empty] | 33.9 |  |  |  |  | 68 |  | 29.2 |  | 10.7 | 0.051 |  | 2.9 | 60.62 | 0.79 |  |  |  |  | 13.569 | 12.713 | [6 empty] | 25.35 | 12.7 | 13.24
2012-02-29 | 6.64 | 5.43 |  |  |  |  | 5.79 | 1.31 |  |  |  |  | 31 |  |  |  | 0 | 1.74 |  |  | 0.101 | 0.114 | [5 empty] | 34.1 |  |  |  |  | 68.2 |  | 27.8 |  | 8.1 | 0.057 |  | 2.9 | 54.75 | 0.6 |  |  |  |  | 13.904 | 13.026 | [6 empty] | 25.77 | 12 | 12.9
2012-03-01 | 6.62 | 6.54 |  |  |  |  | 7.63 | 1.35 |  |  |  |  | 36 |  |  |  | 0 | 1.75 |  |  | 0.092 | 0.194 | [5 empty] | 34.7 |  |  |  |  | 69.4 |  | 28.2 |  | 9.9 | 0.054 |  | 2.8 | 55.26 | 0.62 |  |  |  |  | 14.11 | 12.736 | [6 empty] | 26.13 | 11.17 | 13.27
2012-03-02 | 6.05 | 6.62 |  |  |  |  | 7.54 | 1.33 |  |  |  |  | 37 |  |  |  | 0 | 2.06 |  |  | 0.151 | 0.355 | [5 empty] | 34.3 |  |  |  |  | 68.6 |  | 26.9 |  | 9.3 | 0.063 |  | 3 | 49.86 | 0.48 |  |  |  |  | 13.782 | 12.488 | [6 empty] | 29.56 | 11.81 | 12.25
2012-03-03 | 6.14 | 6.03 |  |  |  |  | 7.23 | 1.21 |  |  |  |  | 39 |  |  |  | 0 | 2.806 |  |  | 0.137 | 0.203 | [5 empty] | 34.2 |  |  |  |  | 68.4 |  | 26 |  | 8.7 | 0.071 |  | 3 | 49.88 | 0.55 |  |  |  |  | 14.21 | 12.85 | [6 empty] | 29.99 | 11.59 | 12.14
2012-03-04 | 6.095 | 6.58 |  |  |  |  | 7.385 | 1.27 |  |  |  |  | 38 |  |  |  | 0 | 2.433 |  |  | 0.144 | 0.279 | [5 empty] | 34.25 |  |  |  |  | 68.5 |  | 26.45 |  | 9 | 0.067 |  | 3 | 49.87 | 0.515 |  |  |  |  | 13.446 | 12.068 | [6 empty] | 29.775 | 11.7 | 12.195
2012-03-05 | 6.49 | 5.77 |  |  |  |  | 7.11 | 1.29 |  |  |  |  | 39 |  |  |  | 0 | 0.814 |  |  | 0.103 | 0.247 | [5 empty] | 32.6 |  |  |  |  | 65.2 |  | 25.4 |  | 7.7 | 0.084 |  | 3.1 | 55.23 | 0.69 |  |  |  |  | 13.969 | 12.663 | [6 empty] | 27.76 | 11.17 | 12.01
2012-03-06 | 6.74 | 6.28 |  |  |  |  | 7.23 | 1.28 |  |  |  |  | 35 |  |  |  | 0 | 0.774 |  |  | 0.094 | 0.193 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 26.3 |  | 7.2 | 0.102 |  | 3.1 | 54.77 | 0.73 |  |  |  |  | 13.735 | 12.376 | [6 empty] | 28.17 | 11.96 | 12.99
2012-03-07 | 5.95 | 6.48 |  |  |  |  | 6.77 | 1.33 |  |  |  |  | 44 |  |  |  | 0 | 0.756 |  |  | 0.164 | 0.33 | [5 empty] | 35.2 |  |  |  |  | 71.4 |  | 25.7 |  | 7.1 | 0.036 |  | 3 | 55.24 | 0.63 |  |  |  |  | 14.088 | 12.791 | [6 empty] | 30.27 | 12.1 | 11.71
2012-03-08 | 5.88 | 5.65 |  |  |  |  | 6.69 | 1.35 |  |  |  |  | 45 |  |  |  | 0 | 0.826 |  |  | 0.113 | 0.224 | [5 empty] | 36.5 |  |  |  |  | 73 |  | 23.9 |  | 6.8 | 0.043 |  | 3.1 | 54.77 | 0.6 |  |  |  |  | 13.576 | 12.759 | [6 empty] | 31.32 | 11.48 | 13.23
2012-03-09 | 6.68 | 6.06 |  |  |  |  | 6.91 | 1.43 |  |  |  |  | 44 |  |  |  | 0 | 0.885 |  |  | 0.101 | 0.237 | [5 empty] | 35.4 |  |  |  |  | 70.9 |  | 25.7 |  | 8.2 | 0.051 |  | 3.2 | 54.33 | 0.58 |  |  |  |  | 13.536 | 12.242 | [6 empty] | 25.35 | 13.05 | 14.97
2012-03-10 | 6.26 | 5.99 |  |  |  |  | 7.27 | 1.51 |  |  |  |  | 31 |  |  |  | 0 | 0.769 |  |  | 0.104 | 0.273 | [5 empty] | 37.3 |  |  |  |  | 74.7 |  | 25.2 |  | 12 | 0.011 |  | 3 | 60.13 | 0.63 |  |  |  |  | 13.6 | 12.76 | [6 empty] | 25.82 | 13.31 | 15.56
2012-03-11 | 6.47 | 5.855 |  |  |  |  | 7.09 | 1.49 |  |  |  |  | 37.5 |  |  |  | 0 | 0.827 |  |  | 0.1025 | 0.255 | [5 empty] | 36.35 |  |  |  |  | 72.8 |  | 25.45 |  | 10.1 | 0.031 |  | 3.1 | 60.15 | 0.6 |  |  |  |  | 13.41 | 13.06 | [6 empty] | 25.82 | 13.31 | 15.56
2012-03-12 | 5.66 | 5.94 |  |  |  |  | 7.11 | 1.43 |  |  |  |  | 39 |  |  |  | 0 | 0.837 |  |  | 0.15 | 0.302 | [5 empty] | 36.9 |  |  |  |  | 73.8 |  | 25.8 |  | 9.1 | 0.021 |  | 3.1 | 60.62 | 0.79 |  |  |  |  | 14.503 | 12.406 | [6 empty] | 32.66 | 14.69 | 13.74
2012-03-13 | 5.68 | 5.53 |  |  |  |  | 6.76 | 1.42 |  |  |  |  | 46 |  |  |  | 0 | 1.674 |  |  | 0.137 | 0.229 | [5 empty] | 37.3 |  |  |  |  | 74.6 |  | 25.2 |  | 9.8 | 0.086 |  | 3.2 | 59.84 | 0.99 |  |  |  |  | 13.468 | 11.28 | [6 empty] | 33.18 | 12.45 | 14.36
2012-03-14 | 6.99 | 5.81 |  |  |  |  | 7.04 | 1.36 |  |  |  |  | 40 |  |  |  | 0 | 1.495 |  |  | 0.121 | 0.197 | [5 empty] | 37.4 |  |  |  |  | 74.8 |  | 28.9 |  | 11.3 | 0.133 |  | 3.3 | 65.09 | 0.72 |  |  |  |  | 14.994 | 14.179 | [6 empty] | 26.76 | 12.91 | 17.35
2012-03-15 | 6.62 | 6.13 |  |  |  |  | 7.09 | 1.33 |  |  |  |  | 39 |  |  |  | 0 | 2.162 |  |  | 0.133 | 0.246 | [5 empty] | 37.3 |  |  |  |  | 74.8 |  | 26 |  | 11.6 | 0.103 |  | 3.3 | 60.19 | 0.95 |  |  |  |  | 13.677 | 11.982 | [6 empty] | 26.29 | 12.66 | 15.12
2012-03-16 | 6.58 | 6 |  |  |  |  | 7.36 | 1.18 |  |  |  |  | 43 |  |  |  | 0 | 0.867 |  |  | 0.177 | 0.486 | [5 empty] | 35.1 |  |  |  |  | 70.2 |  | 24.7 |  | 10.4 | 0.117 |  | 3.4 | 55.24 | 0.85 |  |  |  |  | 13.729 | 12.327 | [6 empty] | 30.73 | 12.36 | 13.85
2012-03-17 | 6.47 | 6.61 |  |  |  |  | 7.49 | 1.29 |  |  |  |  | 54 |  |  |  | 0 | 0.672 |  |  | 0.127 | 0.417 | [5 empty] | 38.1 |  |  |  |  | 76.2 |  | 25.3 |  | 7.8 | 0.142 |  | 3.6 | 60.09 | 0.92 |  |  |  |  | 14.08 | 12.36 | [6 empty] | 30.3 | 12.45 | 13.81
2012-03-18 | 6.525 | 6.065 |  |  |  |  | 7.425 | 1.235 |  |  |  |  | 48.5 |  |  |  | 0 | 0.7695 |  |  | 0.152 | 0.4515 | [5 empty] | 36.6 |  |  |  |  | 73.2 |  | 25 |  | 9.1 | 0.1295 |  | 3.5 | 57.665 | 0.885 |  |  |  |  | 13.703 | 12.1545 | [6 empty] | 30.515 | 12.405 | 13.83
2012-03-19 | 6.64 | 5.71 |  |  |  |  | 7.64 | 1.35 |  |  |  |  | 38 |  |  |  | 0 | 0.641 |  |  | 0.098 | 0.16 | [5 empty] | 37 |  |  |  |  | 74 |  | 34.2 |  | 11.8 | 0.097 |  | 3.7 | 56.51 | 0.72 |  |  |  |  | 13.647 | 12.388 | [6 empty] | 26.29 | 13.87 | 16.29
2012-03-20 | 6.19 | 6.22 |  |  |  |  | 5.92 | 1.34 |  |  |  |  | 37 |  |  |  | 0 | 0.67 |  |  | 0.157 | 0.066 | [5 empty] | 25.1 |  |  |  |  | 50.2 |  | 27.7 |  | 3.7 | 0.187 |  | 3.8 | 65.03 | 0.65 |  |  |  |  | 16.11 | 14.81 | [6 empty] | 26.76 | 13.01 | 15.06
2012-03-21 | 6.59 | 6.4 |  |  |  |  | 7.06 | 1.25 |  |  |  |  | 40 |  |  |  | 0 | 0.752 |  |  | 0.102 | 0.431 | [5 empty] | 26.9 |  |  |  |  | 53.8 |  | 27 |  | 8.2 | 0.12 |  | 3.8 | 60.15 | 0.94 |  |  |  |  | 13.822 | 12.486 | [6 empty] | 27.46 | 11.5 | 13.68
2012-03-22 | 6.59 | 5.8 |  |  |  |  | 5.61 | 1.26 |  |  |  |  | 41 |  |  |  | 0 | 0.812 |  |  | 0.152 | 0.122 | [5 empty] | 27.2 |  |  |  |  | 54.4 |  | 28.7 |  | 6.4 | 0.173 |  | 3.8 | 60.13 | 0.85 |  |  |  |  | 14.263 | 12.956 | [6 empty] | 30.55 | 12.255 | 14.37
2012-03-23 | 5.9 | 6.3 |  |  |  |  | 6.68 | 1.38 |  |  |  |  | 44 |  |  |  | 0 | 0.846 |  |  | 0.156 | 0.525 | [5 empty] | 29.4 |  |  |  |  | 58.8 |  | 27.5 |  | 5.9 | 0.01 |  | 4.1 | 59.65 | 0.75 |  |  |  |  | 13.936 | 12.705 | [6 empty] | 31.06 | 11.8775 | 16.32
2012-03-24 | 6.245 | 6.1 |  |  |  |  | 6.145 | 1.32 |  |  |  |  | 42.5 |  |  |  | 0 | 0.829 |  |  | 0.154 | 0.3235 | [5 empty] | 28.3 |  |  |  |  | 56.6 |  | 28.1 |  | 6.15 | 0.0915 |  | 3.95 | 59.89 | 0.8 |  |  |  |  | 14.0425 | 12.721 | [6 empty] | 30.805 | 12.0663 | 15.345
2012-03-25 | 6.0725 | 6.05 |  |  |  |  | 6.4125 | 1.31 |  |  |  |  | 43.25 |  |  |  | 0 | 0.8375 |  |  | 0.155 | 0.42425 | [5 empty] | 28.85 |  |  |  |  | 57.7 |  | 27.8 |  | 6.025 | 0.05075 |  | 4.025 | 55.24 | 0.8 |  |  |  |  | 13.346 | 11.885 | [6 empty] | 30.9325 | 11.9719 | 15.8325
2012-03-26 | 6.41 | 5.91 |  |  |  |  | 7 | 1.37 |  |  |  |  | 45 |  |  |  | 0 | 0.804 |  |  | 0.125 | 0.412 | [5 empty] | 32.4 |  |  |  |  | 64.8 |  | 25.3 |  | 6 | 0.107 |  | 4.1 | 65.03 | 0.98 |  |  |  |  | 14.804 | 12.565 | [6 empty] | 34.41 | 12.0191 | 14.38
2012-03-27 | 6.57 | 5.97 |  |  |  |  | 7.7 | 1.41 |  |  |  |  | 51 |  |  |  | 0 | 0.687 |  |  | 0.132 | 0.17 | [5 empty] | 28.7 |  |  |  |  | 57.4 |  | 23.6 |  | 7.7 | 0.094 |  | 4.3 | 60.15 | 0.93 |  |  |  |  | 13.928 | 11.667 | [6 empty] | 28.39 | 12.86 | 13.79
2012-03-28 | 6.49 | 6.07 |  |  |  |  | 7.63 | 1.4 |  |  |  |  | 43 |  |  |  | 0 | 0.697 |  |  | 0.119 | 0.154 | [5 empty] | 30.2 |  |  |  |  | 60.4 |  | 23.7 |  | 8.4 | 0.101 |  | 4.4 | 55.48 | 0.59 |  |  |  |  | 13.94 | 12.635 | [6 empty] | 30.18 | 12.15 | 13.95
2012-03-29 | 6.69 | 6.19 |  |  |  |  | 7.53 | 1.45 |  |  |  |  | 50 |  |  |  | 0 | 0.822 |  |  | 0.155 | 0.17 | [5 empty] | 39 |  |  |  |  | 78 |  | 26.8 |  | 8.2 | 0.019 |  | 4.2 | 60.13 | 0.62 |  |  |  |  | 14.447 | 13.164 | [6 empty] | 28.6 | 12.47 | 14.1
2012-03-30 | 6.59 | 6.16 |  |  |  |  | 7.67 | 1.44 |  |  |  |  | 28 |  |  |  | 0 | 0.846 |  |  | 0.183 | 0.179 | [5 empty] | 35.7 |  |  |  |  | 71.6 |  | 25.5 |  | 10.2 | 0.086 |  | 4.2 | 59.55 | 0.53 |  |  |  |  | 14.1 | 13.72 | [6 empty] | 26.76 | 47.48 | 12.19
2012-03-31 | 7.08 | 6.22 |  |  |  |  | 8 | 1.42 |  |  |  |  | 28 |  |  |  | 0 | 0.84 |  |  | 0.271 | 0.189 | [5 empty] | 39.2 |  |  |  |  | 78.6 |  | 29 |  | 13.6 | 0.043 |  | 4.2 | 60.64 | 0.83 |  |  |  |  | 13.541 | 12.25 | [6 empty] | 26.52 | 51.09 | 12.94
2012-04-01 | 6.835 | 6.175 |  |  |  |  | 7.835 | 1.43 |  |  |  |  | 28 |  |  |  | 0 | 0.843 |  |  | 0.227 | 0.184 | [5 empty] | 37.45 |  |  |  |  | 75.1 |  | 27.25 |  | 11.9 | 0.0645 |  | 4.2 | 60.095 | 0.68 |  |  |  |  | 14.2735 | 13.442 | [6 empty] | 26.64 | 49.285 | 12.565
2012-04-02 | 6.23 | 6.8 |  |  |  |  | 7.29 | 1.37 |  |  |  |  | 39 |  |  |  | 0 | 0.659 |  |  | 0.396 | 0.192 | [5 empty] | 41.4 |  |  |  |  | 82.4 |  | 25.1 |  | 12.7 | 0.034 |  | 4.1 | 60.13 | 0.71 |  |  |  |  | 14.889 | 13.147 | [6 empty] | 26.69 | 49.17 | 12.15
2012-04-03 | 6.5325 | 6.1975 |  |  |  |  | 7.5625 | 1.4 |  |  |  |  | 33.5 |  |  |  | 0 | 0.751 |  |  | 0.3115 | 0.188 | [5 empty] | 39.425 |  |  |  |  | 78.75 |  | 26.175 |  | 12.3 | 0.04925 |  | 4.15 | 60.1125 | 0.695 |  |  |  |  | 13.9072 | 12.846 | [6 empty] | 26.665 | 49.2275 | 12.3575
2012-04-04 | 6.73 | 6.45 |  |  |  |  | 7.55 | 1.38 |  |  |  |  | 37 |  |  |  | 0 | 0.568 |  |  | 0.209 | 0.174 | [5 empty] | 35.8 |  |  |  |  | 71.7 |  | 29.5 |  | 9.5 | 0.002 |  | 4.1 | 54.82 | 0.54 |  |  |  |  | 13.41 | 12.987 | [6 empty] | 25.82 | 47.12 | 1.92
2012-04-05 | 6.1 | 6.34 |  |  |  |  | 6.75 | 1.41 |  |  |  |  | 38 |  |  |  | 0 | 0.522 |  |  | 0.142 | 0.173 | [5 empty] | 29.7 |  |  |  |  | 59.4 |  | 27.3 |  | 8.4 | 0.008 |  | 4 | 60.15 | 0.85 |  |  |  |  | 13.569 | 12.109 | [6 empty] | 25.82 | 48.1737 | 12.38
2012-04-06 | 6.34 | 6.19 |  |  |  |  | 7.27 | 1.21 |  |  |  |  | 34 |  |  |  | 0 | 0.661 |  |  | 0.13 | 0.192 | [5 empty] | 29.9 |  |  |  |  | 59.8 |  | 25.5 |  | 7.6 | 0.011 |  | 4.1 | 55.72 | 0.82 |  |  |  |  | 13.925 | 12.486 | [6 empty] | 26.85 | 47.6469 | 14.32
2012-04-07 | 6.59 | 6.15 |  |  |  |  | 7.27 | 1.26 |  |  |  |  | 41 |  |  |  | 0 | 0.673 |  |  | 0.112 | 0.174 | [5 empty] | 31.7 |  |  |  |  | 63.4 |  | 27.1 |  | 7.4 | 0.091 |  | 4.1 | 55.26 | 0.7 |  |  |  |  | 14.27 | 12.83 | [6 empty] | 26.6 | 47.9103 | 11.91
2012-04-08 | 6.465 | 6.265 |  |  |  |  | 7.27 | 1.235 |  |  |  |  | 37.5 |  |  |  | 0 | 0.667 |  |  | 0.121 | 0.183 | [5 empty] | 30.8 |  |  |  |  | 61.6 |  | 26.3 |  | 7.5 | 0.051 |  | 4.1 | 55.49 | 0.76 |  |  |  |  | 13.747 | 12.2975 | [6 empty] | 26.725 | 47.7786 | 13.115
2012-04-09 | 6.18 | 6.28 |  |  |  |  | 7.27 | 1.13 |  |  |  |  | 39 |  |  |  | 0 | 0.531 |  |  | 0.379 | 0.219 | [5 empty] | 31.5 |  |  |  |  | 63 |  | 25.7 |  | 1 | 0.011 |  | 3.7 | 49.86 | 0.7 |  |  |  |  | 13.845 | 12.399 | [6 empty] | 23.47 | 47.8445 | 12.98
2012-04-10 | 6.31 | 6.19 |  |  |  |  | 6.57 | 0.41 |  |  |  |  | 43 |  |  |  | 0 | 0.579 |  |  | 0.156 | 0.397 | [5 empty] | 26.6 |  |  |  |  | 53.2 |  | 28.6 |  | 5.2 | 0.024 |  | 3.6 | 52.675 | 0.73 |  |  |  |  | 14.027 | 12.514 | [6 empty] | 25.35 | 47.8115 | 12.92
2012-04-11 | 6.27 | 5.53 |  |  |  |  | 5.61 | 0.91 |  |  |  |  | 54 |  |  |  | 0 | 0.681 |  |  | 0.149 | 0.956 | [5 empty] | 30.2 |  |  |  |  | 60.4 |  | 26.2 |  | 5.7 | 0.072 |  | 3.8 | 59.65 | 1.21 |  |  |  |  | 14.129 | 12.766 | [6 empty] | 36.9 | 47.828 | 13.36
2012-04-12 | 6.25 | 5.6 |  |  |  |  | 6.94 | 1.26 |  |  |  |  | 42 |  |  |  | 0 | 0.683 |  |  | 0.191 | 0.547 | [5 empty] | 33.3 |  |  |  |  | 66.6 |  | 28.1 |  | 6 | 0.107 |  | 3.9 | 59.54 | 0.87 |  |  |  |  | 14.109 | 12.695 | [6 empty] | 31.63 | 47.8198 | 13.52
2012-04-13 | 5.91 | 5.95 |  |  |  |  | 6.72 | 1.35 |  |  |  |  | 46 |  |  |  | 3 | 0.533 |  |  | 0.331 | 0.567 | [5 empty] | 31.2 |  |  |  |  | 62.4 |  | 26.3 |  | 6.4 | 0.009 |  | 3.4 | 59.67 | 0.8 |  |  |  |  | 13.969 | 12.603 | [6 empty] | 29.19 | 47.8239 | 11.36
2012-04-14 | 6.25 | 6.14 |  |  |  |  | 7.21 | 1.36 |  |  |  |  | 53 |  |  |  | 1 | 0.546 |  |  | 0.381 | 0.29 | [5 empty] | 29.8 |  |  |  |  | 59.6 |  | 25.5 |  | 6.9 | 0.011 |  | 3.4 | 60.55 | 0.79 |  |  |  |  | 14.172 | 12.772 | [6 empty] | 24.86 | 47.8218 | 12.32
2012-04-15 | 6.08 | 5.775 |  |  |  |  | 6.965 | 1.355 |  |  |  |  | 49.5 |  |  |  | 2 | 0.5395 |  |  | 0.356 | 0.4285 | [5 empty] | 30.5 |  |  |  |  | 61 |  | 25.9 |  | 6.65 | 0.01 |  | 3.4 | 60.11 | 0.795 |  |  |  |  | 14.039 | 12.649 | [6 empty] | 27.025 | 47.8228 | 11.84
2012-04-16 | 5.97 | 6.12 |  |  |  |  | 6.83 | 1.33 |  |  |  |  | 51 |  |  |  | 4 | 0.546 |  |  | 0.954 | 0.623 | [5 empty] | 26.5 |  |  |  |  | 53 |  | 23.7 |  | 7.7 | 0.094 |  | 3.2 | 60.15 | 0.81 |  |  |  |  | 15.027 | 12.773 | [6 empty] | 28.06 | 47.8223 | 11.822
2012-04-17 | 6.21 | 6.25 |  |  |  |  | 7 | 1.3425 |  |  |  |  | 47 |  |  |  | 0 | 0.512 |  |  | 0.302 | 0.39 | [5 empty] | 28.7 |  |  |  |  | 57.4 |  | 23.7 |  | 7.2 | 0.061 |  | 2.8 | 60.13 | 0.8025 |  |  |  |  | 14.1055 | 12.7105 | [6 empty] | 21.74 | 47.8226 | 11.23
2012-04-18 | 6.83 | 6.18 |  |  |  |  | 6.79 | 1.32 |  |  |  |  | 55 |  |  |  | 1 | 0.498 |  |  | 0.289 | 0.653 | [5 empty] | 33.4 |  |  |  |  | 66.8 |  | 23.7 |  | 7.6 | 0.001 |  | 2.9 | 54.84 | 0.71 |  |  |  |  | 13.57 | 12.28 | [6 empty] | 24.9 | 47.8225 | 11.526
2012-04-19 | 5.91 | 5.73 |  |  |  |  | 7.85 | 1.18 |  |  |  |  | 52 |  |  |  | 9 | 0.537 |  |  | 1.24 | 0.702 | [5 empty] | 27.5 |  |  |  |  | 55 |  | 23.7 |  | 6.8 | 0.148 |  | 3 | 65.03 | 1.19 |  |  |  |  | 14.85 | 14.39 | [6 empty] | 11.78 | 47.8225 | 11.21
2012-04-20 | 6 | 6.04 |  |  |  |  | 6.12 | 1.54 |  |  |  |  | 44 |  |  |  | 0 | 0.514 |  |  | 0.143 | 0.477 | [5 empty] | 29 |  |  |  |  | 58 |  | 23.7 |  | 7.2 | 0.02 |  | 3.3 | 68.36 | 0.58 |  |  |  |  | 15.01 | 14.65 | [6 empty] | 23.47 | 47.8225 | 14.61
2012-04-21 | 6.51 | 5.84 |  |  |  |  | 6.56 | 1.44 |  |  |  |  | 41 |  |  |  | 0 | 0.522 |  |  | 0.505 | 0.806 | [5 empty] | 28.7 |  |  |  |  | 57.4 |  | 23.7 |  | 7.6 | 0.022 |  | 3.4 | 60.21 | 0.79 |  |  |  |  | 13.6 | 12.25 | [6 empty] | 23.47 | 47.8225 | 11.88
2012-04-22 | 6.255 | 5.885 |  |  |  |  | 6.34 | 1.44 |  |  |  |  | 42.5 |  |  |  | 0 | 0.518 |  |  | 0.324 | 0.6415 | [5 empty] | 28.85 |  |  |  |  | 57.7 |  | 23.7 |  | 7.4 | 0.021 |  | 3.35 | 60.22 | 0.81 |  |  |  |  | 13.445 | 12.162 | [6 empty] | 23.47 | 47.8225 | 11.8
2012-04-23 | 5.92 | 5.13 |  |  |  |  | 6.93 | 1.46 |  |  |  |  | 44 |  |  |  | 3 | 0.45 |  |  | 1.39 | 0.738 | [5 empty] | 29.8 |  |  |  |  | 59.6 |  | 23.7 |  | 6.9 | 0.01 |  | 3.9 | 70.41 | 1.19 |  |  |  |  | 14.287 | 12.062 | [6 empty] | 28.16 | 47.8225 | 12.89
2012-04-24 | 5.7 | 5.82 |  |  |  |  | 6.5 | 1.67 |  |  |  |  | 39 |  |  |  | 0 | 0.522 |  |  | 0.107 | 0.196 | [5 empty] | 29.9 |  |  |  |  | 59.8 |  | 23.7 |  | 6.8 | 0.018 |  | 4.2 | 55.94 | 0.38 |  |  |  |  | 12.6 | 12.4 | [6 empty] | 38.13 | 47.8225 | 13.96
2012-04-25 | 5.9 | 5.51 |  |  |  |  | 6.25 | 1.66 |  |  |  |  | 39 |  |  |  | 0 | 0.444 |  |  | 1.03 | 0.481 | [5 empty] | 29.8 |  |  |  |  | 59.6 |  | 25.5 |  | 7.5 | 0.016 |  | 4.4 | 64.61 | 0.61 |  |  |  |  | 14.076 | 12.946 | [6 empty] | 24.65 | 47.8225 | 16.27
2012-04-26 | 6.53 | 5.59 |  |  |  |  | 6.92 | 1.74 |  |  |  |  | 35 |  |  |  | 0 | 0.456 |  |  | 0.506 | 0.214 | [5 empty] | 36.9 |  |  |  |  | 73.9 |  | 24.9 |  | 12.3 | 0.104 |  | 4.4 | 59.71 | 0.37 |  |  |  |  | 13.871 | 12.825 | [6 empty] | 25.11 | 49.51 | 15.94
2012-04-27 | 7.12 | 6.33 |  |  |  |  | 8.79 | 1.61 |  |  |  |  | 30 |  |  |  | 0 | 0.765 |  |  | 0.282 | 0.275 | [5 empty] | 39.4 |  |  |  |  | 78.8 |  | 26.2 |  | 10.9 | 0.091 |  | 4.9 | 69.5 | 0.65 |  |  |  |  | 14.991 | 13.934 | [6 empty] | 27.74 | 47.03 | 12.58
2012-04-28 | 6.74 | 6.2 |  |  |  |  | 7.64 | 1.59 |  |  |  |  | 35 |  |  |  | 0 | 0.862 |  |  | 0.392 | 0.295 | [5 empty] | 38.2 |  |  |  |  | 76.4 |  | 24.3 |  | 11.7 | 0.08 |  | 4.8 | 59.65 | 0.41 |  |  |  |  | 14.57 | 13.55 | [6 empty] | 27.88 | 38.93 | 12.66
2012-04-29 | 6.93 | 5.96 |  |  |  |  | 8.215 | 1.6 |  |  |  |  | 32.5 |  |  |  | 0 | 0.8135 |  |  | 0.337 | 0.285 | [5 empty] | 38.8 |  |  |  |  | 77.6 |  | 25.25 |  | 11.3 | 0.0855 |  | 4.85 | 64.575 | 0.53 |  |  |  |  | 14.431 | 13.3795 | [6 empty] | 27.81 | 42.98 | 12.62
2012-04-30 | 6.98 | 6.3 |  |  |  |  | 7.72 | 1.52 |  |  |  |  | 43 |  |  |  | 0 | 1.077 |  |  | 0.199 | 0.187 | [5 empty] | 27.7 |  |  |  |  | 55.4 |  | 28.8 |  | 7.8 | 0.181 |  | 5.6 | 65 | 0.62 |  |  |  |  | 16.75 | 13.789 | [6 empty] | 23.9 | 40.955 | 12.51
2012-05-01 | 6.38 | 6.01 |  |  |  |  | 7.99 | 1.48 |  |  |  |  | 47 |  |  |  | 0 | 1.138 |  |  | 0.101 | 0.191 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 25.6 |  | 7.4 | 0.164 |  | 5.7 | 64.09 | 0.57 |  |  |  |  | 15.504 | 14.211 | [6 empty] | 23.94 | 1.48 | 9.93
2012-05-02 | 6.3 | 6.54 |  |  |  |  | 7.32 | 1.48 |  |  |  |  | 43 |  |  |  | 0 | 1.079 |  |  | 0.094 | 0.417 | [5 empty] | 25.7 |  |  |  |  | 51.4 |  | 26.6 |  | 7.9 | 0.14 |  | 5.8 | 65.5 | 0.58 |  |  |  |  | 15.026 | 14.437 | [6 empty] | 27.03 |  | 6.65
2012-05-03 | 6.14 | 4.92 |  |  |  |  | 6.47 | 1.51 |  |  |  |  | 48 |  |  |  | 0 | 0.967 |  |  | 0.077 | 0.313 | [5 empty] | 25.7 |  |  |  |  | 51.5 |  | 23.7 |  | 7.7 | 0.157 |  | 5.7 | 69.92 | 0.53 |  |  |  |  | 16.593 | 15.548 | [6 empty] | 28.43 |  | 8.09
2012-05-04 | 5.97 | 5.63 |  |  |  |  | 8.24 | 1.48 |  |  |  |  | 42 |  |  |  | 1 | 0.826 |  |  | 0.116 | 0.154 | [5 empty] | 24.3 |  |  |  |  | 48.6 |  | 24.7 |  | 7.9 | 0.148 |  | 5.9 | 70.4 | 0.59 |  |  |  |  | 16.554 | 13.416 | [6 empty] | 28.51 |  | 7.12
2012-05-05 | 6.27 | 5.24 |  |  |  |  | 6.71 | 1.54 |  |  |  |  | 44 |  |  |  | 0 | 0.847 |  |  | 0.104 | 0.227 | [5 empty] | 28.9 |  |  |  |  | 57.8 |  | 25.3 |  | 6.7 | 0.132 |  | 6 | 70.38 | 0.8 |  |  |  |  | 14.759 | 13.647 | [6 empty] | 37.67 |  | 13.69
2012-05-06 | 6.12 | 5.275 |  |  |  |  | 7.475 | 1.51 |  |  |  |  | 43 |  |  |  | 0.5 | 0.8365 |  |  | 0.11 | 0.1905 | [5 empty] | 26.6 |  |  |  |  | 53.2 |  | 25 |  | 7.3 | 0.14 |  | 5.95 | 63.95 | 0.64 |  |  |  |  | 14.669 | 13.525 | [6 empty] | 33.09
2012-05-07 | 5.92 | 4.99 |  |  |  |  | 6.93 | 1.47 |  |  |  |  | 40 |  |  |  | 0 | 1.007 |  |  | 0.094 | 0.182 | [5 empty] | 30.9 |  |  |  |  | 61.8 |  | 26.7 |  | 6.2 | 0.173 |  | 7.1 | 65.03 | 0.67 |  |  |  |  | 14.89 | 13.812 | [6 empty] | 31.54 |  | 13.18
2012-05-08 | 6.09 | 5.12 |  |  |  |  | 7.4 | 1.48 |  |  |  |  | 50 |  |  |  | 0 | 1.019 |  |  | 0.073 | 0.181 | [5 empty] | 31.4 |  |  |  |  | 62.8 |  | 24.5 |  | 7.9 | 0.162 |  | 7.2 | 64.86 | 0.58 |  |  |  |  | 15.295 | 14.284 | [6 empty] | 34.1 |  | 12.41
2012-05-09 | 6.04 | 5.3 |  |  |  |  | 7.05 | 1.45 |  |  |  |  | 38 |  |  |  | 0 | 0.906 |  |  | 0.088 | 0.281 | [5 empty] | 29 |  |  |  |  | 58 |  | 23.8 |  | 7.5 | 0.18 |  | 6.8 | 64.69 | 0.67 |  |  |  |  | 15.016 | 13.827 | [6 empty] | 23.69 |  | 16.14
2012-05-10 | 6.13 | 5.24 |  |  |  |  | 6.54 | 1.46 |  |  |  |  | 39 |  |  |  | 0 | 0.674 |  |  | 0.096 | 0.184 | [5 empty] | 29 |  |  |  |  | 58 |  | 24.9 |  | 7.3 | 0.182 |  | 7.7 | 70.32 | 0.85 |  |  |  |  | 14.99 | 13.84 | [6 empty] | 30.75 |  | 14.57
2012-05-11 | 6.86 | 5.75 |  |  |  |  | 6.39 | 1.47 |  |  |  |  | 29 |  |  |  | 0 | 0.958 |  |  | 0.073 | 0.154 | [5 empty] | 29.6 |  |  |  |  | 59.4 |  | 25.6 |  | 7.8 | 0.141 |  | 7.6 | 65.36 | 0.63 |  |  |  |  | 15.097 | 14.106 | [6 empty] | 24.41 |  | 16.71
2012-05-12 | 6.98 | 6.22 |  |  |  |  | 7.08 | 1.41 |  |  |  |  | 35 |  |  |  | 0 | 0.923 |  |  | 0.114 | 0.356 | [5 empty] | 27.3 |  |  |  |  | 54.4 |  | 27.9 |  | 8.2 | 0.065 |  | 7.9 | 65.11 | 0.65 |  |  |  |  | 14.54 | 14.32 | [6 empty] | 23.47 |  | 11.59
2012-05-13 | 6.92 | 5.495 |  |  |  |  | 6.735 | 1.37 |  |  |  |  | 32 |  |  |  | 0 | 0.9405 |  |  | 0.0935 | 0.255 | [5 empty] | 28.45 |  |  |  |  | 56.9 |  | 26.75 |  | 8 | 0.103 |  | 7.75 | 61.01 | 0.72 |  |  |  |  | 14.206 | 13.203 | [6 empty] | 23.47 |  | 11.59
2012-05-14 | 6.19 | 5.74 |  |  |  |  | 7.07 | 1.43 |  |  |  |  | 36 |  |  |  | 0 | 0.883 |  |  | 0.108 | 0.263 | [5 empty] | 27.3 |  |  |  |  | 54.6 |  | 27.2 |  | 7.9 | 0.093 |  | 8.9 | 72.41 | 0.89 |  |  |  |  | 16.235 | 14.149 | [6 empty] | 27.83 |  | 12.8
2012-05-15 | 6.12 | 5.78 |  |  |  |  | 7.07 | 1.49 |  |  |  |  | 33 |  |  |  | 0 | 0.807 |  |  | 0.113 | 0.174 | [5 empty] | 27.6 |  |  |  |  | 55.2 |  | 25.6 |  | 8.1 | 0.103 |  | 9.1 | 71.2 | 0.69 |  |  |  |  | 15.03 | 14.84 | [6 empty] | 40.52 |  | 12.84
2012-05-16 | 6.8 | 5.84 |  |  |  |  | 6.52 | 1.66 |  |  |  |  | 34 |  |  |  | 0 | 0.776 |  |  | 0.096 | 0.152 | [5 empty] | 28.6 |  |  |  |  | 57.3 |  | 27.1 |  | 8.3 | 0.181 |  | 9.3 | 65.03 | 0.66 |  |  |  |  | 13.768 | 12.738 | [6 empty] | 23.94 |  | 15.79
2012-05-17 | 6.88 | 6.13 |  |  |  |  | 7.1 | 1.31 |  |  |  |  | 35 |  |  |  | 0 | 0.819 |  |  | 0.092 | 0.142 | [5 empty] | 29.2 |  |  |  |  | 58.5 |  | 26.1 |  | 8.1 | 0.121 |  | 9.8 | 70.03 | 0.82 |  |  |  |  | 16.041 | 14.897 | [6 empty] | 23.47 |  | 15.85
2012-05-18 | 6.74 | 5.91 |  |  |  |  | 7.73 | 1.24 |  |  |  |  | 30 |  |  |  | 0 | 1.107 |  |  | 0.081 | 0.128 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 24.3 |  | 8.9 | 0.13 |  | 9.9 | 69.92 | 1.08 |  |  |  |  | 14.857 | 13.695 | [6 empty] | 23.78 |  | 14.1
2012-05-19 | 6.79 | 5.98 |  |  |  |  | 7.37 | 1.23 |  |  |  |  | 46 |  |  |  | 0 | 1.107 |  |  | 0.079 | 0.138 | [5 empty] | 31.4 |  |  |  |  | 62.8 |  | 26.3 |  | 8.4 | 0.121 |  | 9.9 | 65.03 | 0.94 |  |  |  |  | 14.73 | 13.58 | [6 empty] | 26.13 |  | 14.8
2012-05-20 | 6.765 | 6.02 |  |  |  |  | 7.55 | 1.235 |  |  |  |  | 38 |  |  |  | 0 | 1.107 |  |  | 0.08 | 0.133 | [5 empty] | 30.9 |  |  |  |  | 61.8 |  | 25.3 |  | 8.65 | 0.1255 |  | 9.9 | 67.475 | 1.01 |  |  |  |  | 15.449 | 14.296 | [6 empty] | 24.955
2012-05-21 | 7.01 | 5.96 |  |  |  |  | 7.15 | 1.42 |  |  |  |  | 39 |  |  |  | 0 | 1.199 |  |  | 0.098 | 0.166 | [5 empty] | 27.2 |  |  |  |  | 54.5 |  | 25.6 |  | 7.4 | 0.183 |  | 9.6 | 75.28 | 0.89 |  |  |  |  | 16 | 14.804 | [6 empty] | 25.35 |  | 13.72
2012-05-22 | 6.13 | 6.03 |  |  |  |  | 7.66 | 1.54 |  |  |  |  | 38 |  |  |  | 0 | 1.171 |  |  | 0.118 | 0.163 | [5 empty] | 25.9 |  |  |  |  | 51.8 |  | 26.7 |  | 7.6 | 0.198 |  | 10.1 | 66.46 | 0.47 |  |  |  |  | 16.21 | 15.021 | [6 empty] | 23.47 |  | 12.41
2012-05-23 | 6.3 | 6.3 |  |  |  |  | 8.22 | 1.5 |  |  |  |  | 33 |  |  |  | 0 | 1.017 |  |  | 0.099 | 0.137 | [5 empty] | 24.9 |  |  |  |  | 49.8 |  | 26.7 |  | 7.9 | 0.174 |  | 11 | 66.67 | 0.61 |  |  |  |  | 15.542 | 14.347 | [6 empty] | 26.03 |  | 11.53
2012-05-24 | 6.97 | 6.16 |  |  |  |  | 7.49 | 1.47 |  |  |  |  | 49 |  |  |  | 0 | 1.009 |  |  | 0.257 | 0.132 | [5 empty] | 33.9 |  |  |  |  | 67.8 |  | 26.4 |  | 9.2 | 0.01 |  | 10.7 | 75.79 | 0.82 |  |  |  |  | 16.435 | 14.988 | [6 empty] | 49.94 |  | 10.106
2012-05-25 | 6.14 | 6.45 |  |  |  |  | 8.49 | 1.39 |  |  |  |  | 42 |  |  |  | 0 | 1.049 |  |  | 0.114 | 0.305 | [5 empty] | 26.5 |  |  |  |  | 53 |  | 26.4 |  | 7.9 | 0.134 |  | 10.8 | 75.28 | 0.82 |  |  |  |  | 16.455 | 15.489 | [6 empty] | 28.68 |  | 9.91
2012-05-26 | 6.21 | 5.53 |  |  |  |  | 7.9 | 1.64 |  |  |  |  | 44 |  |  |  | 0 | 1.558 |  |  | 0.106 | 0.134 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 25.1 |  | 7.3 | 0.098 |  | 11.9 | 79.71 | 0.67 |  |  |  |  | 17.14 | 15.698 | [6 empty] | 23.89 |  | 16.65
2012-05-27 | 6.175 | 6.305 |  |  |  |  | 8.195 | 1.66 |  |  |  |  | 43 |  |  |  | 0 | 1.3035 |  |  | 0.11 | 0.2195 | [5 empty] | 26.65 |  |  |  |  | 53.3 |  | 25.75 |  | 7.6 | 0.116 |  | 11.35 | 75.79 | 0.56 |  |  |  |  | 16.183 | 15.494 | [6 empty] | 26.285
2012-05-28 | 6.21 | 6.18 |  |  |  |  | 6.84 | 1.66 |  |  |  |  | 39 |  |  |  | 0 | 0.859 |  |  | 0.112 | 0 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 25.4 |  | 7.7 | 0.091 |  | 11.8 | 79.8 | 0.83 |  |  |  |  | 16.187 | 14.55 | [6 empty] | 24.88 |  | 14.36
2012-05-29 | 6.31 | 6.2 |  |  |  |  | 6.64 | 1.67 |  |  |  |  | 32 |  |  |  | 0 | 0.841 |  |  | 0.214 | 0.094 | [5 empty] | 29.1 |  |  |  |  | 58.2 |  | 26.8 |  | 7.2 | 0.124 |  | 11.4 | 70.41 | 0.44 |  |  |  |  | 15.843 | 15.13 | [6 empty] | 28.16 |  | 13.38
2012-05-30 | 6.08 | 5.95 |  |  |  |  | 7.1 | 1.7 |  |  |  |  | 32 |  |  |  | 0 | 0.786 |  |  | 0.084 | 0.167 | [5 empty] | 27.3 |  |  |  |  | 54.6 |  | 27.1 |  | 7 | 0.043 |  | 11.9 | 79.69 | 0.74 |  |  |  |  | 16.283 | 14.807 | [6 empty] | 30.44 |  | 12.39
2012-05-31 | 6.33 | 5.92 |  |  |  |  | 6.79 | 1.71 |  |  |  |  | 34 |  |  |  | 0 | 0.928 |  |  | 0.091 | 0.083 | [5 empty] | 27.8 |  |  |  |  | 55.6 |  | 26.1 |  | 7.1 | 0.058 |  | 11.4 | 69.92 | 0.38 |  |  |  |  | 15.89 | 15.17 | [6 empty] | 37.53 |  | 12.08
2012-06-01 | 7.05 | 6.05 |  |  |  |  | 7.3 | 1.68 |  |  |  |  | 32 |  |  |  | 0 | 0.868 |  |  | 0.237 | 0.079 | [5 empty] | 31.1 |  |  |  |  | 61.6 |  | 26.5 |  | 7.8 | 0.031 |  | 11.5 | 74.48 | 0.62 |  |  |  |  | 16.352 | 14.677 | [6 empty] | 27.7 |  | 14.43
2012-06-02 | 6.91 | 6.04 |  |  |  |  | 7.23 | 1.6 |  |  |  |  | 34 |  |  |  | 0 | 1.12 |  |  | 0.499 | 0.117 | [5 empty] | 28.8 |  |  |  |  | 57.6 |  | 28.8 |  | 7.8 | 0.0445 |  | 11.2 | 71.11 | 0.56 |  |  |  |  | 15.21 | 14.94 | [6 empty] | 26.29 |  | 15.01
2012-06-03 | 6.98 | 5.985 |  |  |  |  | 7.265 | 1.7 |  |  |  |  | 33 |  |  |  | 0 | 0.994 |  |  | 0.368 | 0.098 | [5 empty] | 29.95 |  |  |  |  | 59.6 |  | 27.65 |  | 7.8 | 0.03775 |  | 11.35 | 65.38 | 0.65 |  |  |  |  | 13.759 | 12.623 | [6 empty] | 26.99 |  | 15.01
2012-06-04 | 5.24 | 6.28 |  |  |  |  | 8.29 | 1.7 |  |  |  |  | 31 |  |  |  | 0 | 0.836 |  |  | 0.367 | 0.113 | [5 empty] | 28.7 |  |  |  |  | 57.4 |  | 27.5 |  | 7 | 0.09 |  | 10.6 | 85.07 | 0.63 |  |  |  |  | 18.48 | 16.59 | [6 empty] | 33.69 |  | 13.33
2012-06-05 | 6.27 | 5.82 |  |  |  |  | 7.59 | 1.62 |  |  |  |  | 27 |  |  |  | 0 | 0.916 |  |  | 0.097 | 0.091 | [5 empty] | 30 |  |  |  |  | 60 |  | 27.9 |  | 7.5 | 0.003 |  | 10.2 | 69.28 | 0.45 |  |  |  |  | 16.92 | 15.17 | [6 empty] | 37.22 |  | 14.62
2012-06-06 | 6.58 | 6.22 |  |  |  |  | 8.61 | 1.33 |  |  |  |  | 28 |  |  |  | 0 | 1.075 |  |  | 0.105 | 0.096 | [5 empty] | 28.1 |  |  |  |  | 57.9 |  | 28.7 |  | 7.8 | 0.112 |  | 9.9 | 65.03 | 0.6 |  |  |  |  | 16.504 | 15.259 | [6 empty] | 27.46 |  | 14.03
2012-06-07 | 6.78 | 6.04 |  |  |  |  | 8.37 | 1.37 |  |  |  |  | 29 |  |  |  | 0 | 0.816 |  |  | 0.238 | 0.209 | [5 empty] | 27.7 |  |  |  |  | 55.5 |  | 27.6 |  | 5.8 | 0.119 |  | 9.8 | 65.03 | 0.6 |  |  |  |  | 16.664 | 14.983 | [6 empty] | 26.76 |  | 12.13
2012-06-08 | 6.5 | 5.25 |  |  |  |  | 8.38 | 1.39 |  |  |  |  | 40 |  |  |  | 0 | 0.896 |  |  | 0.196 | 0.121 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 28.3 |  | 6.3 | 0.104 |  | 9.9 | 64.78 | 0.62 |  |  |  |  | 16.277 | 14.617 | [6 empty] | 76.16 |  | 14.61
2012-06-09 | 6.63 | 5.59 |  |  |  |  | 8.27 | 1.3 |  |  |  |  | 31 |  |  |  | 0 | 0.794 |  |  | 0.117 | 0.107 | [5 empty] | 26.1 |  |  |  |  | 52.2 |  | 26.1 |  | 7 | 0.119 |  | 10 | 81.12 | 1.22 |  |  |  |  | 15.78 | 14.63 | [6 empty] | 25.78 |  | 12.02
2012-06-10 | 6.565 | 5.645 |  |  |  |  | 8.325 | 1.345 |  |  |  |  | 35.5 |  |  |  | 0 | 0.845 |  |  | 0.1565 | 0.114 | [5 empty] | 27.65 |  |  |  |  | 55.3 |  | 27.2 |  | 6.65 | 0.1115 |  | 9.95 | 72.95 | 0.92 |  |  |  |  | 16.4705 | 14.8 | [6 empty] | 50.97
2012-06-11 | 6.88 | 6.75 |  |  |  |  | 7.01 | 1.5 |  |  |  |  | 32 |  |  |  | 0 | 0.531 |  |  | 0.121 | 0.079 | [5 empty] | 27.5 |  |  |  |  | 55 |  | 26.4 |  | 6.3 | 0.003 |  | 9.8 | 85.58 | 0.82 |  |  |  |  | 18.133 | 16.719 | [6 empty] | 30.98 |  | 12.9
2012-06-12 | 6.98 | 5.97 |  |  |  |  | 7.1 | 1.59 |  |  |  |  | 32 |  |  |  | 0 | 0.564 |  |  | 1.38 | 0.169 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 32.5 |  | 6.5 | 0.019 |  | 10.4 | 84.93 | 0.65 |  |  |  |  | 18.722 | 17.251 | [6 empty] | 27.23 |  | 14.07
2012-06-13 | 6.7 | 6.02 |  |  |  |  | 7.31 | 1.64 |  |  |  |  | 30 |  |  |  | 0 | 0.623 |  |  | 0.101 | 0.094 | [5 empty] | 29.6 |  |  |  |  | 59.2 |  | 29.1 |  | 7.1 | 0.047 |  | 10.4 | 84.74 | 0.64 |  |  |  |  | 18.966 | 16.906 | [6 empty] | 26.26 |  | 13.25
2012-06-14 | 6.69 | 6.11 |  |  |  |  | 7.32 | 1.59 |  |  |  |  | 34 |  |  |  | 0 | 0.561 |  |  | 0.1 | 0.097 | [5 empty] | 26.3 |  |  |  |  | 52.6 |  | 28.8 |  | 6.4 | 0.064 |  | 10.3 | 90.6 | 0.72 |  |  |  |  | 19.433 | 17.826 | [6 empty] | 25.55 |  | 15.05
2012-06-15 | 6.03 | 6.03 |  |  |  |  | 7.19 | 1.44 |  |  |  |  | 31 |  |  |  | 0 | 0.608 |  |  | 0.191 | 0.086 | [5 empty] | 25.9 |  |  |  |  | 51.8 |  | 27.4 |  | 6.1 | 0.053 |  | 12.3 | 70.41 | 0.68 |  |  |  |  | 16.968 | 15.052 | [6 empty] | 21.49 |  | 12.14
2012-06-16 | 6.36 | 6.065 |  |  |  |  | 7.255 | 1.42 |  |  |  |  | 32.5 |  |  |  | 0 | 0.5845 |  |  | 0.1455 | 0.0915 | [5 empty] | 26.1 |  |  |  |  | 52.2 |  | 28.1 |  | 6.25 | 0.0585 |  | 11.3 | 84.58 | 0.98 |  |  |  |  | 17.651 | 15.979 | [6 empty] | 23.52
2012-06-17 | 6.01 | 6.09 |  |  |  |  | 7.84 | 1.36 |  |  |  |  | 33 |  |  |  | 0 | 0.608 |  |  | 0.221 | 0.138 | [5 empty] | 30 |  |  |  |  | 60 |  | 26.9 |  |  | 0.062 |  | 12.5 | 76.16 | 1.02 |  |  |  |  | 15.804 | 14.532 | [6 empty] | 34.37 |  | 14.46
2012-06-18 | 6.65 | 6.18 |  |  |  |  | 7.57 | 1.39 |  |  |  |  | 27 |  |  |  | 2 | 0.559 |  |  | 1.05 | 0.266 | [5 empty] | 28.9 |  |  |  |  | 57.8 |  | 28.4 |  | 6.9 | 0.194 |  | 13.1 | 95.19 | 0.92 |  |  |  |  | 20.327 | 18.669 | [6 empty] | 28.36 |  | 13.67
2012-06-19 | 6.74 | 6.63 |  |  |  |  | 7.99 | 1.23 |  |  |  |  | 32 |  |  |  | 0 | 0.592 |  |  | 1.33 | 0.307 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 28.5 |  | 5.7 | 0.098 |  | 13.4 | 89.88 | 1.02 |  |  |  |  | 19.817 | 18.116 | [6 empty] | 27.72 |  | 14.26
2012-06-20 | 6.695 | 6.135 |  |  |  |  | 7.78 | 1.31 |  |  |  |  | 29.5 |  |  |  | 1 | 0.5755 |  |  | 1.19 | 0.2865 | [5 empty] | 29.05 |  |  |  |  | 58.1 |  | 28.45 |  | 6.3 | 0.146 |  | 13.25 | 92.535 | 0.97 |  |  |  |  | 18.0655 | 16.6005 | [6 empty] | 28.04
2012-06-21 | 6.53 | 5.72 |  |  |  |  | 7.54 | 1.42 |  |  |  |  | 21 |  |  |  | 0 | 0.557 |  |  | 0.235 | 0.144 | [5 empty] | 22.1 |  |  |  |  | 44.2 |  | 27.7 |  | 6.1 | 0.125 |  | 14.1 | 110.49 | 1.12 |  |  |  |  | 21.254 | 19.715 | [6 empty] | 21.26 |  | 9.58
2012-06-22 | 6.34 | 5.81 |  |  |  |  | 8.34 | 1.66 |  |  |  |  | 28 |  |  |  | 0 | 0.602 |  |  | 0.109 | 0.128 | [5 empty] | 29 |  |  |  |  | 57.3 |  | 27.4 |  | 6.4 | 0.107 |  | 14.5 | 120.26 | 0.77 |  |  |  |  | 22.389 | 22.417 | [6 empty] | 31.45 |  | 14.22
2012-06-23 | 6.17 | 5.72 |  |  |  |  | 7.86 | 1.8 |  |  |  |  | 31 |  |  |  | 0 | 0.515 |  |  | 0.084 | 0.111 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 26.5 |  | 6.8 | 0.116 |  | 15 | 104.74 | 0.54 |  |  |  |  | 21.62 | 20.33 | [6 empty] | 26.355 |  | 10.36
2012-06-24 | 6.255 | 5.765 |  |  |  |  | 8.1 | 1.92 |  |  |  |  | 29.5 |  |  |  | 0 | 0.5585 |  |  | 0.0965 | 0.1195 | [5 empty] | 28.7 |  |  |  |  | 57.05 |  | 26.95 |  | 6.6 | 0.1115 |  | 14.75 | 105.69 | 0.49 |  |  |  |  | 21.334 | 19.945 | [6 empty] | 28.9025 |  | 10.36
2012-06-25 | 5.9 | 5.47 |  |  |  |  | 7.93 | 1.64 |  |  |  |  | 32 |  |  |  | 0 | 0.547 |  |  | 0.125 | 0.112 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 25.2 |  | 7.1 | 0.162 |  | 15.5 | 94.46 | 0.44 |  |  |  |  | 21.898 | 20.595 | [6 empty] | 32 |  | 14.94
2012-06-26 | 6.19 | 6.03 |  |  |  |  | 7.91 | 1.35 |  |  |  |  | 24 |  |  |  | 0 | 0.688 |  |  | 0.54 | 0.141 | [5 empty] | 28.6 |  |  |  |  | 57.2 |  | 26.9 |  | 6.9 | 0.157 |  | 15.6 | 105.2 | 0.92 |  |  |  |  | 22.65 | 21.006 | [6 empty] | 24.93 |  | 14.33
2012-06-27 | 6.73 | 5.43 |  |  |  |  | 6.34 | 1.6 |  |  |  |  | 28 |  |  |  | 0 | 0.522 |  |  | 0.083 | 0.28 | [5 empty] | 32.8 |  |  |  |  | 65.6 |  | 23.2 |  | 3.1 | 0.024 |  | 15.6 | 74.97 | 0.59 |  |  |  |  | 18.025 | 15.49 | [6 empty] | 36.15 |  | 14.36
2012-06-28 | 6.8 | 5.87 |  |  |  |  | 8.01 | 1.55 |  |  |  |  | 25 |  |  |  | 0 | 0.537 |  |  | 0.082 | 0.109 | [5 empty] | 32.4 |  |  |  |  | 64.8 |  | 27 |  | 7.1 | 0.044 |  | 15.7 | 83.97 | 0.87 |  |  |  |  | 16.255 | 15.543 | [6 empty] | 31.08 |  | 14.39
2012-06-29 | 6.94 | 5.5 |  |  |  |  | 6.87 | 1.7 |  |  |  |  | 28 |  |  |  | 0 | 0.557 |  |  | 0.082 | 0.152 | [5 empty] | 30.8 |  |  |  |  | 61.6 |  | 25.2 |  | 6.8 | 0.031 |  | 15.6 | 70.5 | 0.59 |  |  |  |  | 16.007 | 13.989 | [6 empty] | 36.62 |  | 14.82
2012-06-30 | 6.82 | 5.98 |  |  |  |  | 8.78 | 1.62 |  |  |  |  | 27 |  |  |  | 0 | 0.697 |  |  | 0.091 | 0.101 | [5 empty] | 34.5 |  |  |  |  | 69 |  | 25.2 |  | 8.1 | 0.071 |  | 16 | 97.62 | 0.93 |  |  |  |  | 18.5 | 17.37 | [6 empty] | 30.35 |  | 14.19
2012-07-01 | 6.88 | 5.685 |  |  |  |  | 7.825 | 1.66 |  |  |  |  | 27.5 |  |  |  | 0 | 0.627 |  |  | 0.0865 | 0.1265 | [5 empty] | 32.65 |  |  |  |  | 65.3 |  | 25.2 |  | 7.45 | 0.051 |  | 15.8 | 84.06 | 0.76 |  |  |  |  | 16.131 | 14.766 | [6 empty] | 33.485
2012-07-02 | 6.59 | 6.14 |  |  |  |  | 8.87 | 1.88 |  |  |  |  | 26 |  |  |  | 0 | 0.585 |  |  | 0.08 | 0.083 | [5 empty] | 29.3 |  |  |  |  | 58.7 |  | 23.4 |  | 7.8 | 0.051 |  | 16.1 | 105.59 | 0.88 |  |  |  |  | 18.982 | 17.372 | [6 empty] | 31.92 |  | 13.47
2012-07-03 | 6.18 | 5.65 |  |  |  |  | 7.22 | 2 |  |  |  |  | 32 |  |  |  | 0 | 0.623 |  |  | 0.069 | 0.125 | [5 empty] | 30.4 |  |  |  |  | 60.4 |  | 27.5 |  | 7.1 | 0.105 |  | 16.5 | 90.54 | 0.37 |  |  |  |  | 17.957 | 17.239 | [6 empty] | 30.51 |  | 14.25
2012-07-04 | 6.77 | 5.65 |  |  |  |  | 8.02 | 1.86 |  |  |  |  | 27 |  |  |  | 0 | 0.679 |  |  | 0.071 | 0.086 | [5 empty] | 30.2 |  |  |  |  | 60.4 |  | 26.3 |  | 8.1 | 0.087 |  | 16.8 | 95.92 | 0.74 |  |  |  |  | 17.725 | 16.734 | [6 empty] | 31.45 |  | 15.16
2012-07-05 | 6.62 | 6.23 |  |  |  |  | 8.83 | 1.81 |  |  |  |  | 26 |  |  |  | 0 | 0.594 |  |  | 0.293 | 0.131 | [5 empty] | 35.1 |  |  |  |  | 70.3 |  | 22 |  | 8.3 | 0.131 |  | 17.4 | 105.13 | 0.77 |  |  |  |  | 19.555 | 18.482 | [6 empty] | 29.1 |  | 17.1
2012-07-06 | 5.98 | 5.75 |  |  |  |  | 8.46 | 1.8 |  |  |  |  | 32 |  |  |  | 0 | 0.62 |  |  | 0.084 | 0.095 | [5 empty] | 28.7 |  |  |  |  | 57.4 |  | 22.7 |  | 8.6 | 0.086 |  | 17.6 | 104.6 | 0.86 |  |  |  |  | 18.912 | 17.862 | [6 empty] | 29.53 |  | 14.43
2012-07-07 | 6.12 | 5.36 |  |  |  |  | 8 | 1.84 |  |  |  |  | 29 |  |  |  | 0 | 0.607 |  |  | 0.08 | 0.091 | [5 empty] | 29.1 |  |  |  |  | 58.2 |  | 23.6 |  | 7.1 | 0.06 |  | 17.7 | 75.46 | 0.67 |  |  |  |  | 14.75 | 13.67 | [6 empty] | 34.03 |  | 11.26
2012-07-08 | 6.05 | 5.99 |  |  |  |  | 8.23 | 1.82 |  |  |  |  | 30.5 |  |  |  | 0 | 0.6135 |  |  | 0.082 | 0.093 | [5 empty] | 28.9 |  |  |  |  | 57.8 |  | 23.15 |  | 7.85 | 0.073 |  | 17.65 | 90.03 | 0.765 |  |  |  |  | 19.2335 | 18.172 | [6 empty] | 31.78
2012-07-09 | 6.98 | 5.8 |  |  |  |  | 7.57 | 1.86 |  |  |  |  | 27 |  |  |  | 0 | 0.556 |  |  | 0.076 | 0.086 | [5 empty] | 29.9 |  |  |  |  | 59.9 |  | 22.9 |  | 7.4 | 0.078 |  | 17.7 | 85.55 | 0.82 |  |  |  |  | 15.484 | 14.48 | [6 empty] | 26.29 |  | 15.28
2012-07-10 | 7.03 | 5.98 |  |  |  |  | 7.52 | 1.82 |  |  |  |  | 26 |  |  |  | 0 | 0.735 |  |  | 0.075 | 0.07 | [5 empty] | 28.6 |  |  |  |  | 57.2 |  | 24.2 |  | 7.9 | 0.062 |  | 17.6 | 90.12 | 0.84 |  |  |  |  | 16.515 | 15.41 | [6 empty] | 29.11 |  | 12.1
2012-07-11 | 6.78 | 6.78 |  |  |  |  | 7.84 | 1.54 |  |  |  |  | 31 |  |  |  | 0 | 0.71 |  |  | 0.079 | 0.082 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 24.7 |  | 7.7 | 0.055 |  | 17.4 | 87.835 | 1.28 |  |  |  |  | 17.605 | 16.075 | [6 empty] | 29.22 |  | 11.56
2012-07-12 | 6.26 | 5.82 |  |  |  |  | 7.74 | 1.6 |  |  |  |  | 32 |  |  |  | 0 | 0.663 |  |  | 0.08 | 0.082 | [5 empty] | 25.5 |  |  |  |  | 51 |  | 25.8 |  | 7.9 | 0.036 |  | 17.2 | 105 | 1.29 |  |  |  |  | 19.349 | 16.474 | [6 empty] | 33.99 |  | 11.15
2012-07-13 | 6.98 | 5.82 |  |  |  |  | 7.55 | 1.95 |  |  |  |  | 27 |  |  |  | 0 | 0.903 |  |  | 0.081 | 0.097 | [5 empty] | 28.9 |  |  |  |  | 57.8 |  | 24.8 |  | 8.3 | 0.062 |  | 17.2 | 100 | 0.71 |  |  |  |  | 18.338 | 17.046 | [6 empty] | 28.17 |  | 13.56
2012-07-14 | 7.02 | 5.94 |  |  |  |  | 7.55 | 2 |  |  |  |  | 26 |  |  |  | 0 | 0.716 |  |  | 0.086 | 0.072 | [5 empty] | 28.8 |  |  |  |  | 57.7 |  | 25.7 |  | 8.4 | 0.059 |  | 17.4 | 102.5 | 1 |  |  |  |  | 18.05 | 16.85 | [6 empty] | 29.1 |  | 16.35
2012-07-15 | 7 | 5.82 |  |  |  |  | 7.55 | 1.93 |  |  |  |  | 26.5 |  |  |  | 0 | 0.8095 |  |  | 0.0835 | 0.0845 | [5 empty] | 28.85 |  |  |  |  | 57.75 |  | 25.25 |  | 8.35 | 0.0605 |  | 17.3 | 101.25 | 0.855 |  |  |  |  | 16.996 | 15.809 | [6 empty] | 29.11 |  | 16.35
2012-07-16 | 6.5 | 5.99 |  |  |  |  | 7.62 | 1.93 |  |  |  |  | 27 |  |  |  | 0 | 0.796 |  |  | 0.084 | 0.072 | [5 empty] | 27.8 |  |  |  |  | 55.6 |  | 25.4 |  | 8.1 | 0.04 |  | 17.5 | 95 | 1.06 |  |  |  |  | 16.406 | 14.436 | [6 empty] | 29.66 |  | 13.18
2012-07-17 | 6.58 | 6.18 |  |  |  |  | 7.09 | 1.81 |  |  |  |  | 25 |  |  |  | 0 | 0.784 |  |  | 0.078 | 0.062 | [5 empty] | 24.7 |  |  |  |  | 49.4 |  | 26.5 |  | 7.9 | 0.025 |  | 17.4 | 80 | 0.84 |  |  |  |  | 14.43 | 13.726 | [6 empty] | 28.07 |  | 8.92
2012-07-18 | 6.91 | 5.76 |  |  |  |  | 6.97 | 1.77 |  |  |  |  | 25 |  |  |  | 0 | 1.011 |  |  | 0.339 | 0.067 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 24.3 |  | 8.6 | 0.037 |  | 17.2 | 80 | 0.93 |  |  |  |  | 14.52 | 13.457 | [6 empty] | 28.17 |  | 12.66
2012-07-19 | 6.94 | 6.37 |  |  |  |  | 7.13 | 1.57 |  |  |  |  | 25 |  |  |  | 0 | 0.544 |  |  | 0.086 | 0.098 | [5 empty] | 27 |  |  |  |  | 54 |  | 26.1 |  | 7.7 | 0.022 |  | 17.1 | 80 | 0.885 |  |  |  |  | 15.01 | 13.904 | [6 empty] | 26.29 |  | 12
2012-07-20 | 6.71 | 5.71 |  |  |  |  | 7.45 | 1.36 |  |  |  |  | 20 |  |  |  | 0 | 0.293 |  |  | 0.074 | 0.067 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 26.3 |  | 7.9 | 0.031 |  | 17 | 80 | 0.9075 |  |  |  |  | 14.346 | 13.195 | [6 empty] | 28.07 |  | 15.13
2012-07-21 | 7.23 | 5.43 |  |  |  |  | 6.73 | 1.56 |  |  |  |  | 31 |  |  |  | 0 | 0.555 |  |  | 0.078 | 0.164 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 25.5 |  | 7.3 | 0.018 |  | 17.1 | 74.97 | 1 |  |  |  |  | 14.42 | 13.29 | [6 empty] | 35.3 |  | 12.96
2012-07-22 | 6.97 | 6.04 |  |  |  |  | 7.09 | 1.46 |  |  |  |  | 25.5 |  |  |  | 0 | 0.424 |  |  | 0.076 | 0.1155 | [5 empty] | 27.1 |  |  |  |  | 54.2 |  | 25.9 |  | 7.6 | 0.0245 |  | 17.05 | 77.485 | 0.95375 |  |  |  |  | 14.678 | 13.5495 | [6 empty] | 31.685
2012-07-23 | 6.56 | 5.58 |  |  |  |  | 7.3 | 1.99 |  |  |  |  | 21 |  |  |  | 0 | 0.307 |  |  | 0.075 | 0.073 | [5 empty] | 30.9 |  |  |  |  | 61.8 |  | 25.8 |  | 7.2 | 0.066 |  | 17.5 | 90.44 | 0.68 |  |  |  |  | 16.408 | 15.375 | [6 empty] | 31.92 |  | 14.94
2012-07-24 | 6.2 | 5.97 |  |  |  |  | 7.76 | 0.453 |  |  |  |  | 26 |  |  |  | 0 | 0.453 |  |  | 0.075 | 0.092 | [5 empty] | 30.5 |  |  |  |  | 61 |  | 22.4 |  | 7.3 | 0.06 |  | 17.7 | 79.69 | 1.11 |  |  |  |  | 17.5 | 16.336 | [6 empty] | 31.92 |  | 14.63
2012-07-25 | 6.89 | 5.98 |  |  |  |  | 8.31 | [5 empty] | 22 |  |  |  | 0 | 0.426 |  |  | 0.082 | 0.11 | [5 empty] | 31.1 |  |  |  |  | 62.3 |  | 23.3 |  | 8.4 | 0.113 |  | 17.9 | 76.6 | 0.895 |  |  |  |  | 14.851 | 13.622 | [6 empty] | 31.92 |  | 16.84
2012-07-26 | 6.4 | 6.52 |  |  |  |  | 7.18 | 2.09 |  |  |  |  | 24 |  |  |  | 0 | 0.372 |  |  | 0.088 | 0.089 | [5 empty] | 28.6 |  |  |  |  | 57.4 |  | 22.9 |  | 8.9 | 0.143 |  | 17.8 | 61.28 | 0.05 |  |  |  |  | 14.779 | 13.079 | [6 empty] | 31.45 |  | 13.89
2012-07-27 | 6.65 | 5.76 |  |  |  |  | 8.14 | 2.11 |  |  |  |  | 22 |  |  |  | 0 | 0.526 |  |  | 0.081 | 0.077 | [5 empty] | 28.8 |  |  |  |  | 57.6 |  | 24.2 |  | 8.6 | 0.1 |  | 17.8 | 86.61 | 0.65 |  |  |  |  | 15.445 | 14.265 | [6 empty] | 32.25 |  | 12.08
2012-07-28 | 6.38 | 5.56 |  |  |  |  | 7.57 | 2.06 |  |  |  |  | 24 |  |  |  | 0 | 0.563 |  |  | 0.086 | 0.087 | [5 empty] | 28.8 |  |  |  |  | 57.6 |  | 23.5 |  | 8.1 | 0.057 |  | 17.9 | 83.24 | 0.67 |  |  |  |  | 14.939 | 13.821 | [6 empty] | 31.52 |  | 7.75
2012-07-29 | 6.515 | 6.14 |  |  |  |  | 7.855 | 2.2 |  |  |  |  | 23 |  |  |  | 0 | 0.5445 |  |  | 0.0835 | 0.082 | [5 empty] | 28.8 |  |  |  |  | 57.6 |  | 23.85 |  | 8.35 | 0.0785 |  | 17.85 | 84.925 | 0.66 |  |  |  |  | 14.86 | 14.148 | [6 empty] | 31.885
2012-07-30 | 6.49 | 5.83 |  |  |  |  | 7.53 | 1.71 |  |  |  |  | 21 |  |  |  | 0 | 0.574 |  |  | 0.059 | 0.091 | [5 empty] | 27.9 |  |  |  |  | 55.8 |  | 22.6 |  | 8 | 0.061 |  | 17.8 | 84.69 | 1.02 |  |  |  |  | 16.156 | 14.04 | [6 empty] | 31.17 |  | 8.64
2012-07-31 | 6.53 | 5.87 |  |  |  |  | 7.78 | 2.08 |  |  |  |  | 18 |  |  |  | 0 | 0.424 |  |  | 0.042 | 0.062 | [5 empty] | 28.3 |  |  |  |  | 56.6 |  | 25.2 |  | 7.7 | 0.077 |  | 17.5 | 89.63 | 0.75 |  |  |  |  | 15.553 | 14.38 | [6 empty] | 31.89 |  | 10.44
2012-08-01 | 6.45 | 5.89 |  |  |  |  | 7.5 | 2.47 |  |  |  |  | 21 |  |  |  | 0 | 0.457 |  |  | 0.076 | 0.078 | [5 empty] | 26.2 |  |  |  |  | 52.4 |  | 24.8 |  | 7.9 | 0.082 |  | 18.5 | 94.68 | 0.3 |  |  |  |  | 16.769 | 15.515 | [6 empty] | 27.61 |  | 11.18
2012-08-02 | 6.49 | 5.77 |  |  |  |  | 6.32 | 2.13 |  |  |  |  | 21 |  |  |  | 0 | 0.429 |  |  | 0.126 | 0.231 | [5 empty] | 23.8 |  |  |  |  | 47.6 |  | 25.6 |  | 6.3 | 0.02 |  | 18.8 | 85.55 | 0.54 |  |  |  |  | 16.217 | 14.559 | [6 empty] | 29.46 |  | 10.71
2012-08-03 | 6.91 | 5.91 |  |  |  |  | 8.09 | 1.62 |  |  |  |  | 25 |  |  |  | 0 | 0.372 |  |  | 0.076 | 0.09 | [5 empty] | 29.5 |  |  |  |  | 59.1 |  | 24.6 |  | 6.7 | 0.044 |  | 18.7 | 84.43 | 0.84 |  |  |  |  | 15.846 | 15.59 | [6 empty] | 30.04 |  | 13.62
2012-08-04 | 6.77 | 5.95 |  |  |  |  | 8.4 | 2.06 |  |  |  |  | 24 |  |  |  | 0 | 0.382 |  |  | 0.115 | 0.087 | [5 empty] | 29.4 |  |  |  |  | 58.8 |  | 26.9 |  | 7.1 | 0.038 |  | 19 | 90.14 | 0.71 |  |  |  |  | 16.28 | 14.78 | [6 empty] | 29.11 |  | 13.94
2012-08-05 | 6.84 | 5.84 |  |  |  |  | 8.245 | 2.44 |  |  |  |  | 24.5 |  |  |  | 0 | 0.377 |  |  | 0.0955 | 0.0885 | [5 empty] | 29.45 |  |  |  |  | 58.95 |  | 25.75 |  | 6.9 | 0.041 |  | 18.85 | 89.96 | 0.22 |  |  |  |  | 16.139 | 15.346 | [6 empty] | 29.11 |  | 13.94
2012-08-06 | 6.16 | 5.99 |  |  |  |  | 7.94 | 1.88 |  |  |  |  | 33 |  |  |  | 1 | 0.34 |  |  | 0.096 | 0.079 | [5 empty] | 27.8 |  |  |  |  | 55.6 |  | 25.9 |  | 7.4 | 0.048 |  | 19.2 | 84.76 | 0.65 |  |  |  |  | 17.31 | 15.181 | [6 empty] | 27.84 |  | 12.25
2012-08-07 | 6.36 | 5.81 |  |  |  |  | 7.86 | 2.19 |  |  |  |  | 19 |  |  |  | 0 | 0.547 |  |  | 0.072 | 0.101 | [5 empty] | 27.8 |  |  |  |  | 55.6 |  | 26.4 |  | 7.2 | 0.071 |  | 19.1 | 95.15 | 0.51 |  |  |  |  | 17.5 | 15.98 | [6 empty] | 26.99 |  | 13.22
2012-08-08 | 7 | 5.86 |  |  |  |  | 7.32 | 1.99 |  |  |  |  | 19 |  |  |  | 0 | 0.515 |  |  | 0.081 | 0.074 | [5 empty] | 28.6 |  |  |  |  | 57.2 |  | 26.8 |  | 8.5 | 0.002 |  | 19.2 | 90.38 | 0.55 |  |  |  |  | 17.281 | 16.128 | [6 empty] | 29.1 |  | 13.03
2012-08-09 | 6.93 | 5.84 |  |  |  |  | 7.44 | 1.82 |  |  |  |  | 17 |  |  |  | 0 | 0.349 |  |  | 0.076 | 0.6069 | [5 empty] | 29 |  |  |  |  | 57.8 |  | 25.9 |  | 8.4 | 0.017 |  | 19.6 | 84.78 | 0.93 |  |  |  |  | 15.232 | 14.02 | [6 empty] | 26.29 |  | 11.09
2012-08-10 | 6.74 | 5.75 |  |  |  |  | 7.45 | 1.79 |  |  |  |  | 14 |  |  |  | 0 | 0.268 |  |  | 0.062 | 0.077 | [5 empty] | 30.6 |  |  |  |  | 61.2 |  | 26.3 |  | 8.1 | 0.024 |  | 19.7 | 73.31 | 0.22 |  |  |  |  | 17.819 | 16.582 | [6 empty] | 25.73 |  | 11.69
2012-08-11 | 6.49 | 5.77 |  |  |  |  | 7.37 | 2.06 |  |  |  |  | 18 |  |  |  | 0 | 0.274 |  |  | 0.082 | 0.071 | [5 empty] | 31.1 |  |  |  |  | 62.2 |  | 24.7 |  | 7.4 | 0.047 |  | 19.4 | 89.45 | 0.79 |  |  |  |  | 15.89 | 14.24 | [6 empty] | 26.13 |  | 11.57
2012-08-12 | 6.615 | 5.795 |  |  |  |  | 7.41 | 1.925 |  |  |  |  | 16 |  |  |  | 0 | 0.271 |  |  | 0.072 | 0.074 | [5 empty] | 30.85 |  |  |  |  | 61.7 |  | 25.5 |  | 7.75 | 0.0355 |  | 19.55 | 81.38 | 0.505 |  |  |  |  | 16.5255 | 15.301 | [6 empty] | 25.93
2012-08-13 | 6.48 | 5.78 |  |  |  |  | 6.96 | 1.58 |  |  |  |  | 19 |  |  |  | 0 | 0.42 |  |  | 0.073 | 0.073 | [5 empty] | 27.8 |  |  |  |  | 55.7 |  | 25.8 |  | 7.9 | 0.037 |  | 19.5 | 77.77 | 0.94 |  |  |  |  | 15.861 | 14.02 | [6 empty] | 28.17 |  | 12.28
2012-08-14 | 6.79 | 5.74 |  |  |  |  | 8.12 | 2.22 |  |  |  |  | 21 |  |  |  | 0 | 0.091 |  |  | 0.078 | 0.095 | [5 empty] | 29.4 |  |  |  |  | 59 |  | 24 |  | 8.5 | 0.054 |  | 19.4 | 80.37 | 0.52 |  |  |  |  | 15.152 | 13.299 | [6 empty] | 27.23 |  | 13.53
2012-08-15 | 6.83 | 6.05 |  |  |  |  | 8.29 | 1.98 |  |  |  |  | 24 |  |  |  | 0 | 0.098 |  |  | 0.091 | 0.102 | [5 empty] | 30.6 |  |  |  |  | 61.2 |  | 24.3 |  | 8 | 0.064 |  | 19 | 75.15 | 0.76 |  |  |  |  | 14.796 | 12.434 | [6 empty] | 27.28 |  | 13.3
2012-08-16 | 6.67 | 5.89 |  |  |  |  | 7.59 | 1.86 |  |  |  |  | 21 |  |  |  | 0 | 0.037 |  |  | 0.06 | 0.073 | [5 empty] | 31.2 |  |  |  |  | 62.4 |  | 23.7 |  | 7.7 | 0.071 |  | 19.2 | 75.19 | 0.74 |  |  |  |  | 14.341 | 13.114 | [6 empty] | 28.3 |  | 12.71
2012-08-17 | 6.36 | 5.91 |  |  |  |  | 7.21 | 1.75 |  |  |  |  | 22 |  |  |  | 0 | 0.036 |  |  | 0.093 | 0.087 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 24.6 |  | 7.6 | 0.068 |  | 18.8 | 75.15 | 0.8 |  |  |  |  | 14.638 | 13.389 | [6 empty] | 27.33 |  | 9.83
2012-08-18 | 6.26 | 5.72 |  |  |  |  | 6.8 | 1.61 |  |  |  |  | 24 |  |  |  | 0 | 0.033 |  |  | 0.143 | 0.091 | [5 empty] | 30.1 |  |  |  |  | 60.2 |  | 25.7 |  | 6.8 | 0.081 |  | 18.5 | 73.51 | 1.05 |  |  |  |  | 13.804 | 12.543 | [6 empty] | 33.48 |  | 12.55
2012-08-19 | 6.31 | 5.9 |  |  |  |  | 7.005 | 1.58 |  |  |  |  | 23 |  |  |  | 0 | 0.0345 |  |  | 0.118 | 0.089 | [5 empty] | 29.15 |  |  |  |  | 58.3 |  | 25.15 |  | 7.2 | 0.0745 |  | 18.65 | 70.41 | 0.96 |  |  |  |  | 13.351 | 12.581 | [6 empty] | 30.405
2012-08-20 | 6.34 | 5.75 |  |  |  |  | 6.99 | 1.75 |  |  |  |  | 21 |  |  |  | 0 | 0.021 |  |  | 0.101 | 0.097 | [5 empty] | 30.8 |  |  |  |  | 61.6 |  | 26.1 |  | 6.4 | 0.071 |  | 18.6 | 80.2 | 0.99 |  |  |  |  | 15.014 | 13.29 | [6 empty] | 31.34 |  | 12.7
2012-08-21 | 6.24 | 5.77 |  |  |  |  | 7.42 | 1.84 |  |  |  |  | 33 |  |  |  | 0 | 0.147 |  |  | 0.093 | 0.084 | [5 empty] | 31.1 |  |  |  |  | 62.2 |  | 23.2 |  | 7.4 | 0.101 |  | 18.3 | 85.31 | 1.09 |  |  |  |  | 14.517 | 13.234 | [6 empty] | 31.34 |  | 12.7
2012-08-22 | 6.29 | 5.77 |  |  |  |  | 7.93 | 1.86 |  |  |  |  | 23 |  |  |  | 0 | 0.021 |  |  | 0.082 | 0.093 | [5 empty] | 31.3 |  |  |  |  | 62.6 |  | 24.5 |  | 7.1 | 0.087 |  | 18.6 | 85.07 | 1.02 |  |  |  |  | 15.149 | 13.427 | [6 empty] | 31.27 |  | 16.92
2012-08-23 | 5.89 | 5.88 |  |  |  |  | 8.24 | 1.79 |  |  |  |  | 24 |  |  |  | 0 | 0.02 |  |  | 0.076 | 0.097 | [5 empty] | 31 |  |  |  |  | 62 |  | 23.5 |  | 7.9 | 0.055 |  | 18.9 | 85.07 | 1.08 |  |  |  |  | 14.79 | 13.46 | [6 empty] | 31.66 |  | 12.43
2012-08-24 | 6.89 | 5.92 |  |  |  |  | 7.22 | 1.98 |  |  |  |  | 31 |  |  |  | 0 | 0.048 |  |  | 0.079 | 0.081 | [5 empty] | 30.8 |  |  |  |  | 61.6 |  | 25.4 |  | 8.8 | 0.105 |  | 18.8 | 80.19 | 0.8 |  |  |  |  | 14.375 | 13.12 | [6 empty] | 30.28 |  | 12.03
2012-08-25 | 6.14 | 5.91 |  |  |  |  | 7.18 | 2.02 |  |  |  |  | 30 |  |  |  | 0 | 0.051 |  |  | 0.084 | 0.083 | [5 empty] | 30.7 |  |  |  |  | 61.5 |  | 26.7 |  | 8.5 | 0.08 |  | 18.5 | 79.2 | 0.78 |  |  |  |  | 14.01 | 12.82 | [6 empty] | 28.17 |  | 13.63
2012-08-26 | 6.515 | 5.9 |  |  |  |  | 7.2 | 2.03 |  |  |  |  | 30.5 |  |  |  | 0 | 0.0495 |  |  | 0.0815 | 0.082 | [5 empty] | 30.75 |  |  |  |  | 61.55 |  | 26.05 |  | 8.65 | 0.0925 |  | 18.65 | 75.43 | 0.73 |  |  |  |  | 13.747 | 12.455 | [6 empty] | 28.17 |  | 13.63
2012-08-27 | 6 | 5.93 |  |  |  |  | 7.19 | 2.07 |  |  |  |  | 30 |  |  |  | 0 | 0.038 |  |  | 0.078 | 0.076 | [5 empty] | 26.5 |  |  |  |  | 53 |  | 25.9 |  | 8.3 | 0.08 |  | 18 | 89.37 | 0.9 |  |  |  |  | 15.96 | 13.655 | [6 empty] | 31.87 |  | 14.67
2012-08-28 | 6.19 | 5.81 |  |  |  |  | 7.39 | 2.03 |  |  |  |  | 28 |  |  |  | 0 | 0.038 |  |  | 0.086 | 0.089 | [5 empty] | 29 |  |  |  |  | 58 |  | 26.7 |  | 7.7 | 0.063 |  | 19.3 | 74.79 | 0.82 |  |  |  |  | 14.97 | 11.91 | [6 empty] | 30.94 |  | 12.92
2012-08-29 | 7.07 | 5.77 |  |  |  |  | 7.62 | 2.09 |  |  |  |  | 27 |  |  |  | 0 | 0.709 |  |  | 0.07 | 0.086 | [5 empty] | 27.2 |  |  |  |  | 54.4 |  | 21.8 |  | 8.5 | 0.104 |  | 18.8 | 80.5 | 0.67 |  |  |  |  | 16.261 | 13.227 | [6 empty] | 28.64 |  | 15.06
2012-08-30 | 6.12 | 5.77 |  |  |  |  | 7.09 | 1.93 |  |  |  |  | 26 |  |  |  | 0 | 0.488 |  |  | 0.069 | 0.079 | [5 empty] | 29.6 |  |  |  |  | 59.3 |  | 24.3 |  | 8.3 | 0.089 |  | 18.8 | 76.8 | 1.1 |  |  |  |  | 13.701 | 11.494 | [6 empty] | 30.51 |  | 14.02
2012-08-31 | 6.21 | 5.87 |  |  |  |  | 7.23 | 2 |  |  |  |  | 25 |  |  |  | 0 | 0.472 |  |  | 0.071 | 0.091 | [5 empty] | 30.6 |  |  |  |  | 61.2 |  | 25.8 |  | 8 | 0.074 |  | 18.8 | 73.69 | 0.63 |  |  |  |  | 14.85 | 12.744 | [6 empty] | 29.24 |  | 13.12
2012-09-01 | 6.43 | 5.91 |  |  |  |  | 7.42 | 1.93 |  |  |  |  | 31 |  |  |  | 0 | 0.547 |  |  | 0.094 | 0.212 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 35.3 |  | 7.4 | 0.061 |  | 18.4 | 70.8 | 0.56 |  |  |  |  | 13.07 | 12.88 | [6 empty] | 31.64 |  | 13.88
2012-09-02 | 6.32 | 5.82 |  |  |  |  | 7.325 | 1.965 |  |  |  |  | 28 |  |  |  | 0 | 0.5095 |  |  | 0.0825 | 0.1515 | [5 empty] | 29.5 |  |  |  |  | 59 |  | 30.55 |  | 7.7 | 0.0675 |  | 18.6 | 72.245 | 0.595 |  |  |  |  | 14.2755 | 12.119 | [6 empty] | 30.44
2012-09-03 | 7.45 | 5.98 |  |  |  |  | 7.12 | 1.89 |  |  |  |  | 31 |  |  |  | 0 | 0.524 |  |  | 0.132 | 0.095 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 24 |  | 8.2 | 0.085 |  | 16.5 | 79.8 | 1.04 |  |  |  |  | 14.049 | 12.358 | [6 empty] | 29.11 |  | 13.7
2012-09-04 | 7.68 | 6.1 |  |  |  |  | 7.12 | 1.82 |  |  |  |  | 30 |  |  |  | 0 | 0.553 |  |  | 0.067 | 0.094 | [5 empty] | 28.7 |  |  |  |  | 57.6 |  | 23.1 |  | 7.9 | 0.081 |  | 16.6 | 76.45 | 0.79 |  |  |  |  | 14.057 | 13.294 | [6 empty] | 30.04 |  | 13.12
2012-09-05 | 6.95 | 5.93 |  |  |  |  | 7.44 | 1.84 |  |  |  |  | 34 |  |  |  | 0 | 0.67 |  |  | 0.077 | 0.111 | [5 empty] | 29.2 |  |  |  |  | 58.5 |  | 23.3 |  | 7.1 | 0.094 |  | 16.8 | 68.62 | 0.53 |  |  |  |  | 13.97 | 13.153 | [6 empty] | 30.18 |  | 12.68
2012-09-06 | 6.87 | 5.49 |  |  |  |  | 7.55 | 1.82 |  |  |  |  | 37 |  |  |  | 0 | 0.621 |  |  | 0.084 | 0.095 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 25.6 |  | 6.4 | 0.087 |  | 16.9 | 81.41 | 1.14 |  |  |  |  | 14.192 | 12.498 | [6 empty] | 29.76 |  | 11.89
2012-09-07 | 5.99 | 5.56 |  |  |  |  | 7.65 | 1.82 |  |  |  |  | 39 |  |  |  | 0 | 0.531 |  |  | 0.101 | 0.108 | [5 empty] | 31 |  |  |  |  | 62 |  | 25.9 |  | 6.3 | 0.091 |  | 16.4 | 71.65 | 0.7 |  |  |  |  | 13.753 | 12.914 | [6 empty] | 29.32 |  | 13.49
2012-09-08 | 5.78 | 5.79 |  |  |  |  | 7.54 | 1.83 |  |  |  |  | 38 |  |  |  | 0 | 0.497 |  |  | 0.108 | 0.102 | [5 empty] | 30.1 |  |  |  |  | 60.2 |  | 25.9 |  | 7.1 | 0.08 |  | 16.2 | 78.26 | 0.94 |  |  |  |  | 14.067 | 12.804 | [6 empty] | 30.42 |  | 15.59
2012-09-09 | 5.885 | 5.525 |  |  |  |  | 7.595 | 1.8 |  |  |  |  | 38.5 |  |  |  | 0 | 0.514 |  |  | 0.1045 | 0.105 | [5 empty] | 30.55 |  |  |  |  | 61.1 |  | 25.9 |  | 6.7 | 0.0855 |  | 16.3 | 74.62 | 0.97 |  |  |  |  | 13.577 | 12.236 | [6 empty] | 29.87
2012-09-10 | 6.19 | 5.86 |  |  |  |  | 7.44 | 1.95 |  |  |  |  | 43 |  |  |  | 0 | 0.649 |  |  | 0.113 | 0.101 | [5 empty] | 29.8 |  |  |  |  | 59.6 |  | 26.4 |  | 6.8 | 0.074 |  | 16.1 | 85.07 | 1.08 |  |  |  |  | 15.183 | 12.746 | [6 empty] | 31.68 |  | 12.69
2012-09-11 | 6.75 | 5.82 |  |  |  |  | 7.85 | 1.86 |  |  |  |  | 43 |  |  |  | 0 | 0.619 |  |  | 0.083 | 0.108 | [5 empty] | 29.5 |  |  |  |  | 59 |  | 26.3 |  | 7.2 | 0.067 |  | 17 | 75.15 | 1.18 |  |  |  |  | 13.719 | 11.235 | [6 empty] | 30.88 |  | 13.36
2012-09-12 | 5.98 | 5.55 |  |  |  |  | 7.65 | 1.86 |  |  |  |  | 44 |  |  |  | 0 | 0.642 |  |  | 0.073 | 0.102 | [5 empty] | 29.4 |  |  |  |  | 58.8 |  | 25.9 |  | 7.1 | 0.055 |  | 16.2 | 79.69 | 0.88 |  |  |  |  | 14.503 | 13.188 | [6 empty] | 29.37 |  | 12.12
2012-09-13 | 6.08 | 5.82 |  |  |  |  | 7.63 | 1.85 |  |  |  |  | 39 |  |  |  | 0 | 0.679 |  |  | 0.106 | 0.109 | [5 empty] | 30.7 |  |  |  |  | 61.4 |  | 24.8 |  | 7.4 | 0.075 |  | 16.3 | 85.07 | 1.08 |  |  |  |  | 14.43 | 13.16 | [6 empty] | 29.55 |  | 12.54
2012-09-14 | 7.26 | 5.71 |  |  |  |  | 8.63 | 2.01 |  |  |  |  | 37 |  |  |  | 0 | 0.648 |  |  | 0.152 | 0.118 | [5 empty] | 30.3 |  |  |  |  | 60.8 |  | 23.9 |  | 8.4 | 0.11 |  | 16.4 | 90.56 | 0.92 |  |  |  |  | 15.33 | 14.033 | [6 empty] | 30.04 |  | 13.38
2012-09-15 | 6.93 | 4.97 |  |  |  |  | 6.7 | 1.74 |  |  |  |  | 38 |  |  |  | 0 | 0.718 |  |  | 0.721 | 0.224 | [5 empty] | 30.4 |  |  |  |  | 60.9 |  | 26.1 |  | 8.6 | 0.091 |  | 16.9 | 85.58 | 1.42 |  |  |  |  | 13.637 | 12.293 | [6 empty] | 26.76 |  | 12.76
2012-09-16 | 7.095 | 5.765 |  |  |  |  | 7.665 | 1.74 |  |  |  |  | 37.5 |  |  |  | 0 | 0.683 |  |  | 0.4365 | 0.171 | [5 empty] | 30.35 |  |  |  |  | 60.85 |  | 25 |  | 8.5 | 0.1005 |  | 16.65 | 96.79 | 1.7 |  |  |  |  | 14.21 | 12.722 | [6 empty] | 26.76 |  | 12.76
2012-09-17 | 6.05 | 5.8 |  |  |  |  | 7.49 | 2.33 |  |  |  |  | 39 |  |  |  | 8 | 0.516 |  |  | 1.63 | 0.41 | [5 empty] | 30.1 |  |  |  |  | 60.2 |  | 25.8 |  | 8.3 | 0.199 |  | 16.6 | 120.77 | 1.65 |  |  |  |  | 15.517 | 13.72 | [6 empty] | 34.08 |  | 15.32
2012-09-18 | 6.17 | 6.5 |  |  |  |  | 7.37 | 2.52 |  |  |  |  | 49 |  |  |  | 2 | 0.497 |  |  | 0.653 | 0.201 | [5 empty] | 29.4 |  |  |  |  | 58.8 |  | 26.3 |  | 7.7 | 0.147 |  | 16.7 | 114.9 | 1.03 |  |  |  |  | 15.8 | 14.68 | [6 empty] | 31.8 |  | 12.96
2012-09-19 | 6.73 | 5.58 |  |  |  |  | 8.71 | 2.11 |  |  |  |  | 36 |  |  |  | 0 | 0.49 |  |  | 0.079 | 0.127 | [5 empty] | 30.6 |  |  |  |  | 61.2 |  | 26.4 |  | 7.9 | 0.088 |  | 16.2 | 85.22 | 0.68 |  |  |  |  | 14.737 | 13.89 | [6 empty] | 31.45 |  | 16.99
2012-09-20 | 6.99 | 5.44 |  |  |  |  | 8.99 | 2.08 |  |  |  |  | 38 |  |  |  | 0 | 0.671 |  |  | 0.089 | 0.113 | [5 empty] | 30.4 |  |  |  |  | 60.9 |  | 26.5 |  | 8.1 | 0.081 |  | 16.2 | 91.09 | 0.87 |  |  |  |  | 14.849 | 14 | [6 empty] | 30.51 |  | 15.3
2012-09-21 | 6.78 | 5.52 |  |  |  |  | 5.77 | 2.11 |  |  |  |  | 39 |  |  |  | 0 | 0.587 |  |  | 0.084 | 0.076 | [5 empty] | 28.8 |  |  |  |  | 57.6 |  | 26.5 |  | 8 | 0.076 |  | 16 | 89.39 | 0.86 |  |  |  |  | 14.728 | 13.67 | [6 empty] | 30.98
2012-09-22 | 6.2 | 5 |  |  |  |  | 3.94 | 1.86 |  |  |  |  | 43 |  |  |  | 0 | 0.571 |  |  | 0.088 | 0.054 | [5 empty] | 25.3 |  |  |  |  | 50.6 |  | 26.1 |  | 5.7 | 0.197 |  | 16.2 | 100.7 | 1.4 |  |  |  |  | 15.726 | 14.033 | [6 empty] | 30.76 |  | 11.95
2012-09-23 | 6.49 | 5.48 |  |  |  |  | 4.855 | 1.985 |  |  |  |  | 41 |  |  |  | 0 | 0.579 |  |  | 0.086 | 0.065 | [5 empty] | 27.05 |  |  |  |  | 54.1 |  | 26.3 |  | 6.85 | 0.1365 |  | 16.1 | 95.045 | 1.13 |  |  |  |  | 14.7885 | 13.835 | [6 empty] | 30.87
2012-09-24 | 6.96 | 6.49 |  |  |  |  | 8.73 | 2.19 |  |  |  |  | 36 |  |  |  | 0 | 0.622 |  |  | 0.085 | 0.095 | [5 empty] | 33.2 |  |  |  |  | 66.7 |  | 21.8 |  | 8.7 | 0.131 |  | 17 | 95.19 | 1.07 |  |  |  |  | 14.918 | 13.257 | [6 empty] | 29.11 |  | 16.15
2012-09-25 | 6.42 | 5.75 |  |  |  |  | 7.34 | 2.19 |  |  |  |  | 35 |  |  |  | 0 | 0.651 |  |  | 0.068 | 0.09 | [5 empty] | 31.4 |  |  |  |  | 62.8 |  | 22.8 |  | 8.5 | 0.121 |  | 16.9 | 90.45 | 0.83 |  |  |  |  | 14.873 | 13.588 | [6 empty] | 28.17 |  | 14.04
2012-09-26 | 6.53 | 5.32 |  |  |  |  | 6.9 | 2.1 |  |  |  |  | 33 |  |  |  | 0 | 0.697 |  |  | 0.071 | 0.097 | [5 empty] | 30.7 |  |  |  |  | 61.4 |  | 23.5 |  | 7.7 | 0.114 |  | 16.6 | 90.98 | 0.93 |  |  |  |  | 14.45 | 13.653 | [6 empty] | 33.6 |  | 14.46
2012-09-27 | 6.44 | 6.06 |  |  |  |  | 7.03 | 2.11 |  |  |  |  | 37 |  |  |  | 0 | 0.72 |  |  | 0.062 | 0.1 | [5 empty] | 32.4 |  |  |  |  | 64.8 |  | 22.7 |  | 9.2 | 0.094 |  | 16.4 | 90.43 | 1.02 |  |  |  |  | 14.52 | 13.123 | [6 empty] | 32.78 |  | 13.11
2012-09-28 | 5.77 | 6.02 |  |  |  |  | 7.22 | 2.04 |  |  |  |  | 36 |  |  |  | 0 | 0.795 |  |  | 0.07 | 0.093 | [5 empty] | 33.5 |  |  |  |  | 67 |  | 23.5 |  | 8.4 | 0.076 |  | 16 | 85.07 | 1 |  |  |  |  | 14.47 | 12.705 | [6 empty] | 32.79 |  | 19.19
2012-09-29 | 5.93 | 6.12 |  |  |  |  | 7.99 | 2.05 |  |  |  |  | 28 |  |  |  | 0 | 0.758 |  |  | 0.071 | 0.108 | [5 empty] | 33.3 |  |  |  |  | 66.6 |  | 25.5 |  | 8.1 | 0.069 |  | 15.4 | 79.79 | 0.87 |  |  |  |  | 13.613 | 12.413 | [6 empty] | 36.69 |  | 16.02
2012-09-30 | 5.85 | 6.04 |  |  |  |  | 7.605 | 1.92 |  |  |  |  | 32 |  |  |  | 0 | 0.7765 |  |  | 0.0705 | 0.1005 | [5 empty] | 33.4 |  |  |  |  | 66.8 |  | 24.5 |  | 8.25 | 0.0725 |  | 15.7 | 74.02 | 0.86 |  |  |  |  | 13.366 | 12.085
2012-10-01 | 6.05 | 5.44 |  |  |  |  | 7.07 | 1.86 |  |  |  |  | 31 |  |  |  | 0 | 0.747 |  |  | 0.052 | 0.102 | [5 empty] | 34.7 |  |  |  |  | 69.5 |  | 26.6 |  | 7.9 | 0.054 |  | 15.6 | 81.54 | 1.08 |  |  |  |  | 14.74 | 12.58 | [6 empty] | 36.73 |  | 14.88
2012-10-02 | 5.95 | 6.08 |  |  |  |  | 7.3375 | 1.89 |  |  |  |  | 31.5 |  |  |  | 0 | 0.76175 |  |  | 0.06125 | 0.10125 | [5 empty] | 34.05 |  |  |  |  | 68.15 |  | 25.55 |  | 8.075 | 0.06325 |  | 15.65 | 77.78 | 0.97 |  |  |  |  | 13.4895 | 12.249 | [6 empty] | 18.365
2012-10-03 | 6.19 | 5.47 |  |  |  |  | 7.54 | 1.84 |  |  |  |  | 40 |  |  |  | 0 | 0.687 |  |  | 0.067 | 0.17 | [5 empty] | 30.6 |  |  |  |  | 61.2 |  | 25.5 |  | 7.2 | 0.078 |  | 15.4 | 80.2 | 1.1 |  |  |  |  | 13.683 | 12.398 | [6 empty] | 33.63 |  | 13.86
2012-10-04 | 6.15 | 5.54 |  |  |  |  | 7.74 | 1.98 |  |  |  |  | 44 |  |  |  | 0 | 0.669 |  |  | 0.083 | 0.116 | [5 empty] | 33.8 |  |  |  |  | 67.6 |  | 25.8 |  | 7.1 | 0.073 |  | 14.9 | 85.07 | 0.93 |  |  |  |  | 14.72 | 13.41 | [6 empty] | 34.18 |  | 14.64
2012-10-05 | 6.34 | 5.55 |  |  |  |  | 7.83 | 1.91 |  |  |  |  | 39 |  |  |  | 0 | 0.664 |  |  | 0.066 | 0.114 | [5 empty] | 35 |  |  |  |  | 70.2 |  | 25.5 |  | 7.6 | 0.088 |  | 14.3 | 79.69 | 1.014 |  |  |  |  | 13.71 | 12.38 | [6 empty] | 31.92 |  | 17.53
2012-10-06 | 6.84 | 5.68 |  |  |  |  | 7.89 | 1.9 |  |  |  |  | 37 |  |  |  | 0 | 0.705 |  |  | 0.072 | 0.111 | [5 empty] | 36.1 |  |  |  |  | 72.2 |  | 23.2 |  | 7.4 | 0.092 |  | 13.8 | 80.13 | 0.99 |  |  |  |  | 13.8 | 12.58 | [6 empty] | 31.45 |  | 16.36
2012-10-07 | 6.59 | 5.545 |  |  |  |  | 7.86 | 1.88 |  |  |  |  | 38 |  |  |  | 0 | 0.6845 |  |  | 0.069 | 0.1125 | [5 empty] | 35.55 |  |  |  |  | 71.2 |  | 24.35 |  | 7.5 | 0.09 |  | 14.05 | 79.69 | 1 |  |  |  |  | 13.895 | 12.541 | [6 empty] | 31.45 |  | 16.36
2012-10-08 | 5.49 | 5.44 |  |  |  |  | 7.84 | 1.97 |  |  |  |  | 37 |  |  |  | 0 | 0.751 |  |  | 0.072 | 0.1 | [5 empty] | 34.3 |  |  |  |  | 68.6 |  | 24.6 |  | 7 | 0.049 |  | 13.7 | 85.55 | 1.08 |  |  |  |  | 14.516 | 12.75 | [6 empty] | 39.84 |  | 16.14
2012-10-09 | 6.01 | 5.57 |  |  |  |  | 7.81 | 1.89 |  |  |  |  | 36 |  |  |  | 0 | 0.487 |  |  | 0.079 | 0.104 | [5 empty] | 33.4 |  |  |  |  | 66.8 |  | 24.8 |  | 7.4 | 0.046 |  | 13.3 | 85.09 | 1.18 |  |  |  |  | 13.85 | 12.57 | [6 empty] | 34.8 |  | 16.29
2012-10-10 | 6.86 | 5.6 |  |  |  |  | 7.85 | 1.81 |  |  |  |  | 38 |  |  |  | 0 | 0.512 |  |  | 0.131 | 0.104 | [5 empty] | 36.2 |  |  |  |  | 72.3 |  | 22.4 |  | 10.3 | 0.102 |  | 12.9 | 80.17 | 0.98 |  |  |  |  | 14.104 | 13.023 | [6 empty] | 31.92 |  | 17.12
2012-10-11 | 7.7 | 5.76 |  |  |  |  | 7.47 | 1.66 |  |  |  |  | 47 |  |  |  | 0 | 0.507 |  |  | 1.15 | 0.282 | [5 empty] | 32.8 |  |  |  |  | 65.7 |  | 21.9 |  | 9.8 | 0.182 |  | 12.6 | 89.48 | 1.49 |  |  |  |  | 14.884 | 12.902 | [6 empty] | 31.45 |  | 17
2012-10-12 | 6.74 | 5.37 |  |  |  |  | 7.63 | 1.9 |  |  |  |  | 54 |  |  |  | 0 | 1.417 |  |  | 0.147 | 0.102 | [5 empty] | 33.9 |  |  |  |  | 67.8 |  | 22.3 |  | 8.9 | 0.131 |  | 12.4 | 90.45 | 1.17 |  |  |  |  | 16.458 | 13.363 | [6 empty] | 32.03 |  | 16.76
2012-10-13 | 6.69 | 5.67 |  |  |  |  | 8.9 | 2.1 |  |  |  |  | 57 |  |  |  | 0 | 0.827 |  |  | 0.142 | 0.127 | [5 empty] | 32.1 |  |  |  |  | 64.2 |  | 23.3 |  | 7.2 | 0.102 |  | 12.5 | 95.65 | 1.32 |  |  |  |  | 14.91 | 12.7 | [6 empty] | 15.39 |  | 31.59
2012-10-14 | 6.715 | 5.565 |  |  |  |  | 8.265 | 2 |  |  |  |  | 55.5 |  |  |  | 0 | 1.122 |  |  | 0.1445 | 0.1145 | [5 empty] | 33 |  |  |  |  | 66 |  | 22.8 |  | 8.05 | 0.1165 |  | 12.45 | 93.05 | 1.245 |  |  |  |  | 15.671 | 13.1325 | [6 empty] | 23.71
2012-10-15 | 6.63 | 5.68 |  |  |  |  | 8.91 | 2.36 |  |  |  |  | 37 |  |  |  | 0 | 0.714 |  |  | 0.097 | 0.107 | [5 empty] | 36 |  |  |  |  | 72.1 |  | 22 |  | 7.9 | 0.089 |  | 10.2 | 100.24 | 1.03 |  |  |  |  | 16.491 | 13.444 | [6 empty] | 34.74 |  | 20.34
2012-10-16 | 6.6 | 5.33 |  |  |  |  | 8.94 | 2.27 |  |  |  |  | 41 |  |  |  | 0 | 0.77 |  |  | 0.226 | 0.158 | [5 empty] | 35 |  |  |  |  | 70 |  | 22.4 |  | 7.7 | 0.148 |  | 9.7 | 90.09 | 0.74 |  |  |  |  | 15.62 | 13.597 | [6 empty] | 29.57 |  | 19
2012-10-17 | 6.71 | 5.77 |  |  |  |  | 9.03 | 2.259 |  |  |  |  | 40 |  |  |  | 0 | 0.796 |  |  | 0.291 | 0.113 | [5 empty] | 33.6 |  |  |  |  | 67.2 |  | 23.2 |  | 7.2 | 0.112 |  | 9.6 | 90.36 | 0.73 |  |  |  |  | 14.398 | 13.591 | [6 empty] | 36.6 |  | 17.77
2012-10-18 | 6.54 | 5.28 |  |  |  |  | 8.53 | 2.38 |  |  |  |  | 31 |  |  |  | 0 | 0.834 |  |  | 0.107 | 0.103 | [5 empty] | 32.1 |  |  |  |  | 64.1 |  | 21.1 |  | 6.7 | 0.154 |  | 10.4 | 89.96 | 0.8 |  |  |  |  | 14.389 | 12.856 | [6 empty] | 33.28 |  | 12.6
2012-10-19 | 5.74 | 5.34 |  |  |  |  | 8.38 | 2.36 |  |  |  |  | 34 |  |  |  | 0 | 0.077 |  |  | 0.088 | 0.109 | [5 empty] | 29.4 |  |  |  |  | 58.8 |  | 22.5 |  | 7.1 | 0.124 |  | 10.2 | 85.55 | 0.72 |  |  |  |  | 13.155 | 12.599 | [6 empty] | 35.58 |  | 14.1
2012-10-20 | 5.48 | 5.21 |  |  |  |  | 8.6 | 2.29 |  |  |  |  | 33 |  |  |  | 0 | 0.774 |  |  | 0.076 | 0.114 | [5 empty] | 34.3 |  |  |  |  | 68.6 |  | 23.6 |  | 7 | 0.097 |  | 10.1 | 79.95 | 0.7 |  |  |  |  | 13.1 | 12.13 | [6 empty] | 34.81 |  | 16.37
2012-10-21 | 5.61 | 5.31 |  |  |  |  | 8.49 | 2.16 |  |  |  |  | 33.5 |  |  |  | 0 | 0.4255 |  |  | 0.082 | 0.1115 | [5 empty] | 31.85 |  |  |  |  | 63.7 |  | 23.05 |  | 7.05 | 0.1105 |  | 10.15 | 74.95 | 0.75 |  |  |  |  | 12.757 | 11.705 | [6 empty] | 35.195
2012-10-22 | 6.04 | 5.38 |  |  |  |  | 8.62 | 2.34 |  |  |  |  | 38 |  |  |  | 0 | 0.747 |  |  | 0.067 | 0.099 | [5 empty] | 34.8 |  |  |  |  | 69.6 |  | 24.3 |  | 6.4 | 0.082 |  | 10 | 90.45 | 0.84 |  |  |  |  | 14.633 | 12.921 | [6 empty] | 34.58 |  | 15.67
2012-10-23 | 6.41 | 5.37 |  |  |  |  | 8.56 | 2.28 |  |  |  |  | 44 |  |  |  | 0 | 0.699 |  |  | 0.096 | 0.097 | [5 empty] | 35.2 |  |  |  |  | 70.4 |  | 36.4 |  | 7.8 | 0.107 |  | 10.5 | 85.55 | 0.7 |  |  |  |  | 13.651 | 13.032 | [6 empty] | 35.96 |  | 13.93
2012-10-24 | 5.65 | 5.57 |  |  |  |  | 8.42 | 2.24 |  |  |  |  | 43 |  |  |  | 0 | 0.694 |  |  | 0.084 | 0.083 | [5 empty] | 31.1 |  |  |  |  | 62.2 |  | 29.5 |  | 7.6 | 0.091 |  | 10.4 | 79.31 | 0.64 |  |  |  |  | 13.666 | 12.513 | [6 empty] | 34.68 |  | 12.09
2012-10-25 | 5.58 | 5.56 |  |  |  |  | 7.7 | 2.23 |  |  |  |  | 42 |  |  |  | 0 | 0.708 |  |  | 0.087 | 0.083 | [5 empty] | 31.7 |  |  |  |  | 63.4 |  | 26.8 |  | 7.7 | 0.099 |  | 10.1 | 80.33 | 0.66 |  |  |  |  | 13.81 | 12.61 | [6 empty] | 37.52 |  | 12.29
2012-10-26 | 6.55 | 5.24 |  |  |  |  | 6.84 | 2.15 |  |  |  |  | 39 |  |  |  | 0 | 0.976 |  |  | 0.145 | 0.086 | [5 empty] | 33.8 |  |  |  |  | 67.7 |  | 26.3 |  | 7.7 | 0.088 |  | 9.7 | 76.23 | 0.5 |  |  |  |  | 13.22 | 13.04 | [6 empty] | 37.58 |  | 14.52
2012-10-27 | 6.48 | 5.16 |  |  |  |  | 7.42 | 1.98 |  |  |  |  | 36 |  |  |  | 0 | 0.681 |  |  | 0.101 | 0.091 | [5 empty] | 34 |  |  |  |  | 68.1 |  | 23.9 |  | 8.1 | 0.081 |  | 9.4 | 74.95 | 0.91 |  |  |  |  | 13.054 | 11.782 | [6 empty] | 35.68 |  | 16.17
2012-10-28 | 6.515 | 5.4 |  |  |  |  | 7.13 | 1.96 |  |  |  |  | 37.5 |  |  |  | 0 | 0.8285 |  |  | 0.123 | 0.0885 | [5 empty] | 33.9 |  |  |  |  | 67.9 |  | 25.1 |  | 7.9 | 0.0845 |  | 9.55 | 79.2 | 1.09 |  |  |  |  | 12.946 | 11.808 | [6 empty] | 35.68 |  | 16.17
2012-10-29 | 5.65 | 5.64 |  |  |  |  | 7.62 | 2.06 |  |  |  |  | 67 |  |  |  | 0 | 2.286 |  |  | 0.079 | 0.089 | [5 empty] | 34.2 |  |  |  |  | 68.4 |  | 24.5 |  | 6.4 | 0.169 |  | 9.4 | 93.21 | 1.32 |  |  |  |  | 14.162 | 12.527 | [6 empty] | 42.16 |  | 15.61
2012-10-30 | 6 | 5.2 |  |  |  |  | 8.64 | 2.07 |  |  |  |  | 62 |  |  |  | 0 | 2.337 |  |  | 0.079 | 0.108 | [5 empty] | 32 |  |  |  |  | 64 |  | 25.7 |  | 7.3 | 0.131 |  | 9.5 | 79.93 | 0.79 |  |  |  |  | 12.92 | 12.7 | [6 empty] | 37.17 |  | 17.52
2012-10-31 | 6.41 | 5.37 |  |  |  |  | 8.41 | 2 |  |  |  |  | 40 |  |  |  | 0 | 0.572 |  |  | 0.084 | 0.094 | [5 empty] | 35.7 |  |  |  |  | 71.4 |  | 23.8 |  | 7.5 | 0.121 |  | 9.7 | 84.58 | 1.13 |  |  |  |  | 12.999 | 12.275 | [6 empty] | 35.7 |  | 16.99
2012-11-01 | 6.36 | 5.35 |  |  |  |  | 8.73 | 1.88 |  |  |  |  | 36 |  |  |  | 0 | 0.467 |  |  | 0.088 | 0.098 | [5 empty] | 37.3 |  |  |  |  | 74.8 |  | 21.6 |  | 7.9 | 0.096 |  | 9.6 | 85.07 | 1.09 |  |  |  |  | 14.18 | 13.014 | [6 empty] | 33.8 |  | 17.61
2012-11-02 | 6.54 | 5.32 |  |  |  |  | 8.75 | 1.82 |  |  |  |  | 42 |  |  |  | 0 | 0.449 |  |  | 0.091 | 0.097 | [5 empty] | 34.9 |  |  |  |  | 69.9 |  | 23.7 |  | 7.4 | 0.087 |  | 9.65 | 74.82 | 0.82 |  |  |  |  | 13.561 | 12.858 | [6 empty] | 32.4 |  | 17.13
2012-11-03 | 6.4 | 5.3 |  |  |  |  | 8.61 | 1.81 |  |  |  |  | 32 |  |  |  | 0 | 0.457 |  |  | 0.077 | 0.092 | [5 empty] | 34.8 |  |  |  |  | 69.6 |  | 24.5 |  | 6.6 | 0.074 |  | 9.4 | 75.87 | 0.95 |  |  |  |  | 12.66 | 12.48 | [6 empty] | 33.27 |  | 15.26
2012-11-04 | 6.47 | 5.335 |  |  |  |  | 8.68 | 1.815 |  |  |  |  | 37 |  |  |  | 0 | 0.453 |  |  | 0.084 | 0.0945 | [5 empty] | 34.85 |  |  |  |  | 69.75 |  | 24.1 |  | 7 | 0.0805 |  | 9.525 | 75.345 | 0.885 |  |  |  |  | 13.8705 | 12.936 | [6 empty] | 32.835
2012-11-05 | 6.58 | 5.18 |  |  |  |  | 8 | 1.81 |  |  |  |  | 31 |  |  |  | 0 | 0.409 |  |  | 0.109 | 0.087 | [5 empty] | 35 |  |  |  |  | 70.2 |  | 31 |  | 8.4 | 0.143 |  | 10.3 | 80.66 | 1.09 |  |  |  |  | 14.173 | 12.626 | [6 empty] | 33.33 |  | 17.46
2012-11-06 | 6.32 | 5.22 |  |  |  |  | 8.62 | 1.82 |  |  |  |  | 33 |  |  |  | 0 | 0.415 |  |  | 0.088 | 0.092 | [5 empty] | 32.5 |  |  |  |  | 65.2 |  | 28.6 |  | 8.2 | 0.132 |  | 10.1 | 75.79 | 0.84 |  |  |  |  | 13.607 | 12.919 | [6 empty] | 33.8 |  | 16.46
2012-11-07 | 6.29 | 5.36 |  |  |  |  | 8.81 | 1.78 |  |  |  |  | 31 |  |  |  | 0 | 0.467 |  |  | 0.074 | 0.097 | [5 empty] | 34.7 |  |  |  |  | 69.4 |  | 28 |  | 7.7 | 0.117 |  | 9.9 | 64.74 | 0.67 |  |  |  |  | 12.672 | 11.99 | [6 empty] | 32.51 |  | 16.4
2012-11-08 | 6.24 | 5.25 |  |  |  |  | 8.48 | 1.81 |  |  |  |  | 40 |  |  |  | 0 | 0.447 |  |  | 0.074 | 0.091 | [5 empty] | 34.2 |  |  |  |  | 68.4 |  | 26.6 |  | 7 | 0.114 |  | 10 | 80.04 | 1.04 |  |  |  |  | 14.276 | 12.729 | [6 empty] | 31.68 |  | 15.45
2012-11-09 | 5.59 | 5.45 |  |  |  |  | 8.62 | 1.71 |  |  |  |  | 42 |  |  |  | 0 | 0.448 |  |  | 0.083 | 0.097 | [5 empty] | 35 |  |  |  |  | 70 |  | 25.9 |  | 7.3 | 0.097 |  | 8.8 | 69.92 | 0.77 |  |  |  |  | 13.567 | 12.786 | [6 empty] | 40.69 |  | 16.11
2012-11-10 | 5.5 | 5.66 |  |  |  |  | 8.72 | 1.67 |  |  |  |  | 43 |  |  |  | 0 | 0.578 |  |  | 0.178 | 0.108 | [5 empty] | 34 |  |  |  |  | 68 |  | 26.9 |  | 7.6 | 0.113 |  | 9.1 | 75.15 | 1.19 |  |  |  |  | 12.91 | 11.92 | [6 empty] | 39.57 |  | 15.81
2012-11-11 | 5.545 | 5.35 |  |  |  |  | 8.67 | 1.67 |  |  |  |  | 42.5 |  |  |  | 0 | 0.513 |  |  | 0.1305 | 0.1025 | [5 empty] | 34.5 |  |  |  |  | 69 |  | 26.4 |  | 7.45 | 0.105 |  | 8.95 | 65.03 | 0.97 |  |  |  |  | 12.418 | 11.88 | [6 empty] | 40.13
2012-11-12 | 5.83 | 5.11 |  |  |  |  | 7.78 | 1.67 |  |  |  |  | 37 |  |  |  | 0 | 0.491 |  |  | 0.107 | 0.096 | [5 empty] | 34.7 |  |  |  |  | 69.4 |  | 25.8 |  | 6.9 | 0.107 |  | 8.9 | 80.57 | 1.23 |  |  |  |  | 14.381 | 12.604 | [6 empty] | 37.08 |  | 14.91
2012-11-13 | 6.12 | 5.15 |  |  |  |  | 8.08 | 1.66 |  |  |  |  | 32 |  |  |  | 0 | 0.524 |  |  | 0.177 | 0.113 | [5 empty] | 31.3 |  |  |  |  | 62.6 |  | 22.7 |  | 6.5 | 0.113 |  | 8.9 | 70.05 | 1.68 |  |  |  |  | 13.658 | 9.512 | [6 empty] | 37.02 |  | 15.23
2012-11-14 | 6.14 | 5.33 |  |  |  |  | 7.88 | 1.7 |  |  |  |  | 31 |  |  |  | 0 | 0.608 |  |  | 0.163 | 0.108 | [5 empty] | 33.4 |  |  |  |  | 66.8 |  | 24.5 |  | 6.3 | 0.126 |  | 7.9 | 74.95 | 1.05 |  |  |  |  | 13.461 | 12.368 | [6 empty] | 37.03 |  | 15.59
2012-11-15 | 5.59 | 5.2 |  |  |  |  | 7.69 | 1.72 |  |  |  |  | 33 |  |  |  | 0 | 0.547 |  |  | 0.126 | 0.108 | [5 empty] | 31.9 |  |  |  |  | 63.8 |  | 23.5 |  | 6.5 | 0.114 |  | 7.4 | 75.3 | 1.15 |  |  |  |  | 13.088 | 11.896 | [6 empty] | 35.84 |  | 15.53
2012-11-16 | 6.42 | 5.01 |  |  |  |  | 7.09 | 1.81 |  |  |  |  | 48 |  |  |  | 0 | 0.522 |  |  | 0.086 | 0.093 | [5 empty] | 34.7 |  |  |  |  | 69.3 |  | 25.6 |  | 7.2 | 0.108 |  | 7.3 | 70.25 | 0.68 |  |  |  |  | 13.56 | 12.791 | [6 empty] | 34.27 |  | 15.27
2012-11-17 | 6.46 | 5.24 |  |  |  |  | 8.07 | 1.96 |  |  |  |  | 44 |  |  |  | 0 | 0.485 |  |  | 0.086 | 0.091 | [5 empty] | 34.1 |  |  |  |  | 68.3 |  | 25.6 |  | 8.2 | 0.094 |  | 7.1 | 75.79 | 0.9 |  |  |  |  | 13.62 | 12.03 | [6 empty] | 34.5 |  | 14.9
2012-11-18 | 6.44 | 5.105 |  |  |  |  | 7.58 | 1.83 |  |  |  |  | 46 |  |  |  | 0 | 0.5035 |  |  | 0.086 | 0.092 | [5 empty] | 34.4 |  |  |  |  | 68.8 |  | 25.6 |  | 7.7 | 0.101 |  | 7.2 | 69.59 | 0.81 |  |  |  |  | 13.446 | 11.98 | [6 empty] | 34.5 |  | 14.9
2012-11-19 | 5.44 | 5.19 |  |  |  |  | 8.36 | 1.74 |  |  |  |  | 45 |  |  |  | 0 | 0.473 |  |  | 0.094 | 0.098 | [5 empty] | 32 |  |  |  |  | 64 |  | 24.39 |  | 7.7 | 0.087 |  | 6.2 | 64.39 | 0.68 |  |  |  |  | 13.176 | 12.898 | [6 empty] | 35.81 |  | 14.38
2012-11-20 | 5.49 | 5.55 |  |  |  |  | 7.97 | 1.75 |  |  |  |  | 43 |  |  |  | 0 | 0.487 |  |  | 0.114 | 0.097 | [5 empty] | 33.5 |  |  |  |  | 67 |  | 25.8 |  | 7.8 | 0.096 |  | 6 | 75.79 | 1.01 |  |  |  |  | 14.04 | 12.46 | [6 empty] | 39.49 |  | 14.04
2012-11-21 | 6.65 | 5.16 |  |  |  |  | 8.55 | 1.87 |  |  |  |  | 40 |  |  |  | 0 | 0.46 |  |  | 0.076 | 0.093 | [5 empty] | 35 |  |  |  |  | 70.1 |  | 23.1 |  | 8.1 | 0.093 |  | 5.6 | 65.03 | 0.45 |  |  |  |  | 12.91 | 12.72 | [6 empty] | 33.8 |  | 16.26
2012-11-22 | 6.57 | 5.15 |  |  |  |  | 8.25 | 1.95 |  |  |  |  | 43 |  |  |  | 0 | 0.464 |  |  | 0.086 | 0.09 | [5 empty] | 32.9 |  |  |  |  | 65.8 |  | 26.7 |  | 9.2 | 0.181 |  | 5.4 | 69.35 | 0.64 |  |  |  |  | 13.305 | 12.15 | [6 empty] | 34.03 |  | 15.98
2012-11-23 | 6.34 | 5.18 |  |  |  |  | 8.58 | 1.99 |  |  |  |  | 42 |  |  |  | 0 | 0.483 |  |  | 0.094 | 0.093 | [5 empty] | 33.1 |  |  |  |  | 66.2 |  | 26.3 |  | 8.9 | 0.174 |  | 5.4 | 74.15 | 0.64 |  |  |  |  | 13.975 | 12.794 | [6 empty] | 33.25 |  | 15.3
2012-11-24 | 6.19 | 5.29 |  |  |  |  | 8.57 | 1.97 |  |  |  |  | 39 |  |  |  | 0 | 0.467 |  |  | 0.089 | 0.091 | [5 empty] | 32.6 |  |  |  |  | 65.2 |  | 25.6 |  | 7.8 | 0.161 |  | 5.5 | 59.8 | 0.21 |  |  |  |  | 13.1075 | 12.52 | [6 empty] | 33.32 |  | 14.12
2012-11-25 | 6.265 | 5.165 |  |  |  |  | 8.575 | 1.98 |  |  |  |  | 40.5 |  |  |  | 0 | 0.475 |  |  | 0.0915 | 0.092 | [5 empty] | 32.85 |  |  |  |  | 65.7 |  | 25.95 |  | 8.35 | 0.1675 |  | 5.45 | 66.975 | 0.425 |  |  |  |  | 13.64 | 12.472 | [6 empty] | 33.285
2012-11-26 | 6.67 | 5.28 |  |  |  |  | 8.64 | 1.94 |  |  |  |  | 47 |  |  |  | 0 | 0.84 |  |  | 0.144 | 0.101 | [5 empty] | 34.3 |  |  |  |  | 68.5 |  | 25.8 |  | 10.1 | 0.12 |  | 5.6 | 75.19 | 0.74 |  |  |  |  | 14.103 | 12.76 | [6 empty] | 31.92 |  | 17.1
2012-11-27 | 6.69 | 5.1 |  |  |  |  | 8.58 | 1.78 |  |  |  |  | 43 |  |  |  | 0 | 0.67 |  |  | 0.097 | 0.093 | [5 empty] | 32.4 |  |  |  |  | 64.9 |  | 22.8 |  | 10.3 | 0.112 |  | 5 | 70.56 | 0.77 |  |  |  |  | 13.379 | 12.575 | [6 empty] | 32.39 |  | 14.17
2012-11-28 | 6.52 | 5.15 |  |  |  |  | 7.82 | 1.73 |  |  |  |  | 43 |  |  |  | 0 | 0.641 |  |  | 0.152 | 0.1 | [5 empty] | 33.7 |  |  |  |  | 67.5 |  | 25.3 |  | 8.4 | 0.103 |  | 5.4 | 74.75 | 0.98 |  |  |  |  | 14.189 | 12.506 | [6 empty] | 31.14 |  | 14.12
2012-11-29 | 6.71 | 5.47 |  |  |  |  | 8.13 | 1.66 |  |  |  |  | 50 |  |  |  | 0 | 0.637 |  |  | 0.206 | 0.183 | [5 empty] | 34.2 |  |  |  |  | 68.4 |  | 25.1 |  | 8.2 | 0.157 |  | 5.2 | 70.56 | 0.88 |  |  |  |  | 13.235 | 12.588 | [6 empty] | 32.09 |  | 14.24
2012-11-30 | 5.27 | 5.3 |  |  |  |  | 8.09 | 1.63 |  |  |  |  | 49 |  |  |  | 0 | 0.563 |  |  | 0.115 | 0.126 | [5 empty] | 30.8 |  |  |  |  | 61.6 |  | 24.9 |  | 7.9 | 0.167 |  | 5.6 | 74.88 | 1.13 |  |  |  |  | 13.806 | 12.324 | [6 empty] | 32.96 |  | 13.73
2012-12-01 | 5.45 | 5.23 |  |  |  |  | 7.44 | 1.75 |  |  |  |  | 48 |  |  |  | 0 | 0.557 |  |  | 0.274 | 0.116 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 24.6 |  | 7.4 | 0.154 |  | 5.6 | 70.8 | 0.82 |  |  |  |  | 13.43 | 12.49 | [6 empty] | 31.21 |  | 11.03
2012-12-02 | 5.36 | 5.385 |  |  |  |  | 7.765 | 1.71 |  |  |  |  | 48.5 |  |  |  | 0 | 0.56 |  |  | 0.1945 | 0.121 | [5 empty] | 30.6 |  |  |  |  | 61.2 |  | 24.75 |  | 7.65 | 0.1605 |  | 5.6 | 79.53 | 0.95 |  |  |  |  | 14.31 | 13.589 | [6 empty] | 32.085
2012-12-03 | 6.04 | 5.5 |  |  |  |  | 8.07 | 1.65 |  |  |  |  | 46 |  |  |  | 0 | 0.554 |  |  | 0.106 | 0.123 | [5 empty] | 29.7 |  |  |  |  | 59.4 |  | 24.9 |  | 7.2 | 0.109 |  | 5.5 | 74.09 | 0.87 |  |  |  |  | 15.064 | 13.373 | [6 empty] | 34.34 |  | 11.88
2012-12-04 | 6.48 | 5.48 |  |  |  |  | 8.12 | 1.65 |  |  |  |  | 50 |  |  |  | 0 | 0.687 |  |  | 0.098 | 0.143 | [5 empty] | 33.7 |  |  |  |  | 67.4 |  | 21.2 |  | 7.9 | 0.123 |  | 5.6 | 85.47 | 0.99 |  |  |  |  | 15.888 | 14.682 | [6 empty] | 33.55 |  | 12.74
2012-12-05 | 5.6 | 5.39 |  |  |  |  | 7.98 | 1.61 |  |  |  |  | 46 |  |  |  | 0 | 0.508 |  |  | 0.144 | 0.16 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 22.4 |  | 7.7 | 0.02 |  | 5.3 | 79.8 | 1 |  |  |  |  | 14.876 | 13.868 | [6 empty] | 35.26 |  | 13.68
2012-12-06 | 5.33 | 5.15 |  |  |  |  | 6.69 | 1.74 |  |  |  |  | 47 |  |  |  | 1 | 0.477 |  |  | 0.1 | 0.189 | [5 empty] | 29.5 |  |  |  |  | 59 |  | 25.3 |  | 6.9 | 0.003 |  | 5.2 | 70.16 | 0.91 |  |  |  |  | 13.9 | 12.04 | [6 empty] | 35.91 |  | 10.88
2012-12-07 | 6.14 | 5.02 |  |  |  |  | 6.8 | 1.87 |  |  |  |  | 49 |  |  |  | 0 | 0.437 |  |  | 0.837 | 0.209 | [5 empty] | 31.8 |  |  |  |  | 63.5 |  | 26.2 |  | 6.8 | 0.014 |  | 4.9 | 75.74 | 0.98 |  |  |  |  | 13.827 | 12.053 | [6 empty] | 32.86 |  | 11.68
2012-12-08 | 6.38 | 5.58 |  |  |  |  | 6.74 | 2 |  |  |  |  | 45 |  |  |  | 0 | 0.42 |  |  | 0.094 | 0.235 | [5 empty] | 29.2 |  |  |  |  | 58.5 |  | 25.2 |  | 7.2 | 0.0085 |  | 5.1 | 69.59 | 0.53 |  |  |  |  | 13.14 | 12.5 | [6 empty] | 33.33 |  | 10.2
2012-12-09 | 6.26 | 5.085 |  |  |  |  | 6.77 | 1.9 |  |  |  |  | 47 |  |  |  | 0 | 0.4285 |  |  | 0.4655 | 0.222 | [5 empty] | 30.5 |  |  |  |  | 61 |  | 25.7 |  | 7 | 0.01125 |  | 5 | 65.18 | 0.54 |  |  |  |  | 12.767 | 12.127 | [6 empty] | 33.33 |  | 10.2
2012-12-10 | 6.13 | 5.41 |  |  |  |  | 6.87 | 1.83 |  |  |  |  | 44 |  |  |  | 0 | 0.428 |  |  | 0.091 | 0.264 | [5 empty] | 30.3 |  |  |  |  | 60.6 |  | 24.7 |  | 6.9 | 0.087 |  | 5.1 | 79.71 | 1.05 |  |  |  |  | 14.652 | 12.586 | [6 empty] | 38.23 |  | 8.59
2012-12-11 | 5.84 | 5.27 |  |  |  |  | 6.77 | 1.9 |  |  |  |  | 47 |  |  |  | 0 | 0.406 |  |  | 0.314 | 0.283 | [5 empty] | 32.4 |  |  |  |  | 64.8 |  | 23.9 |  | 6.5 | 0.173 |  | 5 | 70.74 | 0.78 |  |  |  |  | 13.08 | 11.99 | [6 empty] | 33.16 |  | 15.37
2012-12-12 | 6.61 | 4.8 |  |  |  |  | 5.96 | 1.69 |  |  |  |  | 46 |  |  |  | 0 | 0.401 |  |  | 0.29 | 0.286 | [5 empty] | 31.9 |  |  |  |  | 63.9 |  | 23.2 |  | 6.7 | 0.121 |  | 5.1 | 70.41 | 0.87 |  |  |  |  | 16.085 | 12.497 | [6 empty] | 32.86 |  | 12.86
2012-12-13 | 6.06 | 4.98 |  |  |  |  | 6.76 | 1.83 |  |  |  |  | 42 |  |  |  | 0 | 0.396 |  |  | 0.109 | 0.331 | [5 empty] | 33.3 |  |  |  |  | 66.6 |  | 26.4 |  | 7.1 | 0.86 |  | 5 | 75.28 | 0.76 |  |  |  |  | 15.6 | 13.196 | [6 empty] | 33.1 |  | 15.52
2012-12-14 | 6.21 | 5.62 |  |  |  |  | 7.33 | 1.76 |  |  |  |  | 47 |  |  |  | 0 | 0.397 |  |  | 0.201 | 0.407 | [5 empty] | 32.1 |  |  |  |  | 64.2 |  | 25.4 |  | 6.7 | 0.113 |  | 4.9 | 70.08 | 0.75 |  |  |  |  | 13.927 | 12.661 | [6 empty] | 34.05 |  | 16.39
2012-12-15 | 6.34 | 5.64 |  |  |  |  | 7.33 | 1.85 |  |  |  |  | 42 |  |  |  | 0 | 0.377 |  |  | 0.129 | 0.407 | [5 empty] | 33.3 |  |  |  |  | 66.7 |  | 25.1 |  | 6.5 | 0.104 |  | 4.9 | 65.03 | 0.59 |  |  |  |  | 13.15 | 12.11 | [6 empty] | 33.83 |  | 17.32
2012-12-16 | 6.275 | 5.3 |  |  |  |  | 7.33 | 1.805 |  |  |  |  | 44.5 |  |  |  | 0 | 0.387 |  |  | 0.165 | 0.407 | [5 empty] | 32.7 |  |  |  |  | 65.45 |  | 25.25 |  | 6.6 | 0.1085 |  | 4.9 | 67.555 | 0.67 |  |  |  |  | 14.7635 | 12.9285 | [6 empty] | 33.94
2012-12-17 | 6.53 | 5.74 |  |  |  |  | 7.28 | 1.8 |  |  |  |  | 46 |  |  |  | 0 | 0.341 |  |  | 0.076 | 0.401 | [5 empty] | 36 |  |  |  |  | 72 |  | 23.7 |  | 8.7 | 0.139 |  | 4.8 | 64.78 | 0.62 |  |  |  |  | 13.273 | 12.146 | [6 empty] | 33.56 |  | 18.39
2012-12-18 | 6.26 | 5.71 |  |  |  |  | 8.27 | 1.91 |  |  |  |  | 45 |  |  |  | 0 | 0.345 |  |  | 0.069 | 0.394 | [5 empty] | 35.8 |  |  |  |  | 71.6 |  | 22.8 |  | 8.5 | 0.121 |  | 4.9 | 69.57 | 0.51 |  |  |  |  | 14.204 | 13.027 | [6 empty] | 33.33 |  | 16.51
2012-12-19 | 5.8 | 5.3 |  |  |  |  | 8.93 | 1.77 |  |  |  |  | 44 |  |  |  | 0 | 0.352 |  |  | 0.514 | 0.389 | [5 empty] | 35.5 |  |  |  |  | 71 |  | 23.4 |  | 8.8 | 0.18 |  | 4.6 | 55.74 | 0.3 |  |  |  |  | 13.451 | 12.255 | [6 empty] | 31.92 |  | 17.28
2012-12-20 | 6.21 | 5.92 |  |  |  |  | 7.84 | 1.81 |  |  |  |  | 45 |  |  |  | 0 | 0.329 |  |  | 0.19 | 0.381 | [5 empty] | 34.9 |  |  |  |  | 69.8 |  | 22.3 |  | 7.9 | 0.109 |  | 4.3 | 65.99 | 0.59 |  |  |  |  | 13.196 | 12.456 | [6 empty] | 33.53 |  | 13.77
2012-12-21 | 5.51 | 6.37 |  |  |  |  | 6.52 | 1.91 |  |  |  |  | 47 |  |  |  | 4 | 0.339 |  |  | 0.295 | 0.374 | [5 empty] | 31.5 |  |  |  |  | 63 |  | 24.4 |  | 7.8 | 0.029 |  | 4.6 | 74.46 | 0.63 |  |  |  |  | 14.083 | 13.309 | [6 empty] | 35.54 |  | 13.48
2012-12-22 | 5.15 | 4.76 |  |  |  |  | 6.96 | 1.87 |  |  |  |  | 46 |  |  |  | 1 | 0.338 |  |  | 0.107 | 0.38 | [5 empty] | 34.8 |  |  |  |  | 69.6 |  | 24.7 |  | 7.2 | 0.042 |  | 4.5 | 70.41 | 0.59 |  |  |  |  | 14.228 | 13.017 | [6 empty] | 32.43 |  | 15.59
2012-12-23 | 5.33 | 6.145 |  |  |  |  | 6.74 | 1.85 |  |  |  |  | 46.5 |  |  |  | 2.5 | 0.3385 |  |  | 0.201 | 0.377 | [5 empty] | 33.15 |  |  |  |  | 66.3 |  | 24.55 |  | 7.5 | 0.0355 |  | 4.55 | 65.16 | 0.5 |  |  |  |  | 13.788 | 12.573 | [6 empty] | 33.985
2012-12-24 | 5.47 | 5.33 |  |  |  |  | 7.63 | 1.85 |  |  |  |  | 47 |  |  |  | 0 | 0.314 |  |  | 0.113 | 0.38 | [5 empty] | 33.9 |  |  |  |  | 67.9 |  | 24.3 |  | 6.8 | 0.062 |  | 4.4 | 79.01 | 0.92 |  |  |  |  | 14.314 | 12.964 | [6 empty] | 33.35 |  | 17.37
2012-12-25 | 5.39 | 5.31 |  |  |  |  | 7.65 | 1.78 |  |  |  |  | 42 |  |  |  | 0 | 0.294 |  |  | 0.083 | 0.387 | [5 empty] | 34.7 |  |  |  |  | 69.5 |  | 26.7 |  | 8.3 | 0.047 |  | 4.3 | 53.29 | 0.32 |  |  |  |  | 12.874 | 11.512 | [6 empty] | 35.29 |  | 16.91
2012-12-26 | 5.27 | 5.16 |  |  |  |  | 7.52 | 1.89 |  |  |  |  | 45 |  |  |  | 0 | 0.308 |  |  | 0.104 | 0.374 | [5 empty] | 34.8 |  |  |  |  | 69.6 |  | 25.5 |  | 7.9 | 0.041 |  | 43 | 64.29 | 0.53 |  |  |  |  | 13.27 | 12.06 | [6 empty] | 40.54 |  | 16.73
2012-12-27 | 5.34 | 5.17 |  |  |  |  | 7.5 | 1.89 |  |  |  |  | 48 |  |  |  | 1 | 0.312 |  |  | 0.099 | 0.383 | [5 empty] | 35.8 |  |  |  |  | 71.6 |  | 24.7 |  | 7.7 | 0.038 |  | 4.7 | 70.12 | 0.53 |  |  |  |  | 13.9 | 13.16 | [6 empty] | 34.35 |  | 14.83
2012-12-28 | 5.96 | 5.27 |  |  |  |  | 7.5 | 1.88 |  |  |  |  | 40 |  |  |  | 0 | 0.315 |  |  | 0.102 | 0.383 | [5 empty] | 35.7 |  |  |  |  | 71.4 |  | 27.3 |  | 8.1 | 0.056 |  | 4.3 | 70.51 | 0.64 |  |  |  |  | 13.42 | 12.71 | [6 empty] | 35.21 |  | 16.53
2012-12-29 | 6.28 | 5.14 |  |  |  |  | 7.48 | 1.8 |  |  |  |  | 44 |  |  |  | 0 | 0.308 |  |  | 0.107 | 0.373 | [5 empty] | 33.5 |  |  |  |  | 67.1 |  | 26.8 |  | 6.9 | 0.096 |  | 4.4 | 59.64 | 0.34 |  |  |  |  | 13.31 | 13.11 | [6 empty] | 38.02 |  | 15.77
2012-12-30 | 6.12 | 5.22 |  |  |  |  | 7.49 | 1.99 |  |  |  |  | 42 |  |  |  | 0 | 0.3115 |  |  | 0.1045 | 0.378 | [5 empty] | 34.6 |  |  |  |  | 69.25 |  | 27.05 |  | 7.5 | 0.076 |  | 4.35 | 64.74 | 0.22 |  |  |  |  | 13.551 | 13.313 | [6 empty] | 38.02 |  | 15.77
2012-12-31 | 5.27 | 5.28 |  |  |  |  | 7.61 | 2.03 |  |  |  |  | 46 |  |  |  | 0 | 0.306 |  |  | 0.097 | 0.398 | [5 empty] | 32.3 |  |  |  |  | 64.6 |  | 24.8 |  | 7.6 | 0.047 |  | 4.3 | 65.11 | 0.24 |  |  |  |  | 14.187 | 13.011 | [6 empty] | 36.31 |  | 15.58

## 2013
All of the data presented below was copied verbatim from spreadsheets transcribed by Debbie Rideout, Town PLO
| pH | [6 empty] | Chlorine |  |  |  | Colour | [5 empty] | Turbidity | [5 empty] | Total Dissolved Solids |  |  |  |  | Conductivity |  |  |  |  | Hardness |  | Alkalinity |  | Aluminum | Temperature |  | Cl Used | Cl Demand | UVT |  | UVA |  | Flows within plant |  |  |  | Flows from plant |  |  | Chemical Dosages |  |  |  | Dennis Penney
Date | Raw | PTC | PTC (OL) | SWC | Filter | Finish (OL) | Finish | Free | Total | Sample | Analyzer | Raw A | Raw T | SWC A | Filter A | Finish A | Finish T | Raw | Raw (OL) | SWC | Filter | Finish | Finish (OL) | Raw | PTC | SWC | Filter | Finish | Raw | PTC | SWC | Filter | Finish | Raw | Finish | Raw | Finish | Finish (Free) | Raw | Finish |  |  | Raw | Filter | Raw | Filter | Raw | Finish | Filter | Backwash | Bishop's | Botwood | GFW | Chlorine | Alum | Lime (Pre) | Lime (Post) | Jerry Loveless
2013-01-01 | 5.29 | 5.03 |  |  |  |  | 7.46 | 2.11 |  |  |  |  | 45 |  |  |  | 0 | 0.298 |  |  | 0.108 | 0.387 | [5 empty] | 36.4 |  |  |  |  | 72.8 |  | 26.3 |  | 6.7 | 0.074 |  | 4.3 | 70.56 | 0.37 |  |  |  |  | 14.13 | 12.93 | [6 empty] | 35.91 |  | 15.23 | Noland Simms
2013-01-02 | 6.39 | 5.11 |  |  |  |  | 7.37 | 1.9 |  |  |  |  | 42 |  |  |  | 0 | 0.298 |  |  | 0.077 | 0.383 | [5 empty] | 34.8 |  |  |  |  | 69.6 |  | 26 |  | 8.2 | 0.086 |  | 4.2 | 65.47 | 0.47 |  |  |  |  | 13.361 | 12.566 | [6 empty] | 33.33 |  | 17.66
2013-01-03 | 6.1 | 5.36 |  |  |  |  | 8.32 | 1.78 |  |  |  |  | 40 |  |  |  | 0 | 0.29 |  |  | 0.08 | 0.388 | [5 empty] | 37.1 |  |  |  |  | 74.4 |  | 25.8 |  | 10.7 | 0.129 |  | 4.3 | 75.28 | 0.72 |  |  |  |  | 14.405 | 13.669 | [6 empty] | 30.98 |  | 16.38
2013-01-04 | 6.09 | 5.45 |  |  |  |  | 7.84 | 1.88 |  |  |  |  | 37 |  |  |  | 0 | 0.284 |  |  | 0.064 | 0.388 | [5 empty] | 35.4 |  |  |  |  | 70.8 |  | 26.3 |  | 9.6 | 0.099 |  | 4.1 | 69.92 | 0.5 |  |  |  |  | 14.555 | 13.312 | [6 empty] | 29.79 |  | 16.08 | Continuous
2013-01-05 | 6 | 5.37 |  |  |  |  | 7.85 | 1.86 |  |  |  |  | 31 |  |  |  | 0 | 0.287 |  |  | 0.057 | 0.389 | [5 empty] | 34.9 |  |  |  |  | 69.9 |  | 23.3 |  | 9.7 | 0.084 |  | 4.1 | 70.41 | 0.61 |  |  |  |  | 13.19 | 12.96 | [6 empty] | 31.49 |  | 16.43 | Grab
2013-01-06 | 6.045 | 5.41 |  |  |  |  | 7.845 | 1.87 |  |  |  |  | 34 |  |  |  | 0 | 0.2855 |  |  | 0.0605 | 0.3885 | [5 empty] | 35.15 |  |  |  |  | 70.35 |  | 24.8 |  | 9.65 | 0.0915 |  | 4.1 | 70.165 | 0.555 |  |  |  |  | 13.8725 | 13.136 | [6 empty] | 30.64 |  | 16.255 | ^ Stuff for form dropdown menus
2013-01-07 | 6.18 | 5.51 |  |  |  |  | 7.79 | 1.81 |  |  |  |  | 43 |  |  |  | 0 | 0.287 |  |  | 0.082 | 0.388 | [5 empty] | 36.5 |  |  |  |  | 73.1 |  | 22.6 |  | 9.8 | 0.117 |  | 4.2 | 69.79 | 0.68 |  |  |  |  | 14.49 | 12.735 | [6 empty] | 34.74 |  | 17.26
2013-01-08 | 5.9 | 5.04 |  |  |  |  | 7.8 | 1.76 |  |  |  |  | 37 |  |  |  | 0 | 0.278 |  |  | 0.082 | 0.387 | [5 empty] | 36.7 |  |  |  |  | 73.6 |  | 26.4 |  | 9.7 | 0.108 |  | 4.1 | 69.96 | 0.56 |  |  |  |  | 14.446 | 13.675 | [6 empty] | 32.86 |  | 15.53
2013-01-09 | 6.01 | 5.03 |  |  |  |  | 7.88 | 1.71 |  |  |  |  | 30 |  |  |  | 0 | 0.243 |  |  | 0.096 | 0.367 | [5 empty] | 35.9 |  |  |  |  | 71.8 |  | 25.6 |  | 9.1 | 0.112 |  | 4 | 70.85 | 0.75 |  |  |  |  | 13.977 | 13.091 | [6 empty] | 31.34 |  | 14.66
2013-01-10 | 5.94 | 5.13 |  |  |  |  | 7.88 | 1.76 |  |  |  |  | 33 |  |  |  | 0 | 0.267 |  |  | 0.097 | 0.394 | [5 empty] | 34.4 |  |  |  |  | 68.8 |  | 26.4 |  | 8.8 | 0.097 |  | 4 | 65.71 | 0.55 |  |  |  |  | 13.719 | 12.936 | [6 empty] | 32.51 |  | 15.2
2013-01-11 | 5.38 | 4.92 |  |  |  |  | 7.2 | 1.78 |  |  |  |  | 35 |  |  |  | 0 | 0.276 |  |  | 0.131 | 0.398 | [5 empty] | 36.6 |  |  |  |  | 73.2 |  | 25.9 |  | 7.9 | 0.099 |  | 4.1 | 68.28 | 0.65 |  |  |  |  | 13.481 | 11.923 | [6 empty] | 33.79 |  | 15.24
2013-01-12 | 5.43 | 4.94 |  |  |  |  | 6.87 | 2.3 |  |  |  |  | 37 |  |  |  | 0 | 0.262 |  |  | 0.118 | 0.218 | [5 empty] | 34 |  |  |  |  | 68 |  | 24.7 |  | 7.4 | 0.087 |  | 3.9 | 66.995 | 0.6 |  |  |  |  | 14.614 | 13.321 | [6 empty] | 32.84 |  | 16.21
2013-01-13 | 5.53 | 4.89 |  |  |  |  | 7.35 | 2.12 |  |  |  |  | 36 |  |  |  | 0 | 0.258 |  |  | 0.086 | 0.147 | [5 empty] | 36.9 |  |  |  |  | 73.8 |  | 23.8 |  | 7.1 | 0.053 |  | 3.9 | 67.6375 | 0.625 |  |  |  |  | 13.714 | 12.906 | [6 empty] | 32.81 |  | 16.08
2013-01-14 | 5.74 | 5.2 |  |  |  |  | 7.95 | 1.73 |  |  |  |  | 38 |  |  |  | 0 | 0.276 |  |  | 0.074 | 0.271 | [5 empty] | 35.9 |  |  |  |  | 71.8 |  | 23 |  | 6.8 | 0.049 |  | 4 | 70 | 0.79 |  |  |  |  | 13.552 | 12.642 | [6 empty] | 32.6 |  | 15.9
2013-01-15 | 6.02 | 5.18 |  |  |  |  | 8.11 | 1.96 |  |  |  |  | 33 |  |  |  | 0 | 0.241 |  |  | 0.102 | 0.154 | [5 empty] | 33.7 |  |  |  |  | 67.4 |  | 23.7 |  | 6.9 | 0.061 |  | 4.1 | 70 | 0.49 |  |  |  |  | 14.737 | 12.989 | [6 empty] | 32.11 |  | 16.31
2013-01-16 | 5.56 | 5.2 |  |  |  |  | 7.52 | 1.88 |  |  |  |  | 36 |  |  |  | 0 | 0.248 |  |  | 0.094 | 0.117 | [5 empty] | 36.8 |  |  |  |  | 73.6 |  | 24.9 |  | 6.7 | 0.053 |  | 4.2 | 60 | 0.25 |  |  |  |  | 13.605 | 12.771 | [6 empty] | 32.45 |  | 15.59
2013-01-17 | 5.53 | 5.13 |  |  |  |  | 7.18 | 1.92 |  |  |  |  | 37 |  |  |  | 0 | 0.247 |  |  | 0.098 | 0.114 | [5 empty] | 36.3 |  |  |  |  | 72.6 |  | 25.4 |  | 6.9 | 0.068 |  | 3.9 | 80 | 0.81 |  |  |  |  | 13.61 | 13.29 | [6 empty] | 33.73 |  | 15.69
2013-01-18 | 6.56 | 4.87 |  |  |  |  | 7.35 | 1.8 |  |  |  |  | 34 |  |  |  | 0 | 0.25 |  |  | 0.079 | 0.123 | [5 empty] | 36.6 |  |  |  |  | 73.3 |  | 23.5 |  | 11.5 | 0.235 |  | 4 | 80 | 0.79 |  |  |  |  | 15.422 | 14.029 | [6 empty] | 31.45 |  | 16.86
2013-01-19 | 6.38 | 5.12 |  |  |  |  | 7.09 | 1.78 |  |  |  |  | 35 |  |  |  | 0 | 0.256 |  |  | 0.077 | 0.132 | [5 empty] | 35.7 |  |  |  |  | 71.5 |  | 25.2 |  | 10.6 | 0.181 |  | 4 | 80 | 0.8 |  |  |  |  | 14.3 | 12.96 | [6 empty] | 33.33 |  | 17.65
2013-01-20 | 6.47 | 4.995 |  |  |  |  | 7.22 | 1.87 |  |  |  |  | 34.5 |  |  |  | 0 | 0.253 |  |  | 0.078 | 0.1275 | [5 empty] | 36.15 |  |  |  |  | 72.4 |  | 24.35 |  | 11.05 | 0.208 |  | 4 | 80 | 0.795 |  |  |  |  | 13.762 | 13.388 | [6 empty] | 32.39 |  | 17.255
2013-01-21 | 5.53 | 5.91 |  |  |  |  | 8.38 | 1.91 |  |  |  |  | 36 |  |  |  | 0 | 0.247 |  |  | 0.096 | 0.138 | [5 empty] | 41.1 |  |  |  |  | 82.2 |  | 24.6 |  | 10.8 | 0.163 |  | 3.8 | 80 | 0.82 |  |  |  |  | 14.606 | 13.314 | [6 empty] | 26.8 |  | 19.53
2013-01-22 | 5.51 | 5.53 |  |  |  |  | 8.05 | 1.78 |  |  |  |  | 35 |  |  |  | 0 | 0.248 |  |  | 0.101 | 0.124 | [5 empty] | 39.4 |  |  |  |  | 78.8 |  | 25.4 |  | 10.6 | 0.098 |  | 3.8 | 60 | 0.38 |  |  |  |  | 13.95 | 12.62 | [6 empty] | 34.41 |  | 17.45
2013-01-23 | 5.65 | 5.2 |  |  |  |  | 6.54 | 1.87 |  |  |  |  | 34 |  |  |  | 0 | 0.249 |  |  | 0.084 | 0.2 | [5 empty] | 34.8 |  |  |  |  | 69.5 |  | 26 |  | 8.8 | 0.034 |  | 3.8 | 80 | 0.98 |  |  |  |  | 14.21 | 12.759 | [6 empty] | 31.92 |  | 13.2
2013-01-24 | 6.21 | 5.1 |  |  |  |  | 7.45 | 1.87 |  |  |  |  | 35 |  |  |  | 0 | 0.247 |  |  | 0.092 | 0.115 | [5 empty] | 38.1 |  |  |  |  | 76.2 |  | 24.8 |  | 10.9 | 0.051 |  | 4 | 70 | 0.68 |  |  |  |  | 14.296 | 13.463 | [6 empty] | 31.92 |  | 18.21
2013-01-25 | 6.17 | 5.15 |  |  |  |  | 6.26 | 1.78 |  |  |  |  | 32 |  |  |  | 0 | 0.231 |  |  | 0.064 | 0.132 | [5 empty] | 38.1 |  |  |  |  | 76.2 |  | 24.6 |  | 9.7 | 0.048 |  | 3.9 | 75 | 0.83 |  |  |  |  | 14.1 | 13.331 | [6 empty] | 30.7 |  | 16.35
2013-01-26 | 6.02 | 5.15 |  |  |  |  | 7.07 | 1.91 |  |  |  |  | 40 |  |  |  | 0 | 0.239 |  |  | 0.077 | 0.137 | [5 empty] | 36.4 |  |  |  |  | 77.6 |  | 26.5 |  | 8.2 | 0.071 |  | 3.9 | 72.5 | 0.755 |  |  |  |  | 14.63 | 13.32 | [6 empty] | 32.72 |  | 17.47
2013-01-27 | 6.095 | 5.15 |  |  |  |  | 6.665 | 1.845 |  |  |  |  | 36 |  |  |  | 0 | 0.235 |  |  | 0.0705 | 0.1345 | [5 empty] | 37.25 |  |  |  |  | 76.9 |  | 25.55 |  | 8.95 | 0.0595 |  | 3.9 | 73.75 | 0.7925 |  |  |  |  | 14.365 | 13.3255 | [6 empty] | 31.71 |  | 16.91
2013-01-28 | 6.4 | 4.83 |  |  |  |  | 5.35 | 1.79 |  |  |  |  | 41 |  |  |  | 0 | 0.252 |  |  | 0.117 | 0.417 | [5 empty] | 26.5 |  |  |  |  | 53 |  | 25.5 |  | 4.1 | 0.226 |  | 3.8 | 80 | 0.97 |  |  |  |  | 14.94 | 13.167 | [6 empty] | 31.92 |  | 16.1
2013-01-29 | 5.77 | 5.34 |  |  |  |  | 8.54 | 1.8 |  |  |  |  | 38 |  |  |  | 0 | 0.243 |  |  | 0.111 | 0.126 | [5 empty] | 38.3 |  |  |  |  | 76.6 |  | 26.8 |  | 6.525 | 0.14275 |  | 3.85 | 76.875 | 0.88125 |  |  |  |  | 14.552 | 13.802 | [6 empty] | 31.815 |  | 16.505
2013-01-30 | 5.94 | 5.71 |  |  |  |  | 7.91 | 1.795 |  |  |  |  | 35 |  |  |  | 0 | 0.245 |  |  | 0.091 | 0.121 | [5 empty] | 37.2 |  |  |  |  | 74.4 |  | 25.1 |  | 10.1 | 0.082 |  | 3.9 | 78.4375 | 0.92562 |  |  |  |  | 15.264 | 13.986 | [6 empty] | 32.35 |  | 16.46
2013-01-31 | 6.1 | 5.6 |  |  |  |  | 6.29 | 1.65 |  |  |  |  | 38 |  |  |  | 0 | 0.247 |  |  | 0.127 | 0.176 | [5 empty] | 32.9 |  |  |  |  | 65.8 |  | 23.4 |  | 6.4 | 0.143 |  | 3.9 | 70 | 0.67 |  |  |  |  | 14.556 | 13.726 | [6 empty] | 34.89 |  | 13.08
2013-02-01 | 5.3 | 5.37 |  |  |  |  | 6.72 | 1.73 |  |  |  |  | 39 |  |  |  | 0 | 0.238 |  |  | 0.167 | 0.4 | [5 empty] | 29.5 |  |  |  |  | 59 |  | 24.8 |  | 6.7 | 0.113 |  | 3.7 | 70 | 0.7 |  |  |  |  | 14.417 | 13.07 | [6 empty] | 30.73 |  | 16.59
2013-02-02 | 5.67 | 5.24 |  |  |  |  | 7.8 | 1.78 |  |  |  |  | 38 |  |  |  | 0 | 0.238 |  |  | 0.163 | 0.124 | [5 empty] | 34.6 |  |  |  |  | 69.2 |  | 24.9 |  | 7.4 | 0.083 |  | 3.8 | 90 | 1.18 |  |  |  |  | 14.655 | 13.787 | [6 empty] | 30.96 |  | 16.49
2013-02-03 | 5.485 | 5.305 |  |  |  |  | 7.26 | 1.755 |  |  |  |  | 38.5 |  |  |  | 0 | 0.238 |  |  | 0.165 | 0.262 | [5 empty] | 32.05 |  |  |  |  | 64.1 |  | 24.85 |  | 7.05 | 0.098 |  | 3.75 | 80 | 0.94 |  |  |  |  | 14.536 | 13.4285 | [6 empty] | 30.845 |  | 16.54
2013-02-04 | 5.95 | 5.03 |  |  |  |  | 7.34 | 1.68 |  |  |  |  | 37 |  |  |  | 0 | 0.317 |  |  | 0.123 | 0.115 | [5 empty] | 38.6 |  |  |  |  | 77.2 |  | 28.5 |  | 9.8 | 0.081 |  | 3.8 | 60 | 0.44 |  |  |  |  | 14.37 | 12.87 | [6 empty] | 33.8 |  | 18.1
2013-02-05 | 6.01 | 5.13 |  |  |  |  | 6.99 | 1.67 |  |  |  |  | 37 |  |  |  | 0 | 0.291 |  |  | 0.086 | 0.145 | [5 empty] | 46.5 |  |  |  |  | 93.1 |  | 25.2 |  | 11.1 | 0.129 |  | 4.4 | 70 | 0.72 |  |  |  |  | 14.583 | 13.31 | [6 empty] | 31.45 |  | 17.3
2013-02-06 | 5.25 | 5.14 |  |  |  |  | 7.18 | 1.59 |  |  |  |  | 38 |  |  |  | 1 | 0.274 |  |  | 0.085 | 0.709 | [5 empty] | 38.9 |  |  |  |  | 77.8 |  | 25.7 |  | 7.4 | 0.121 |  | 3.7 | 80 | 0.98 |  |  |  |  | 14.954 | 14.155 | [6 empty] | 31.59 |  | 18.53
2013-02-07 | 5.46 | 5.03 |  |  |  |  | 8.07 | 1.67 |  |  |  |  | 38 |  |  |  | 1 | 0.208 |  |  | 0.11 | 0.826 | [5 empty] | 38.7 |  |  |  |  | 77.4 |  | 24.5 |  | 9.2 | 0.118 |  | 3.7 | 70 | 0.54 |  |  |  |  | 15.66 | 14.39 | [6 empty] | 33.67 |  | 18.42
2013-02-08 | 6.54 | 5.47 |  |  |  |  | 7.05 | 1.63 |  |  |  |  | 38 |  |  |  | 0 | 0.272 |  |  | 0.096 | 0.368 | [5 empty] | 40.2 |  |  |  |  | 80.4 |  | 23.8 |  | 11.5 | 0.081 |  | 3.7 | 70 | 0.74 |  |  |  |  | 14.65 | 13.4 | [6 empty] | 32.86 |  | 20.66
2013-02-09 | 6.39 | 5.41 |  |  |  |  | 8.32 | 1.52 |  |  |  |  | 37 |  |  |  | 0 | 0.274 |  |  | 0.091 | 0.336 | [5 empty] | 38.8 |  |  |  |  | 77.5 |  | 24.4 |  | 11.2 | 0.076 |  | 3.8 | 70 | 0.64 |  |  |  |  | 14.12 | 13.76 | [6 empty] | 32.86 |  | 17.44
2013-02-10 | 6.465 | 5.44 |  |  |  |  | 7.685 | 1.575 |  |  |  |  | 37.5 |  |  |  | 0 | 0.273 |  |  | 0.0935 | 0.352 | [5 empty] | 39.5 |  |  |  |  | 78.95 |  | 24.1 |  | 11.35 | 0.0785 |  | 3.75 | 70 | 0.69 |  |  |  |  | 14.385 | 13.58 | [6 empty] | 32.86 |  | 17.44
2013-02-11 | 5.64 | 4.72 |  |  |  |  | 6.9 | 1.51 |  |  |  |  | 38 |  |  |  | 1 | 0.265 |  |  | 0.107 | 0.468 | [5 empty] | 39.2 |  |  |  |  | 78.4 |  | 24.8 |  | 6.1 | 0.118 |  | 3.7 | 80 | 1.08 |  |  |  |  | 16.228 | 13.98 | [6 empty] | 32.09 |  | 18.42
2013-02-12 | 5.32 | 5.54 |  |  |  |  | 8.3 | 1.78 |  |  |  |  | 37 |  |  |  | 0 | 0.256 |  |  | 0.091 | 0.293 | [5 empty] | 39.3 |  |  |  |  | 78.6 |  | 23.7 |  | 9.1 | 0.083 |  | 3.8 | 70 | 0.57 |  |  |  |  | 14.96 | 13.55 | [6 empty] | 32.66 |  | 19.84
2013-02-13 | 6.43 | 5.24 |  |  |  |  | 7.99 | 1.73 |  |  |  |  | 34 |  |  |  | 0 | 0.257 |  |  | 0.109 | 0.384 | [5 empty] | 42.1 |  |  |  |  | 84.2 |  | 26.5 |  | 10.1 | 0.086 |  | 3.7 | 70 | 0.7 |  |  |  |  | 14.37 | 13.09 | [6 empty] | 30.51 |  | 18.23
2013-02-14 | 5.83 | 5.27 |  |  |  |  | 6.67 | 1.76 |  |  |  |  | 36 |  |  |  | 0 | 0.251 |  |  | 0.078 | 0.383 | [5 empty] | 37.8 |  |  |  |  | 75.5 |  | 24.5 |  | 9.8 | 0.084 |  | 3.7 | 70 | 0.635 |  |  |  |  | 14.873 | 13.277 | [6 empty] | 33.8 |  | 19.89
2013-02-15 | 5.75 | 5.85 |  |  |  |  | 6.72 | 1.76 |  |  |  |  | 43 |  |  |  | 0 | 0.246 |  |  | 0.397 | 0.374 | [5 empty] | 35.5 |  |  |  |  | 71 |  | 26.3 |  | 8.4 | 0.143 |  | 3.7 | 60 | 0.23 |  |  |  |  | 14.499 | 13.692 | [6 empty] | 18.9 |  | 33.2
2013-02-16 | 5.64 | 5.02 |  |  |  |  | 7.18 | 1.86 |  |  |  |  | 36 |  |  |  | 0 | 0.246 |  |  | 0.114 | 0.361 | [5 empty] | 32.9 |  |  |  |  | 65.8 |  | 25.4 |  | 6.9 | 0.094 |  | 3.8 | 65 | 6.3 |  |  |  |  | 14.95 | 13.67 | [6 empty] | 33.28 |  | 14.25
2013-02-17 | 5.695 | 5.435 |  |  |  |  | 6.95 | 1.81 |  |  |  |  | 39.5 |  |  |  | 0 | 0.246 |  |  | 0.2555 | 0.3675 | [5 empty] | 34.2 |  |  |  |  | 68.4 |  | 25.85 |  | 7.65 | 0.1185 |  | 3.75 | 62.5 | 3.265 |  |  |  |  | 14.7245 | 13.681 | [6 empty] | 26.09 |  | 23.725
2013-02-18 | 6.32 | 4.87 |  |  |  |  | 7.14 | 1.82 |  |  |  |  | 36 |  |  |  | 0 | 0.25 |  |  | 0.111 | 0.41 | [5 empty] | 37.6 |  |  |  |  | 75.3 |  | 26.3 |  | 9.4 | 0.059 |  | 3.7 | 80 | 0.98 |  |  |  |  | 14.053 | 12.963 | [6 empty] | 32.39 |  | 17.71
2013-02-19 | 6.23 | 5.27 |  |  |  |  | 7.12 | 1.86 |  |  |  |  | 36 |  |  |  | 0 | 0.246 |  |  | 0.078 | 0.383 | [5 empty] | 37.6 |  |  |  |  | 75.2 |  | 23.3 |  | 9.6 | 0.048 |  | 3.6 | 71.25 | 2.1225 |  |  |  |  | 14.533 | 13.312 | [6 empty] | 33.33 |  | 17.47
2013-02-20 | 6.09 | 5.24 |  |  |  |  | 7.1 | 1.78 |  |  |  |  | 32 |  |  |  | 0 | 0.231 |  |  | 0.109 | 0.276 | [5 empty] | 36.9 |  |  |  |  | 73.8 |  | 22.9 |  | 9.2 | 0.057 |  | 3.6 | 75.625 | 1.5513 |  |  |  |  | 14.382 | 13.112 | [6 empty] | 34.24 |  | 15.94
2013-02-21 | 6.18 | 5.24 |  |  |  |  | 7.17 | 1.8 |  |  |  |  | 40 |  |  |  | 0 | 0.238 |  |  | 0.126 | 0.256 | [5 empty] | 36.6 |  |  |  |  | 73.2 |  | 24.6 |  | 8.8 | 0.061 |  | 3.5 | 70 | 0.6 |  |  |  |  | 14.462 | 13.126 | [6 empty] | 32.73 |  | 15.29
2013-02-22 | 5.57 | 5.28 |  |  |  |  | 7.33 | 1.6 |  |  |  |  | 39 |  |  |  | 0 | 0.237 |  |  | 0.131 | 0.218 | [5 empty] | 37.8 |  |  |  |  | 75.6 |  | 23.8 |  | 8.1 | 0.056 |  | 3.8 | 80 | 1.1 |  |  |  |  | 14.7052 | 13.439 | [6 empty] | 35.45 |  | 15.95
2013-02-23 | 5.52 | 5.35 |  |  |  |  | 7.28 | 1.46 |  |  |  |  | 39.5 |  |  |  | 0 | 0.239 |  |  | 0.139 | 0.198 | [5 empty] | 36.4 |  |  |  |  | 72.8 |  | 24.7 |  | 8.4 | 0.069 |  | 3.4 | 75 | 0.85 |  |  |  |  | 14.548 | 13.843 | [6 empty] | 33.56 |  | 15.2
2013-02-24 | 5.545 | 5.315 |  |  |  |  | 7.305 | 1.53 |  |  |  |  | 39.25 |  |  |  | 0 | 0.238 |  |  | 0.135 | 0.208 | [5 empty] | 37.1 |  |  |  |  | 74.2 |  | 24.25 |  | 8.25 | 0.0625 |  | 3.6 | 77.5 | 0.975 |  |  |  |  | 13.896 | 13.177 | [6 empty] | 34.505 |  | 15.575
2013-02-25 | 5.49 | 5.24 |  |  |  |  | 7.5 | 1.495 |  |  |  |  | 37 |  |  |  | 0 | 0.224 |  |  | 0.121 | 0.231 | [5 empty] | 35.9 |  |  |  |  | 71.9 |  | 25 |  | 8.4 | 0.071 |  | 3.3 | 76.25 | 0.9125 |  |  |  |  | 14.612 | 13.269 | [6 empty] | 32.425 |  | 16.62
2013-02-26 | 5.64 | 5.19 |  |  |  |  | 7.96 | 1.57 |  |  |  |  | 40 |  |  |  | 0 | 0.227 |  |  | 0.149 | 0.177 | [5 empty] | 35.2 |  |  |  |  | 70.4 |  | 23.8 |  | 8.7 | 0.063 |  | 3.4 | 90 | 1.38 |  |  |  |  | 14.665 | 13.83 | [6 empty] | 33.4 |  | 15.78
2013-02-27 | 5.51 | 5.08 |  |  |  |  | 8.44 | 1.5325 |  |  |  |  | 41 |  |  |  | 0 | 0.224 |  |  | 0.143 | 0.198 | [5 empty] | 36.8 |  |  |  |  | 73.6 |  | 23.8 |  | 8.4 | 0.072 |  | 3.7 | 70 | 1.1462 |  |  |  |  | 14.157 | 13.237 | [6 empty] | 31.12 |  | 16.43
2013-02-28 | 5.62 | 5.16 |  |  |  |  | 6.48 | 1.47 |  |  |  |  | 42 |  |  |  | 1 | 0.216 |  |  | 0.183 | 0.634 | [5 empty] | 31 |  |  |  |  | 62 |  | 24.9 |  | 6.2 | 0.143 |  | 3.5 | 70 | 0.91 |  |  |  |  | 15.12 | 13.36 | [6 empty] | 35.99 |  | 16.27
2013-03-01 | 5.565 | 5.12 |  |  |  |  | 7.46 | 1.5013 |  |  |  |  | 41.5 |  |  |  | 0.5 | 0.22 |  |  | 0.163 | 0.416 | [5 empty] | 33.9 |  |  |  |  | 67.8 |  | 24.35 |  | 7.3 | 0.1075 |  | 3.6 | 70 | 1.0281 |  |  |  |  | 14.6385 | 13.2985 | [6 empty] | 33.555 |  | 16.35
2013-03-02 | 6.26 | 5.3 |  |  |  |  | 8.47 | 1.63 |  |  |  |  | 38 |  |  |  | 0 | 0.222 |  |  | 0.177 | 0.219 | [5 empty] | 30.9 |  |  |  |  | 61.7 |  | 24.7 |  | 8.4 | 0.139 |  | 3.6 | 60 | 0.4 |  |  |  |  | 14.241 | 13.401 | [6 empty] | 31.45 |  | 19.72
2013-03-03 | 6.55 | 5.29 |  |  |  |  | 7.75 | 1.64 |  |  |  |  | 36 |  |  |  | 0 | 0.221 |  |  | 0.189 | 0.206 | [5 empty] | 31.1 |  |  |  |  | 62.3 |  | 23.9 |  | 8.6 | 0.142 |  | 3.7 | 65 | 0.71406 |  |  |  |  | 14.09 | 12.78 | [6 empty] | 31.92 |  | 18.99
2013-03-04 | 6.405 | 5.295 |  |  |  |  | 8.11 | 1.635 |  |  |  |  | 37 |  |  |  | 0 | 0.2215 |  |  | 0.183 | 0.2125 | [5 empty] | 31 |  |  |  |  | 62 |  | 24.3 |  | 8.5 | 0.1405 |  | 3.65 | 62.5 | 0.55703 |  |  |  |  | 14.106 | 12.727 | [6 empty] | 31.92 |  | 18.99
2013-03-05 | 5.13 | 4.85 |  |  |  |  | 6.93 | 1.53 |  |  |  |  | 34 |  |  |  | 3 | 0.226 |  |  | 0.16 | 0.591 | [5 empty] | 34.5 |  |  |  |  | 69 |  | 23.9 |  | 7.6 | 0.02 |  | 3.4 | 80 | 1.02 |  |  |  |  | 14.596 | 13.283 | [6 empty] | 39.33 |  | 18.56
2013-03-06 | 5.29 | 5.52 |  |  |  |  | 6.67 | 1.6 |  |  |  |  | 35 |  |  |  | 0 | 0.287 |  |  | 0.173 | 0.249 | [5 empty] | 37.9 |  |  |  |  | 75.8 |  | 24.5 |  | 7.4 | 0.041 |  | 3.3 | 60 | 0.44 |  |  |  |  | 14.13 | 13.35 | [6 empty] | 26.94 |  | 15.89
2013-03-07 | 5.78 | 5.1 |  |  |  |  | 6.88 | 1.6 |  |  |  |  | 40 |  |  |  | 0 | 0.262 |  |  | 0.134 | 0.169 | [5 empty] | 38.5 |  |  |  |  | 77 |  | 26.7 |  | 7.8 | 0.04 |  | 3.4 | 80 | 1.23 |  |  |  |  | 14.217 | 12.823 | [6 empty] | 27.7 |  | 18.12
2013-03-08 | 6.11 | 5.05 |  |  |  |  | 7.33 | 1.61 |  |  |  |  | 39 |  |  |  | 0 | 0.249 |  |  | 0.124 | 0.145 | [5 empty] | 35.1 |  |  |  |  | 70.3 |  | 23 |  | 8.2 | 0.051 |  | 3.5 | 70 | 0.835 |  |  |  |  | 14.942 | 14.129 | [6 empty] | 27.23 |  | 17.89
2013-03-09 | 5.99 | 5.08 |  |  |  |  | 7.28 | 1.61 |  |  |  |  | 40 |  |  |  | 0 | 0.239 |  |  | 0.141 | 0.227 | [5 empty] | 34.9 |  |  |  |  | 69.8 |  | 23.8 |  | 7.7 | 0.061 |  | 3.4 | 75 | 1.0325 |  |  |  |  | 14.402 | 13.597 | [6 empty] | 30.83 |  | 17.7
2013-03-10 | 6.09 | 5.014 |  |  |  |  | 7.34 | 1.61 |  |  |  |  | 37 |  |  |  | 0 | 0.234 |  |  | 0.143 | 0.21 | [5 empty] | 34.2 |  |  |  |  | 68.4 |  | 26.3 |  | 7.2 | 0.064 |  | 3.4 | 75 | 1.02 |  |  |  |  | 14.26 | 12.94 | [6 empty] | 33.13 |  | 19.34
2013-03-11 | 6.04 | 5.047 |  |  |  |  | 7.31 | 1.61 |  |  |  |  | 38.5 |  |  |  | 0 | 0.2365 |  |  | 0.142 | 0.2185 | [5 empty] | 34.55 |  |  |  |  | 69.1 |  | 25.05 |  | 7.45 | 0.0625 |  | 3.4 | 75 | 1.0263 |  |  |  |  | 14.331 | 13.2685 | [6 empty] | 31.98 |  | 18.52
2013-03-12 | 6.23 | 4.5 |  |  |  |  | 4.77 | 1.57 |  |  |  |  | 40 |  |  |  | 0 | 0.239 |  |  | 0.114 | 0.296 | [5 empty] | 28.7 |  |  |  |  | 57.4 |  | 20.3 |  | 2.7 | 0.189 |  | 4.1 | 90 | 1.39 |  |  |  |  | 15.527 | 13.732 | [6 empty] | 34.27 |  | 10.03
2013-03-13 | 5.73 | 5.16 |  |  |  |  | 6.13 | 1.91 |  |  |  |  | 39 |  |  |  | 0 | 0.23 |  |  | 0.082 | 0.5 | [5 empty] | 34.1 |  |  |  |  | 68.2 |  | 22.4 |  | 6.9 | 0.076 |  | 3.7 | 82.5 | 1.2081 |  |  |  |  | 15.161 | 14.388 | [6 empty] | 34.27 |  | 21.16
2013-03-14 | 5.94 | 5.38 |  |  |  |  | 8.61 | 2.22 |  |  |  |  | 37 |  |  |  | 0 | 0.229 |  |  | 0.077 | 0.21 | [5 empty] | 33.7 |  |  |  |  | 67.4 |  | 24.2 |  | 7.2 | 0.069 |  | 3.9 | 86.25 | 1.2991 |  |  |  |  | 14.57 | 14.128 | [6 empty] | 32.44 |  | 19.1
2013-03-15 | 6.79 | 5.5 |  |  |  |  | 7.94 | 2.18 |  |  |  |  | 33 |  |  |  | 0 | 0.229 |  |  | 0.074 | 0.147 | [5 empty] | 34.8 |  |  |  |  | 69.6 |  | 23.9 |  | 8.4 | 0.061 |  | 4 | 80 | 0.37 |  |  |  |  | 15.902 | 14.127 | [6 empty] | 32.23 |  | 17.65
2013-03-16 | 5.26 | 4.96 |  |  |  |  | 7.77 | 1.92 |  |  |  |  | 35 |  |  |  | 0 | 0.217 |  |  | 0.151 | 0.228 | [5 empty] | 39.9 |  |  |  |  | 79.8 |  | 24.5 |  | 8.1 | 0.076 |  | 3.6 | 70 | 0.46 |  |  |  |  | 14.19 | 13.368 | [6 empty] | 31.71 |  | 17.27
2013-03-17 | 5.13 | 5.65 |  |  |  |  | 8.24 | 2.14 |  |  |  |  | 37 |  |  |  | 0 | 0.228 |  |  | 0.121 | 0.147 | [5 empty] | 36 |  |  |  |  | 72 |  | 24.8 |  | 8.7 | 0.061 |  | 3.2 | 75 | 0.415 |  |  |  |  | 15.37 | 13.7 | [6 empty] | 32.5 |  | 17.2
2013-03-18 | 5.195 | 5.305 |  |  |  |  | 8.005 | 2.03 |  |  |  |  | 36 |  |  |  | 0 | 0.2225 |  |  | 0.136 | 0.1875 | [5 empty] | 37.95 |  |  |  |  | 75.9 |  | 24.65 |  | 8.4 | 0.0685 |  | 3.4 | 72.5 | 0.4375 |  |  |  |  | 15.188 | 13.444 | [6 empty] | 32.105 |  | 17.235
2013-03-19 | 5.9 | 5.67 |  |  |  |  | 6.86 | 2.06 |  |  |  |  | 39 |  |  |  | 0 | 0.227 |  |  | 0.107 | 0.143 | [5 empty] | 35.7 |  |  |  |  | 71.4 |  | 25.1 |  | 8 | 0.077 |  | 3.3 | 73.75 | 0.42625 |  |  |  |  | 14.743 | 13.446 | [6 empty] | 31.04 |  | 15.3
2013-03-20 | 6.09 | 5.55 |  |  |  |  | 8.33 | 2.01 |  |  |  |  | 41 |  |  |  | 0 | 0.211 |  |  | 0.113 | 0.157 | [5 empty] | 34.4 |  |  |  |  | 68.8 |  | 24.6 |  | 7.7 | 0.067 |  | 3.2 | 70 | 0.32 |  |  |  |  | 14.844 | 13.613 | [6 empty] | 29.01 |  | 14.91
2013-03-21 | 5.5 | 5.43 |  |  |  |  | 7.86 | 1.91 |  |  |  |  | 40 |  |  |  | 0 | 0.226 |  |  | 0.109 | 0.214 | [5 empty] | 32.2 |  |  |  |  | 64.4 |  | 23.8 |  | 7.1 | 0.058 |  | 3.8 | 70 | 0.71 |  |  |  |  | 13.466 | 12.152 | [6 empty] | 30.93 |  | 13.22
2013-03-22 | 5.51 | 5.76 |  |  |  |  | 7.04 | 1.94 |  |  |  |  | 42 |  |  |  | 0 | 0.217 |  |  | 0.108 | 0.174 | [5 empty] | 32.3 |  |  |  |  | 64.6 |  | 24.8 |  | 7.3 | 0.051 |  | 3.7 | 60 | 0.11 |  |  |  |  | 14 | 13.29 | [6 empty] | 29.52 |  | 16.75
2013-03-23 | 6.16 | 5.14 |  |  |  |  | 7.4 | 1.89 |  |  |  |  | 38 |  |  |  | 0 | 0.221 |  |  | 0.099 | 0.114 | [5 empty] | 35.5 |  |  |  |  | 71 |  | 23.8 |  | 9.3 | 0.117 |  | 4 | 70 | 0.57 |  |  |  |  | 14.181 | 12.936 | [6 empty] | 26.76 |  | 16.55
2013-03-24 | 6.29 | 5.31 |  |  |  |  | 7.97 | 1.76 |  |  |  |  | 37 |  |  |  | 0 | 0.214 |  |  | 0.089 | 0.116 | [5 empty] | 35.1 |  |  |  |  | 70.3 |  | 26.3 |  | 9.1 | 0.103 |  | 3.7 | 65 | 0.34 |  |  |  |  | 14.21 | 13.03 | [6 empty] | 28.14 |  | 15.98
2013-03-25 | 6.225 | 5.225 |  |  |  |  | 7.685 | 1.825 |  |  |  |  | 37.5 |  |  |  | 0 | 0.2175 |  |  | 0.094 | 0.115 | [5 empty] | 35.3 |  |  |  |  | 70.65 |  | 25.05 |  | 9.2 | 0.11 |  | 3.85 | 67.5 | 0.455 |  |  |  |  | 13.96 | 12.727 | [6 empty] | 28.64 |  | 15.98
2013-03-26 | 5.44 | 5.58 |  |  |  |  | 6.77 | 1.62 |  |  |  |  | 36 |  |  |  | 0 | 0.214 |  |  | 0.104 | 0.14 | [5 empty] | 33 |  |  |  |  | 66 |  | 25.8 |  | 7.1 | 0.084 |  | 3.8 | 70 | 0.73 |  |  |  |  | 14.767 | 13.507 | [6 empty] | 32.15 |  | 20.8
2013-03-27 | 5.42 | 4.81 |  |  |  |  | 8 | 1.61 |  |  |  |  | 37 |  |  |  | 2 | 0.217 |  |  | 0.103 | 0.243 | [5 empty] | 32.8 |  |  |  |  | 65.6 |  | 25.6 |  | 7.5 | 0.134 |  | 3.9 | 70 | 0.75 |  |  |  |  | 14.61 | 13.49 | [6 empty] | 30.33 |  | 19.18
2013-03-28 | 5.65 | 5.23 |  |  |  |  | 6.4 | 1.83 |  |  |  |  | 38 |  |  |  | 0 | 0.204 |  |  | 0.114 | 0.203 | [5 empty] | 30.5 |  |  |  |  | 61.1 |  | 23.4 |  | 8.2 | 0.121 |  | 3.4 | 70 | 0.57 |  |  |  |  | 13.99 | 13.215 | [6 empty] | 30.04 |  | 13.27
2013-03-29 | 5.95 | 5.47 |  |  |  |  | 6.9 | 1.72 |  |  |  |  | 37 |  |  |  | 0 | 0.207 |  |  | 0.081 | 0.172 | [5 empty] | 32.9 |  |  |  |  | 65.8 |  | 25.4 |  | 7.2 | 0.037 |  | 3.5 | 70 | 0.66 |  |  |  |  | 14.886 | 13.697 | [6 empty] | 29.57 |  | 22.67
2013-03-30 | 5.91 | 5.17 |  |  |  |  | 7.08 | 1.775 |  |  |  |  | 40 |  |  |  | 0 | 0.209 |  |  | 0.101 | 0.127 | [5 empty] | 33.2 |  |  |  |  | 66.4 |  | 24.8 |  | 7 | 0.079 |  | 3.5 | 70 | 0.615 |  |  |  |  | 14.024 | 13.369 | [6 empty] | 30.4 |  | 19.25
2013-03-31 | 6.02 | 5.15 |  |  |  |  | 7 | 1.72 |  |  |  |  | 44 |  |  |  | 0 | 0.204 |  |  | 0.113 | 0.147 | [5 empty] | 33.4 |  |  |  |  | 66.8 |  | 26.1 |  | 6.4 | 0.059 |  | 3.6 | 70 | 0.69 |  |  |  |  | 14.27 | 13.18 | [6 empty] | 28.836 |  | 17.91
2013-04-01 | 5.965 | 5.16 |  |  |  |  | 7.04 | 1.7475 |  |  |  |  | 42 |  |  |  | 0 | 0.2065 |  |  | 0.107 | 0.137 | [5 empty] | 33.3 |  |  |  |  | 66.6 |  | 25.45 |  | 6.7 | 0.069 |  | 3.55 | 70 | 0.6525 |  |  |  |  | 14.147 | 13.2745 | [6 empty] | 29.618 |  | 18.58
2013-04-02 | 5.91 | 4.05 |  |  |  |  | 6.1 | 1.8 |  |  |  |  | 38 |  |  |  | 0 | 0.201 |  |  | 0.099 | 0.178 | [5 empty] | 29.6 |  |  |  |  | 59.2 |  | 26.8 |  | 5.8 | 0.013 |  | 3.5 | 80 | 0.92 |  |  |  |  | 14.536 | 13.353 | [6 empty] | 28.17 |  | 23.94
2013-04-03 | 6.16 | 5.56 |  |  |  |  | 7.13 | 1.89 |  |  |  |  | 37 |  |  |  | 0 | 0.206 |  |  | 0.094 | 0.095 | [5 empty] | 32.5 |  |  |  |  | 65.1 |  | 24.1 |  | 6.2 | 0.061 |  | 3.5 | 75 | 0.78625 |  |  |  |  | 14.416 | 13.279 | [6 empty] | 29.11 |  | 14.02
2013-04-04 | 6.09 | 5.5 |  |  |  |  | 6.42 | 1.845 |  |  |  |  | 37 |  |  |  | 0 | 0.193 |  |  | 0.127 | 0.227 | [5 empty] | 33.3 |  |  |  |  | 66.6 |  | 24.3 |  | 6.4 | 0.074 |  | 3.5 | 77.5 | 0.85313 |  |  |  |  | 14.07 | 12.929 | [6 empty] | 30.68 |  | 14.74
2013-04-05 | 6.14 | 5.54 |  |  |  |  | 7.83 | 1.78 |  |  |  |  | 40 |  |  |  | 0 | 0.198 |  |  | 0.157 | 0.19 | [5 empty] | 32.6 |  |  |  |  | 65.2 |  | 23.8 |  | 6.9 | 0.069 |  | 3.5 | 70 | 0.55 |  |  |  |  | 14.879 | 13.647 | [6 empty] | 29.75 |  | 14.34
2013-04-06 | 5.55 | 5.19 |  |  |  |  | 7.24 | 1.85 |  |  |  |  | 41 |  |  |  | 0 | 0.198 |  |  | 0.116 | 0.143 | [5 empty] | 31.6 |  |  |  |  | 63.2 |  | 23.6 |  | 7 | 0.054 |  | 3.2 | 80 | 0.94 |  |  |  |  | 14.172 | 13.019 | [6 empty] | 30.71 |  | 14.03
2013-04-07 | 5.82 | 5.57 |  |  |  |  | 7.37 | 1.89 |  |  |  |  | 40 |  |  |  | 0 | 0.186 |  |  | 0.104 | 0.126 | [5 empty] | 32.8 |  |  |  |  | 65.6 |  | 24.8 |  | 6.8 | 0.071 |  | 3.6 | 75 | 0.745 |  |  |  |  | 14.49 | 13.43 | [6 empty] | 38.82 |  | 12.19
2013-04-08 | 5.685 | 5.38 |  |  |  |  | 7.305 | 1.71 |  |  |  |  | 40.5 |  |  |  | 0 | 0.192 |  |  | 0.11 | 0.1345 | [5 empty] | 32.2 |  |  |  |  | 64.4 |  | 24.2 |  | 6.9 | 0.0625 |  | 3.4 | 77.5 | 0.8425 |  |  |  |  | 14.116 | 12.982 | [6 empty] | 34.765 |  | 13.11
2013-04-09 | 6.01 | 5.24 |  |  |  |  | 9.11 | 1.93 |  |  |  |  | 37 |  |  |  | 0 | 0.217 |  |  | 0.097 | 0.114 | [5 empty] | 33.7 |  |  |  |  | 67.4 |  | 24.2 |  | 7.4 | 0.067 |  | 3.6 | 76.25 | 0.79375 |  |  |  |  | 15.184 | 13.028 | [6 empty] | 35.13 |  | 14.14
2013-04-10 | 5.89 | 5.45 |  |  |  |  | 8.16 | 1.79 |  |  |  |  | 34 |  |  |  | 0 | 0.187 |  |  | 0.091 | 0.117 | [5 empty] | 31.9 |  |  |  |  | 63.8 |  | 25.7 |  | 8 | 0.074 |  | 3.7 | 76.875 | 0.81812 |  |  |  |  | 14.209 | 12.075 | [6 empty] | 34.6 |  | 14.88
2013-04-11 | 5.29 | 5.45 |  |  |  |  | 7.84 | 1.84 |  |  |  |  | 32 |  |  |  | 0 | 0.174 |  |  | 0.121 | 0.104 | [5 empty] | 30.3 |  |  |  |  | 60.6 |  | 25.9 |  | 8.3 | 0.081 |  | 3.6 | 70 | 0.62 |  |  |  |  | 14.089 | 12.917 | [6 empty] | 26.99 |  | 13.47
2013-04-12 | 5.59 | 5.48 |  |  |  |  | 7.34 | 1.91 |  |  |  |  | 34 |  |  |  | 0 | 0.164 |  |  | 0.104 | 0.148 | [5 empty] | 32.9 |  |  |  |  | 65.8 |  | 24.9 |  | 7.6 | 0.072 |  | 3.7 | 70 | 0.45 |  |  |  |  | 14.26 | 13.46 | [6 empty] | 26.65 |  | 13.21
2013-04-13 | 5.94 | 5.75 |  |  |  |  | 8.24 | 1.89 |  |  |  |  | 31 |  |  |  | 0 | 0.177 |  |  | 0.099 | 0.082 | [5 empty] | 32.2 |  |  |  |  | 64.5 |  | 25.4 |  | 8.2 | 0.066 |  | 3.9 | 70 | 0.58 |  |  |  |  | 14.323 | 12.878 | [6 empty] | 27.23 |  | 14.39
2013-04-14 | 6.06 | 5.37 |  |  |  |  | 7.53 | 1.87 |  |  |  |  | 32 |  |  |  | 0 | 0.173 |  |  | 0.093 | 0.102 | [5 empty] | 32.6 |  |  |  |  | 65.3 |  | 25.7 |  | 8.3 | 0.064 |  | 3.4 | 70 | 0.51 |  |  |  |  | 14.49 | 13.35 | [6 empty] | 25.82 |  | 13.39
2013-04-15 | 6 | 5.56 |  |  |  |  | 7.885 | 1.81 |  |  |  |  | 31.5 |  |  |  | 0 | 0.175 |  |  | 0.096 | 0.092 | [5 empty] | 32.4 |  |  |  |  | 64.9 |  | 25.55 |  | 8.25 | 0.065 |  | 3.65 | 70 | 0.545 |  |  |  |  | 13.793 | 12.664 | [6 empty] | 26.525 |  | 13.89
2013-04-16 | 5.83 | 5.49 |  |  |  |  | 7.57 | 1.83 |  |  |  |  | 33 |  |  |  | 0 | 0.184 |  |  | 0.117 | 0.104 | [5 empty] | 31.7 |  |  |  |  | 63.4 |  | 24.7 |  | 7.9 | 0.071 |  |  | 70 | 0.59 |  |  |  |  | 14.972 | 13.118 | [6 empty] | 28.21 |  | 13.24
2013-04-17 | 5.85 | 5.53 |  |  |  |  | 6.54 | 1.85 |  |  |  |  | 32 |  |  |  | 0 | 0.184 |  |  | 0.184 | 0.176 | [5 empty] | 30.6 |  |  |  |  | 61.2 |  | 24.9 |  | 6.4 | 0.093 |  | 3.7 | 70 | 0.5 |  |  |  |  | 15.39 | 13.55 | [6 empty] | 29.12 |  | 11.29
2013-04-18 | 6.62 | 5.31 |  |  |  |  | 7.01 | 1.87 |  |  |  |  | 36 |  |  |  | 0 | 0.297 |  |  | 0.119 | 0.116 | [5 empty] | 32.7 |  |  |  |  | 65.5 |  | 25.6 |  | 7.1 | 0.072 |  | 3.4 | 80 | 0.91 |  |  |  |  | 14.234 | 13.084 | [6 empty] | 29.11 |  | 9.66
2013-04-19 | 6.03 | 5.53 |  |  |  |  | 7.3 | 1.9 |  |  |  |  | 37 |  |  |  | 0 | 0.307 |  |  | 0.216 | 0.082 | [5 empty] | 33.5 |  |  |  |  | 67.1 |  | 23.8 |  | 7.4 | 0.081 |  | 3.4 | 75 | 0.705 |  |  |  |  | 14.559 | 13.922 | [6 empty] | 26.76 |  | 24.5
2013-04-20 | 6.14 | 5.26 |  |  |  |  | 7.64 | [5 empty] | 33 |  |  |  | 0 | 0.314 |  |  | 0.072 | 0.099 | [5 empty] | 32.8 |  |  |  |  | 65.6 |  | 23.8 |  | 7.4 | 0.087 |  | 3.5 | 77.5 | 0.8075 |  |  |  |  | 14.414 | 12.865 | [6 empty] | 27.07 |  | 21.9
2013-04-21 | 6.04 | 5.19 |  |  |  |  | 7.56 | 1.77 |  |  |  |  | 38 |  |  |  | 0 | 0.301 |  |  | 0.061 | 0.098 | [5 empty] | 33.9 |  |  |  |  | 67.8 |  | 23.7 |  | 7 | 0.054 |  | 3.5 | 70 | 0.52 |  |  |  |  | 13.97 | 13.87 | [6 empty] | 27.93 |  | 22.14
2013-04-22 | 6.09 | 5.225 |  |  |  |  | 7.6 | 0.885 |  |  |  |  | 35.5 |  |  |  | 0 | 0.3075 |  |  | 0.0665 | 0.0985 | [5 empty] | 33.35 |  |  |  |  | 66.7 |  | 23.75 |  | 7.2 | 0.0705 |  | 3.5 | 73.75 | 0.66375 |  |  |  |  | 14.192 | 13.3675 | [6 empty] | 27.5 |  | 22.02
2013-04-23 | 6.52 | 5.12 |  |  |  |  | 7.25 | 1.75 |  |  |  |  | 38 |  |  |  | 0 | 0.51 |  |  | 0.084 | 0.081 | [5 empty] | 30.7 |  |  |  |  | 61.4 |  | 25.2 |  | 10.9 | 0.074 |  | 3.4 | 70 | 0.7 |  |  |  |  | 13.984 | 12.971 | [6 empty] | 26.29 |  | 22.68
2013-04-24 | 6.18 | 5.45 |  |  |  |  | 7.32 | 1.83 |  |  |  |  | 37 |  |  |  | 0 | 0.387 |  |  | 0.071 | 0.082 | [5 empty] | 30.9 |  |  |  |  | 61.7 |  | 32.3 |  | 10.7 | 0.068 |  | 3.7 | 71.875 | 0.68188 |  |  |  |  | 13.007 | 12.01 | [6 empty] | 29.57 |  | 13.99
2013-04-25 | 6.09 | 5.29 |  |  |  |  | 7.01 | 1.86 |  |  |  |  | 39 |  |  |  | 0 | 0.442 |  |  | 0.065 | 0.134 | [5 empty] | 31.2 |  |  |  |  | 62.4 |  | 26.7 |  | 8.9 | 0.077 |  | 3.7 | 70.9375 | 0.69094 |  |  |  |  | 13.14 | 12.165 | [6 empty] | 3.014 |  | 13.24
2013-04-26 | 5.87 | 5.38 |  |  |  |  | 6.98 | 1.87 |  |  |  |  | 41 |  |  |  | 0 | 0.49 |  |  | 0.071 | 0.132 | [5 empty] | 28.9 |  |  |  |  | 58 |  | 24.1 |  | 8.1 | 0.105 |  | 5.3 | 71.4062 | 0.68641 |  |  |  |  | 13.274 | 12.329 | [6 empty] | 28.58 |  | 14.75
2013-04-27 | 5.22 | 4.98 |  |  |  |  | 7.73 | 1.96 |  |  |  |  | 41 |  |  |  | 0 | 0.408 |  |  | 0.078 | 0.134 | [5 empty] | 29.4 |  |  |  |  | 58.8 |  | 25.5 |  | 7.6 | 0.097 |  | 4 | 50 | 0.68867 |  |  |  |  | 13.816 | 12.818 | [6 empty] | 15.18 |  | 28.04
2013-04-28 | 5.46 | 5.49 |  |  |  |  | 7.54 | 1.99 |  |  |  |  | 42 |  |  |  | 0 | 0.384 |  |  | 0.081 | 0.104 | [5 empty] | 29.1 |  |  |  |  | 58.2 |  | 24.6 |  | 7.1 | 0.083 |  | 4 | 60.7031 | 0.68754 |  |  |  |  | 13.5 | 12.459 | [6 empty] | 28.62 |  | 15.49
2013-04-29 | 5.34 | 5.235 |  |  |  |  | 7.635 | 1.975 |  |  |  |  | 41.5 |  |  |  | 0 | 0.396 |  |  | 0.0795 | 0.119 | [5 empty] | 29.25 |  |  |  |  | 58.5 |  | 25.05 |  | 7.35 | 0.09 |  | 4 | 55.3516 | 0.68811 |  |  |  |  | 13.658 | 12.6385 | [6 empty] | 21.9 |  | 21.765
2013-04-30 | 5.39 | 5.37 |  |  |  |  | 7.91 | 1.88 |  |  |  |  | 47 |  |  |  | 0 | 0.479 |  |  | 0.078 | 0.089 | [5 empty] | 29.9 |  |  |  |  | 59.9 |  | 23.8 |  | 6.9 | 0.078 |  | 4.1 | 58.0273 | 0.68782 |  |  |  |  | 13.257 | 12.312 | [6 empty] | 28.31 |  | 16.17
2013-05-01 | 5.68 | 5.28 |  |  |  |  | 7.76 | 1.95 |  |  |  |  | 50 |  |  |  | 0 | 0.549 |  |  | 0.098 | 0.081 | [5 empty] | 30.7 |  |  |  |  | 61.4 |  | 24.4 |  | 7.2 | 0.091 |  | 4.1 | 60 | 0.14 |  |  |  |  | 14 | 13.04 | [6 empty] | 27.93 |  | 15.75
2013-05-02 | 5.6 | 5.31 |  |  |  |  | 7.96 | 2.06 |  |  |  |  | 48 |  |  |  | 0 | 0.638 |  |  | 0.095 | 0.083 | [5 empty] | 29 |  |  |  |  | 58 |  | 44.2 |  | 7.6 | 0.083 |  | 5.5 | 70 | 0.48 |  |  |  |  | 13.607 | 12.532 | [6 empty] | 26.77 |  | 15.59
2013-05-03 | 5.99 | 5.35 |  |  |  |  | 7.77 | 1.96 |  |  |  |  | 47 |  |  |  | 0 | 0.497 |  |  | 0.087 | 0.094 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 23.9 |  | 7.1 | 0.073 |  | 5.3 | 70 | 0.27 |  |  |  |  | 15.11 | 14.22 | [6 empty] | 26.68 |  | 16.45
2013-05-04 | 6.6 | 5.45 |  |  |  |  | 8.03 | 1.91 |  |  |  |  | 46 |  |  |  | 0 | 0.477 |  |  | 0.081 | 0.114 | [5 empty] | 28.7 |  |  |  |  | 57.5 |  | 26.2 |  | 7.4 | 0.067 |  | 5.6 | 80 | 0.73 |  |  |  |  | 14.708 | 13.752 | [6 empty] | 27.7 |  | 13.41
2013-05-05 | 6.17 | 5.39 |  |  |  |  | 8.01 | 1.98 |  |  |  |  | 46 |  |  |  | 0 | 0.506 |  |  | 0.068 | 0.112 | [5 empty] | 28.3 |  |  |  |  | 56.7 |  | 25.3 |  | 7.6 | 0.062 |  | 5.9 | 75 | 0.5 |  |  |  |  | 14.427 | 13.451 | [6 empty] | 27.23 |  | 12.76
2013-05-06 | 6.385 | 5.42 |  |  |  |  | 8.02 | 1.945 |  |  |  |  | 46 |  |  |  | 0 | 0.4915 |  |  | 0.0745 | 0.113 | [5 empty] | 28.5 |  |  |  |  | 57.1 |  | 25.75 |  | 7.5 | 0.0645 |  | 5.75 | 77.5 | 0.615 |  |  |  |  | 13.948 | 13.008 | [6 empty] | 27.465 |  | 13.085
2013-05-07 | 5.79 | 5.44 |  |  |  |  | 8.03 | 2.07 |  |  |  |  | 45 |  |  |  | 0 | 0.486 |  |  | 0.084 | 0.126 | [5 empty] | 27.2 |  |  |  |  | 54.4 |  | 25.8 |  | 7.7 | 0.086 |  | 7.1 | 70 | 0.25 |  |  |  |  | 15.168 | 13.674 | [6 empty] | 26.53 |  | 26.53
2013-05-08 | 5.23 | 5.54 |  |  |  |  | 8.03 | 2.12 |  |  |  |  | 46 |  |  |  | 0 | 0.528 |  |  | 0.098 | 0.128 | [5 empty] | 27.6 |  |  |  |  | 55.2 |  | 44.1 |  | 7.9 | 0.061 |  | 7.3 | 73.75 | 0.4325 |  |  |  |  | 15.92 | 15.46 | [6 empty] | 28.46 |  | 14.54
2013-05-09 | 6.33 | 5.63 |  |  |  |  | 8.25 | 1.87 |  |  |  |  | 38 |  |  |  | 0 | 0.614 |  |  | 0.061 | 0.112 | [5 empty] | 26.9 |  |  |  |  | 53.9 |  | 24.1 |  | 7.9 | 0.064 |  | 7.9 | 80 | 0.91 |  |  |  |  | 13.866 | 13.084 | [6 empty] | 27.23 |  | 13.66
2013-05-10 | 6.02 | 5.46 |  |  |  |  | 7.89 | 1.89 |  |  |  |  | 36 |  |  |  | 0 | 0.697 |  |  | 0.108 | 0.105 | [5 empty] | 27.7 |  |  |  |  | 55.5 |  | 24.1 |  | 3.4 | 0.068 |  | 8.1 | 76.875 | 0.67125 |  |  |  |  | 14.253 | 13.273 | [6 empty] | 25.82 |  | 10.83
2013-05-11 | 5.99 | 5.24 |  |  |  |  | 7.95 | 1.94 |  |  |  |  | 35 |  |  |  | 0 | 0.587 |  |  | 0.097 | 0.118 | [5 empty] | 29.2 |  |  |  |  | 68.4 |  | 22.4 |  | 5.9 | 0.071 |  | 8.2 | 78.4375 | 0.79063 |  |  |  |  | 14.811 | 13.847 | [6 empty] | 26.39 |  | 11.33
2013-05-12 | 6.1 | 5.31 |  |  |  |  | 8.05 | 1.94 |  |  |  |  | 41 |  |  |  | 0 | 0.781 |  |  | 0.094 | 0.114 | [5 empty] | 30.6 |  |  |  |  | 61.2 |  | 23.5 |  | 6.4 | 0.057 |  | 8.2 | 70 | 0.55 |  |  |  |  | 13.78 | 12.76 | [6 empty] | 25.88 |  | 12.47
2013-05-13 | 6.045 | 5.275 |  |  |  |  | 8 | 1.94 |  |  |  |  | 38 |  |  |  | 0 | 0.684 |  |  | 0.0955 | 0.116 | [5 empty] | 29.9 |  |  |  |  | 64.8 |  | 22.95 |  | 6.15 | 0.064 |  | 8.2 | 74.2188 | 0.67031 |  |  |  |  | 14.2955 | 13.3035 | [6 empty] | 26.135 |  | 11.9
2013-05-14 | 6.29 | 5.31 |  |  |  |  | 7.87 | 1.96 |  |  |  |  | 36 |  |  |  | 0 | 0.637 |  |  | 0.067 | 0.092 | [5 empty] | 26.7 |  |  |  |  | 53.5 |  | 26.6 |  | 7.8 | 0.071 |  | 9.1 | 70 | 0.49 |  |  |  |  | 13.985 | 12.951 | [6 empty] | 24.41 |  | 12.71
2013-05-15 | 6.58 | 5.32 |  |  |  |  | 7.53 | 1.96 |  |  |  |  | 35 |  |  |  | 0 | 0.845 |  |  | 0.073 | 0.153 | [5 empty] | 24.3 |  |  |  |  | 48.7 |  | 23.6 |  | 4.2 | 0.08 |  | 9.6 | 72.1094 | 0.58016 |  |  |  |  | 16.152 | 12.897 | [6 empty] | 24.88 |  | 13.98
2013-05-16 | 6.48 | 5.79 |  |  |  |  | 8.45 | 2.04 |  |  |  |  | 41 |  |  |  | 0 | 0.867 |  |  | 0.061 | 0.087 | [5 empty] | 27.6 |  |  |  |  | 55.2 |  | 23 |  | 5.1 | 0.074 |  | 9.6 | 71.0547 | 0.53508 |  |  |  |  | 14.938 | 13.568 | [6 empty] | 25.17 |  | 14.1
2013-05-17 | 6.53 | 5.67 |  |  |  |  | 7.99 | 2 |  |  |  |  | 38 |  |  |  | 0 | 0.856 |  |  | 0.067 | 0.12 | [5 empty] | 25.95 |  |  |  |  | 51.95 |  | 23.3 |  | 4.65 | 0.077 |  | 9.6 | 71.582 | 0.55762 |  |  |  |  | 15.613 | 12.717 | [6 empty] | 25.025 |  | 14.04
2013-05-18 | 5.69 | 5.69 |  |  |  |  | 7.78 | 2.06 |  |  |  |  | 41 |  |  |  | 0 | 0.743 |  |  | 0.091 | 0.083 | [5 empty] | 25.9 |  |  |  |  | 51.8 |  | 24.6 |  | 5.7 | 0.059 |  | 10.4 | 70 | 0.43 |  |  |  |  | 14.559 | 12.748 | [6 empty] | 24.55 |  | 11.47
2013-05-19 | 6.09 | 5.86 |  |  |  |  | 7.15 | 2.06 |  |  |  |  | 42 |  |  |  | 0 | 0.958 |  |  | 0.096 | 0.074 | [5 empty] | 23.9 |  |  |  |  | 47.8 |  | 23.4 |  | 6 | 0.063 |  | 9.7 | 70.791 | 0.49381 |  |  |  |  | 14.267 | 12.494 | [6 empty] | 32.65 |  | 9.8
2013-05-20 | 5.89 | 5.775 |  |  |  |  | 7.465 | 2.06 |  |  |  |  | 41.5 |  |  |  | 0 | 0.8505 |  |  | 0.0935 | 0.0785 | [5 empty] | 24.9 |  |  |  |  | 49.8 |  | 24 |  | 5.85 | 0.061 |  | 10.05 | 70.3955 | 0.4619 |  |  |  |  | 16.132 | 11.861 | [6 empty] | 28.6 |  | 10.635
2013-05-21 | 5.92 | 5.59 |  |  |  |  | 6.65 | 1.72 |  |  |  |  | 35 |  |  |  | 0 | 0.897 |  |  | 0.087 | 0.114 | [5 empty] | 26.2 |  |  |  |  | 52.4 |  | 23.1 |  | 8.9 | 0.071 |  | 9.7 | 70.5933 | 0.47786 |  |  |  |  | 19.649 | 11.306 | [6 empty] | 30.58 |  | 10.35
2013-05-22 | 6.04 | 5.63 |  |  |  |  | 7.76 | 1.91 |  |  |  |  | 37 |  |  |  | 0 | 0.971 |  |  | 0.371 | 0.143 | [5 empty] | 25.9 |  |  |  |  | 51.8 |  | 22.3 |  | 5.4 | 0.113 |  | 9.8 | 90 | 0.97 |  |  |  |  | 16.582 | 14.188 | [6 empty] | 31.3 |  | 11.57
2013-05-23 | 5.54 | 5.48 |  |  |  |  | 6.39 | 2.08 |  |  |  |  | 38 |  |  |  | 0 | 0.763 |  |  | 0.091 | 0.064 | [5 empty] | 26.2 |  |  |  |  | 52.4 |  | 22.8 |  | 4.9 | 0.026 |  | 10.6 | 70 | 0.3 |  |  |  |  | 14.293 | 13.368 | [6 empty] | 30.6 |  | 11.08
2013-05-24 | 5.95 | 5.19 |  |  |  |  | 7.84 | 2.09 |  |  |  |  | 37 |  |  |  | 0 | 0.753 |  |  | 0.097 | 0.084 | [5 empty] | 26.1 |  |  |  |  | 52.2 |  | 23 |  | 5.3 | 0.033 |  | 8.9 | 80 | 0.59 |  |  |  |  | 14.03 | 13.54 | [6 empty] | 30.04 |  | 13.26
2013-05-25 | 6.56 | 5.24 |  |  |  |  | 7.6 | 2.05 |  |  |  |  | 34 |  |  |  | 0 | 0.939 |  |  | 0.101 | 0.079 | [5 empty] | 28.6 |  |  |  |  | 57.2 |  | 26.3 |  | 6.5 | 0.59 |  | 9.2 | 60 | 0.08 |  |  |  |  | 13.298 | 12.784 | [6 empty] | 29.11 |  | 12.93
2013-05-26 | 6.58 | 5.28 |  |  |  |  | 8.13 | 2.03 |  |  |  |  | 36 |  |  |  | 0 | 0.864 |  |  | 0.096 | 0.085 | [5 empty] | 28.7 |  |  |  |  | 57.5 |  | 23.9 |  | 6.4 | 0.054 |  | 9.3 | 70 | 0.335 |  |  |  |  | 13.2 | 12.31 | [6 empty] | 29.575 |  | 13.36
2013-05-27 | 6.57 | 5.26 |  |  |  |  | 7.865 | 1.91 |  |  |  |  | 35 |  |  |  | 0 | 0.9015 |  |  | 0.0985 | 0.082 | [5 empty] | 28.65 |  |  |  |  | 57.35 |  | 25.1 |  | 6.45 | 0.322 |  | 9.25 | 65 | 0.2075 |  |  |  |  | 12.918 | 12.002 | [6 empty] | 28.17 |  | 13.36
2013-05-28 | 5.61 | 5.34 |  |  |  |  | 7.78 | 1.97 |  |  |  |  | 37 |  |  |  | 0 | 1.058 |  |  | 0.09 | 0.083 | [5 empty] | 26 |  |  |  |  | 52 |  | 23.5 |  | 6.2 | 0.049 |  | 10.6 | 90 | 1.02 |  |  |  |  | 14.729 | 13.714 | [6 empty] | 29.26 |  | 12.33
2013-05-29 | 5.72 | 5.49 |  |  |  |  | 7.78 | 1.98 |  |  |  |  | 36 |  |  |  | 0 | 1.256 |  |  | 0.094 | 0.086 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 23.7 |  | 6.5 | 0.052 |  | 10.8 | 77.5 | 0.61375 |  |  |  |  | 14.373 | 13.443 | [6 empty] | 31.36 |  | 12.54
2013-05-30 | 5.94 | 5.22 |  |  |  |  | 7.76 | 1.97 |  |  |  |  | 39 |  |  |  | 0 | 0.918 |  |  | 0.087 | 0.074 | [5 empty] | 29.3 |  |  |  |  | 58.6 |  | 24.3 |  | 6.2 | 0.061 |  | 10.8 | 83.75 | 0.81688 |  |  |  |  | 14.786 | 14.3 | [6 empty] | 31.36 |  | 12.54
2013-05-31 | 5.83 | 5.24 |  |  |  |  | 8.1 | 1.96 |  |  |  |  | 42 |  |  |  | 0 | 0.786 |  |  | 0.097 | 0.084 | [5 empty] | 30.1 |  |  |  |  | 60.2 |  | 23.9 |  | 6.5 | 0.069 |  | 10.7 | 80.625 | 0.71531 |  |  |  |  | 15.177 | 14.224 | [6 empty] | 31.36 |  | 12.54
2013-06-01 | 5.79 | 5.47 |  |  |  |  | 7.99 | 1.965 |  |  |  |  | 43 |  |  |  | 0 | 0.773 |  |  | 0.107 | 0.072 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 23.3 |  | 6.7 | 0.072 |  | 10.8 | 82.1875 | 0.76609 |  |  |  |  | 14.216 | 13.726 | [6 empty] | 31.34 |  | 12.07
2013-06-02 | 5.73 | 5.49 |  |  |  |  | 7.73 | 1.96 |  |  |  |  | 37 |  |  |  | 0 | 1.04 |  |  | 0.113 | 0.781 | [5 empty] | 31.1 |  |  |  |  | 62.2 |  | 23.1 |  | 6 | 0.064 |  | 10.9 | 70 | 0.34 |  |  |  |  | 14.8 | 13.83 | [6 empty] | 30.11 |  | 11.12
2013-06-03 | 5.76 | 5.48 |  |  |  |  | 7.86 | 1.9625 |  |  |  |  | 40 |  |  |  | 0 | 0.9065 |  |  | 0.11 | 0.4265 | [5 empty] | 30.75 |  |  |  |  | 61.5 |  | 23.2 |  | 6.35 | 0.068 |  | 10.85 | 76.0938 | 0.55305 |  |  |  |  | 14.508 | 13.778 | [6 empty] | 30.725 |  | 11.595
2013-06-04 | 6.32 | 5.47 |  |  |  |  | 7.37 | 1.89 |  |  |  |  | 31 |  |  |  | 0 | 0.905 |  |  | 0.123 | 0.07 | [5 empty] | 26.6 |  |  |  |  | 53.3 |  | 26.3 |  | 7 | 0.038 |  | 11.6 | 70 | 0.56 |  |  |  |  | 13.94 | 12.996 | [6 empty] | 24.88 |  | 11.11
2013-06-05 | 6.04 | 5.37 |  |  |  |  | 7.05 | 1.91 |  |  |  |  | 33 |  |  |  | 0 | 0.907 |  |  | 0.104 | 0.063 | [5 empty] | 27.4 |  |  |  |  | 55.8 |  | 25.8 |  | 6.9 | 0.042 |  | 11.6 | 73.0469 | 0.55652 |  |  |  |  | 13.788 | 13.333 | [6 empty] | 27.72 |  | 11.11
2013-06-06 | 5.85 | 5.25 |  |  |  |  | 7.03 | 1.96 |  |  |  |  | 20 |  |  |  | 0 | 0.942 |  |  | 0.067 | 0.063 | [5 empty] | 27.7 |  |  |  |  | 55.4 |  | 25.4 |  | 5.7 | 0.008 |  | 12.1 | 90 | 1.22 |  |  |  |  | 13.77 | 12.85 | [6 empty] | 25.39 |  | 11.77
2013-06-07 | 5.91 | 5.12 |  |  |  |  | 7.76 | 1.95 |  |  |  |  | 26 |  |  |  | 0 | 0.751 |  |  | 0.082 | 0.078 | [5 empty] | 28 |  |  |  |  | 56 |  | 25 |  | 6 | 0.032 |  | 12.1 | 60 | 0.17 |  |  |  |  | 13.905 | 12.872 | [6 empty] | 25.05 |  | 12.48
2013-06-08 | 5.53 | 5.13 |  |  |  |  | 7.84 | 1.87 |  |  |  |  | 23 |  |  |  | 0 | 0.843 |  |  | 0.087 | 0.074 | [5 empty] | 28.6 |  |  |  |  | 57.2 |  | 24.7 |  | 6.2 | 0.049 |  | 11.7 | 80 | 0.96 |  |  |  |  | 13.838 | 12.834 | [6 empty] | 31.46 |  | 13.78
2013-06-09 | 6.02 | 5.69 |  |  |  |  | 7.9 | 1.84 |  |  |  |  | 24 |  |  |  | 0 | 0.943 |  |  | 0.093 | 0.076 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 24.6 |  | 6.4 | 0.052 |  | 11.7 | 70 | 0.565 |  |  |  |  | 13.37 | 12.37 | [6 empty] | 33.39 |  | 11.96
2013-06-10 | 5.775 | 5.41 |  |  |  |  | 7.87 | 1.84 |  |  |  |  | 23.5 |  |  |  | 0 | 0.893 |  |  | 0.09 | 0.075 | [5 empty] | 28.35 |  |  |  |  | 56.7 |  | 24.65 |  | 6.3 | 0.0505 |  | 11.7 | 75 | 0.7625 |  |  |  |  | 12.404 | 11.892 | [6 empty] | 32.425 |  | 12.87
2013-06-11 | 6.07 | 5.29 |  |  |  |  | 7.1 | 1.91 |  |  |  |  | 27 |  |  |  | 0 | 0.747 |  |  | 0.083 | 0.079 | [5 empty] | 29.2 |  |  |  |  | 68.4 |  | 25.3 |  | 6.8 | 0.064 |  | 11.8 | 70 | 0.57 |  |  |  |  | 13.819 | 12.827 | [6 empty] | 32.94 |  | 12.77
2013-06-12 | 5.95 | 5.22 |  |  |  |  | 7.45 | 1.875 |  |  |  |  | 32 |  |  |  | 0 | 0.823 |  |  | 0.073 | 0.079 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 23.9 |  | 6.2 | 0.077 |  | 11.7 | 72.5 | 0.66625 |  |  |  |  | 13.37 | 12.844 | [6 empty] | 32.69 |  | 11.75
2013-06-13 | 6.14 | 5.17 |  |  |  |  | 6.39 | 1.85 |  |  |  |  | 35 |  |  |  | 0 | 0.926 |  |  | 0.116 | 0.087 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 22.2 |  | 4.4 | 0.119 |  | 14 | 70 | 0.61 |  |  |  |  | 14.388 | 12.896 | [6 empty] | 29.56 |  | 10.94
2013-06-14 | 5.65 | 5.86 |  |  |  |  | 7.91 | 1.92 |  |  |  |  | 34 |  |  |  | 0 | 0.948 |  |  | 0.107 | 0.073 | [5 empty] | 28 |  |  |  |  | 56 |  | 23.6 |  | 6.5 | 0.094 |  | 13.1 | 60 | 0.12 |  |  |  |  | 13.93 | 13.37 | [6 empty] | 30.73 |  | 11.43
2013-06-15 | 6.36 | 5.47 |  |  |  |  | 7.29 | 1.85 |  |  |  |  | 29 |  |  |  | 0 | 0.804 |  |  | 0.064 | 0.069 | [5 empty] | 27.4 |  |  |  |  | 54.9 |  | 23.7 |  | 7.2 | 0.081 |  | 13 | 70 | 0.79 |  |  |  |  | 13.044 | 12.057 | [6 empty] | 25.35 |  | 11.6
2013-06-16 | 6.29 | 5.46 |  |  |  |  | 7.09 | 1.86 |  |  |  |  | 30 |  |  |  | 0 | 0.958 |  |  | 0.072 | 0.066 | [5 empty] | 28 |  |  |  |  | 56.1 |  | 22 |  | 6.9 | 0.079 |  | 13.1 | 65 | 0.455 |  |  |  |  | 13.59 | 12.63 | [6 empty] | 25.36 |  | 15.36
2013-06-17 | 6.325 | 5.465 |  |  |  |  | 7.19 | 1.83 |  |  |  |  | 29.5 |  |  |  | 0 | 0.881 |  |  | 0.068 | 0.0675 | [5 empty] | 27.7 |  |  |  |  | 55.5 |  | 22.85 |  | 7.05 | 0.08 |  | 13.05 | 67.5 | 0.6225 |  |  |  |  | 12.896 | 11.887 | [6 empty] | 25.35 |  | 15.36
2013-06-18 | 5.96 | 5.46 |  |  |  |  | 7.17 | 1.845 |  |  |  |  | 29 |  |  |  | 0 | 0.896 |  |  | 0.087 | 0.074 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 23.7 |  | 5.8 | 0.05 |  | 12.5 | 66.25 | 0.53875 |  |  |  |  | 14.224 | 12.226 | [6 empty] | 26.8 |  | 11.38
2013-06-19 | 5.88 | 5.55 |  |  |  |  | 6.84 | 1.8375 |  |  |  |  | 31 |  |  |  | 0 | 0.841 |  |  | 0.074 | 0.065 | [5 empty] | 27.2 |  |  |  |  | 54.4 |  | 24.4 |  | 5.2 | 0.067 |  | 12.6 | 66.875 | 0.58063 |  |  |  |  | 13.622 | 12.6 | [6 empty] | 27.19 |  | 12.09
2013-06-20 | 6.01 | 5.54 |  |  |  |  | 6.84 | 1.81 |  |  |  |  | 32 |  |  |  | 0 | 0.809 |  |  | 0.097 | 0.076 | [5 empty] | 27.8 |  |  |  |  | 55.6 |  | 24.8 |  | 6.3 | 0.071 |  | 12.4 | 66.5625 | 0.55969 |  |  |  |  | 13.908 | 12.894 | [6 empty] | 27.19 |  | 12.09
2013-06-21 | 5.66 | 5.59 |  |  |  |  | 7.34 | 1.8237 |  |  |  |  | 31 |  |  |  | 0 | 0.824 |  |  | 0.081 | 0.074 | [5 empty] | 24.1 |  |  |  |  | 48.2 |  | 25.2 |  | 6 | 0.083 |  | 12.8 | 66.7188 | 0.57016 |  |  |  |  | 14.135 | 13.189 | [6 empty] | 27.19 |  | 12.09
2013-06-22 | 5.79 | 5.61 |  |  |  |  | 7.72 | 1.93 |  |  |  |  | 26 |  |  |  | 0 | 0.854 |  |  | 0.084 | 0.079 | [5 empty] | 26 |  |  |  |  | 52 |  | 26.3 |  | 5.7 | 0.079 |  | 12.9 | 66.6406 | 0.56492 |  |  |  |  | 14.588 | 13.555 | [6 empty] | 28.05 |  | 12.06
2013-06-23 | 5.88 | 5.64 |  |  |  |  | 7.99 | 1.8 |  |  |  |  | 21 |  |  |  | 0 | 0.881 |  |  | 0.083 | 0.074 | [5 empty] | 28.7 |  |  |  |  | 57.4 |  | 23.7 |  | 5.7 | 0.064 |  | 13 | 70 | 0.43 |  |  |  |  | 14.4 | 13.77 | [6 empty] | 26.9 |  | 11.61
2013-06-24 | 5.835 | 5.625 |  |  |  |  | 7.855 | 1.865 |  |  |  |  | 23.5 |  |  |  | 0 | 0.8675 |  |  | 0.0835 | 0.0765 | [5 empty] | 27.35 |  |  |  |  | 54.7 |  | 25 |  | 5.7 | 0.0715 |  | 12.95 | 68.3203 | 0.49746 |  |  |  |  | 14.494 | 13.6625 | [6 empty] | 27.475 |  | 11.835
2013-06-25 | 6.58 | 5.66 |  |  |  |  | 7.61 | 1.83 |  |  |  |  | 27 |  |  |  | 0 | 0.646 |  |  | 0.074 | 0.142 | [5 empty] | 27.9 |  |  |  |  | 55.8 |  | 21.9 |  | 6.3 | 0.072 |  | 14.6 | 80 | 0.75 |  |  |  |  | 16.45 | 14.061 | [6 empty] | 26.76 |  | 12.28
2013-06-26 | 6.46 | 5.4 |  |  |  |  | 7.34 | 1.91 |  |  |  |  | 26 |  |  |  | 0 | 0.987 |  |  | 0.062 | 0.071 | [5 empty] | 25.9 |  |  |  |  | 51.9 |  | 25.5 |  | 6.8 | 0.062 |  | 15.1 | 70 | 0.3 |  |  |  |  | 16.147 | 14.375 | [6 empty] | 26.52 |  | 13.01
2013-06-27 | 5.73 | 5.74 |  |  |  |  | 7.05 | 1.94 |  |  |  |  | 27 |  |  |  | 0 | 0.761 |  |  | 0.081 | 0.074 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 24.6 |  | 5.7 | 0.074 |  | 14.8 | 75 | 0.525 |  |  |  |  | 13.79 | 12.34 | [6 empty] | 26.52 |  | 13.01
2013-06-28 | 6.095 | 5.57 |  |  |  |  | 7.195 | 1.925 |  |  |  |  | 26.5 |  |  |  | 0 | 0.874 |  |  | 0.0715 | 0.0725 | [5 empty] | 26.65 |  |  |  |  | 53.35 |  | 25.05 |  | 6.25 | 0.068 |  | 14.95 | 72.5 | 0.4125 |  |  |  |  | 14.9685 | 13.3575 | [6 empty] | 26.52 |  | 13.01
2013-06-29 | 5.91 | 5.74 |  |  |  |  | 7.46 | 1.79 |  |  |  |  | 26 |  |  |  | 0 | 1.153 |  |  | 0.094 | [6 empty] | 27.69 |  |  |  |  | 55.2 |  | 24.7 |  | 6.1 | 0.071 |  | 12.9 | 70 | 0.8 |  |  |  |  | 13.29 | 12.252 | [6 empty] | 26.17 |  | 11.28
2013-06-30 | 6.15 | 5.37 |  |  |  |  | 7.45 | 1.88 |  |  |  |  | 31 |  |  |  | 0 | 1.234 |  |  | 0.128 | 0.074 | [5 empty] | 24.7 |  |  |  |  | 49.4 |  | 24 |  | 6 | 0.068 |  | 13.1 | 70 | 0.73 |  |  |  |  | 13.198 | 12.157 | [6 empty] | 25.96 |  | 14.38
2013-07-01 | 6.03 | 5.555 |  |  |  |  | 7.455 | 1.835 |  |  |  |  | 28.5 |  |  |  | 0 | 1.1935 |  |  | 0.111 | 0.037 | [5 empty] | 26.195 |  |  |  |  | 52.3 |  | 24.35 |  | 6.05 | 0.0695 |  | 13 | 70 | 0.765 |  |  |  |  | 13.244 | 12.2045 | [6 empty] | 26.065 |  | 12.83
2013-07-02 | 5.76 | 5.33 |  |  |  |  | 7.09 | 1.98 |  |  |  |  | 33 |  |  |  | 0 | 1.077 |  |  | 0.094 | 0.053 | [5 empty] | 25.6 |  |  |  |  | 51.2 |  | 23.9 |  | 5.8 | 0.054 |  | 14.4 | 70 | 0.7475 |  |  |  |  | 15.15 | 13.74 | [6 empty] | 27.04 |  | 14.38
2013-07-03 | 5.895 | 5.4425 |  |  |  |  | 7.2725 | 1.9075 |  |  |  |  | 30.75 |  |  |  | 0 | 1.1353 |  |  | 0.1025 | 0.045 | [5 empty] | 25.8975 |  |  |  |  | 51.75 |  | 24.125 |  | 5.925 | 0.06175 |  | 13.7 | 70 | 0.75625 |  |  |  |  | 14.197 | 12.9722 | [6 empty] | 26.5525 |  | 13.605
2013-07-04 | 6.01 | 5.34 |  |  |  |  | 7.43 | 1.96 |  |  |  |  | 32 |  |  |  | 0 | 1.226 |  |  | 0.173 | 0.074 | [5 empty] | 26.7 |  |  |  |  | 53.4 |  | 25.4 |  | 6.2 | 0.086 |  | 15.7 | 80 | 0.51 |  |  |  |  | 15.652 | 14.68 | [6 empty] | 27.64 |  | 13.9925
2013-07-05 | 5.89 | 5.46 |  |  |  |  | 7.04 | 1.9 |  |  |  |  | 33 |  |  |  | 0 | 1.498 |  |  | 0.124 | 0.117 | [5 empty] | 21.1 |  |  |  |  | 42.2 |  | 24.7 |  | 5.3 | 0.091 |  | 16 | 80 | 0.46 |  |  |  |  | 16.4 | 15.41 | [6 empty] | 31.11 |  | 9.13
2013-07-06 | 6.33 | 5.32 |  |  |  |  | 6.53 | 1.86 |  |  |  |  | 26 |  |  |  | 0 | 1.845 |  |  | 0.061 | 0.17 | [5 empty] | 26.5 |  |  |  |  | 53.1 |  | 25.3 |  | 4.8 | 0.074 |  | 16 | 70 | 0.14 |  |  |  |  | 15.87 | 15.88 | [6 empty] | 26.29 |  | 12.62
2013-07-07 | 6.46 | 5.27 |  |  |  |  | 7.88 | 1.83 |  |  |  |  | 25 |  |  |  | 0 | 1.535 |  |  | 0.058 | 0.086 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 23.9 |  | 5.1 | 0.077 |  | 16.2 | 75 | 0.3 |  |  |  |  | 15.53 | 14.55 | [6 empty] | 29.1 |  | 18.7
2013-07-08 | 6.395 | 5.295 |  |  |  |  | 7.205 | 1.845 |  |  |  |  | 25.5 |  |  |  | 0 | 1.69 |  |  | 0.0595 | 0.128 | [5 empty] | 27.35 |  |  |  |  | 54.75 |  | 24.6 |  | 4.95 | 0.0755 |  | 16.1 | 72.5 | 0.22 |  |  |  |  | 15.318 | 14.323 | [6 empty] | 29.11 |  | 18.7
2013-07-09 | 6.01 | 5.24 |  |  |  |  | 7.29 | 1.75 |  |  |  |  | 25 |  |  |  | 0 | 1.684 |  |  | 0.073 | 0.086 | [5 empty] | 27.9 |  |  |  |  | 55.8 |  | 23.8 |  | 5.4 | 0.063 |  | 17 | 100 | 1.09 |  |  |  |  | 17.536 | 15.998 | [6 empty] | 28.76 |  | 11.87
2013-07-10 | 6.01 | 5.54 |  |  |  |  | 8.35 | 1.76 |  |  |  |  | 24 |  |  |  | 0 | 1.376 |  |  | 0.184 | 0.097 | [5 empty] | 30.1 |  |  |  |  | 60.2 |  | 24.6 |  | 6.3 | 0.071 |  | 17.5 | 80 | 0.21 |  |  |  |  | 18.94 | 18.48 | [6 empty] | 28.21 |  | 14.01
2013-07-11 | 6.22 | 5.62 |  |  |  |  | 8.31 | 1.77 |  |  |  |  | 25 |  |  |  | 0 | 1.107 |  |  | 0.057 | 0.074 | [5 empty] | 27.8 |  |  |  |  | 55.6 |  | 25.3 |  | 6.8 | 0.068 |  | 17.8 | 90 | 0.67 |  |  |  |  | 17.655 | 16.73 | [6 empty] | 29.81 |  | 12.17
2013-07-12 | 6.64 | 5.4 |  |  |  |  | 7.08 | 1.87 |  |  |  |  | 26 |  |  |  | 0 | 4.522 |  |  | 0.068 | 0.063 | [5 empty] | 26.6 |  |  |  |  | 53.3 |  | 22.8 |  | 6.2 | 0.077 |  | 17.4 | 85 | 0.44 |  |  |  |  | 19.397 | 18.668 | [6 empty] | 29.57 |  | 11.8
2013-07-13 | 6.48 | 5.39 |  |  |  |  | 7.58 | 1.87 |  |  |  |  | 29 |  |  |  | 0 | 4.671 |  |  | 0.099 | 0.069 | [5 empty] | 27.2 |  |  |  |  | 54.4 |  | 22.6 |  | 5.9 | 0.068 |  | 17.5 | 70 | 0.24 |  |  |  |  | 16.036 | 15.071 | [6 empty] | 30.11 |  | 1.91
2013-07-14 | 6.01 | 5.35 |  |  |  |  | 7.52 | 1.9 |  |  |  |  | 31 |  |  |  | 0 | 3.974 |  |  | 0.113 | 0.084 | [5 empty] | 27.8 |  |  |  |  | 55.6 |  | 24.7 |  | 6 | 0.073 |  | 17.5 | 95 | 0.74 |  |  |  |  | 17.32 | 16.36 | [6 empty] | 31.94 |  | 10.99
2013-07-15 | 6.245 | 5.37 |  |  |  |  | 7.55 | 1.885 |  |  |  |  | 30 |  |  |  | 0 | 4.3225 |  |  | 0.106 | 0.0765 | [5 empty] | 27.5 |  |  |  |  | 55 |  | 23.65 |  | 5.95 | 0.0705 |  | 17.5 | 82.5 | 0.49 |  |  |  |  | 16.678 | 15.7155 | [6 empty] | 31.025 |  | 6.45
2013-07-16 | 6.72 | 5.28 |  |  |  |  | 7.81 | 2.02 |  |  |  |  | 27 |  |  |  | 0 | 3.196 |  |  | 0.058 | 0.071 | [5 empty] | 29.9 |  |  |  |  | 59.8 |  | 26.1 |  | 6.2 | 0.071 |  | 18.2 | 100 | 0.6 |  |  |  |  | 19.023 | 17.359 | [6 empty] | 29.11 |  | 14.51
2013-07-17 | 6.4 | 5.35 |  |  |  |  | 7.96 | 1.85 |  |  |  |  | 26 |  |  |  | 0 | 3.123 |  |  | 0.06 | 0.076 | [5 empty] | 27 |  |  |  |  | 54 |  | 25.9 |  | 6.8 | 0.072 |  | 18.7 | 91.25 | 0.545 |  |  |  |  | 18.703 | 18.268 | [6 empty] | 28.17 |  | 12.65
2013-07-18 | 6.56 | 5.315 |  |  |  |  | 7.885 | 1.935 |  |  |  |  | 26.5 |  |  |  | 0 | 3.1595 |  |  | 0.059 | 0.0735 | [5 empty] | 28.45 |  |  |  |  | 56.9 |  | 26 |  | 6.5 | 0.0715 |  | 18.45 | 95.625 | 0.5725 |  |  |  |  | 18.863 | 17.8135 | [6 empty] | 28.64 |  | 13.58
2013-07-19 | 6.48 | 5.3325 |  |  |  |  | 7.9225 | 1.8925 |  |  |  |  | 26.25 |  |  |  | 0 | 3.1413 |  |  | 0.0595 | 0.07475 | [5 empty] | 27.725 |  |  |  |  | 55.45 |  | 25.95 |  | 6.65 | 0.07175 |  | 18.575 | 93.4375 | 0.55875 |  |  |  |  | 18.783 | 18.0408 | [6 empty] | 28.405 |  | 13.115
2013-07-20 | 6.06 | 5.53 |  |  |  |  | 7.87 | 1.82 |  |  |  |  | 25 |  |  |  | 0 | 2.974 |  |  | 0.093 | 0.074 | [5 empty] | 29.6 |  |  |  |  | 59.2 |  | 25.5 |  | 6.5 | 0.069 |  | 17.9 | 80 | 0.66 |  |  |  |  | 15.73 | 14.637 | [6 empty] | 30.19 |  | 13.3475
2013-07-21 | 5.21 | 5.21 |  |  |  |  | 6.4 | 1.91 |  |  |  |  | 26 |  |  |  | 0 | 2.717 |  |  | 0.057 | 0.064 | [5 empty] | 26.1 |  |  |  |  | 52.2 |  | 24.6 |  | 5.8 | 0.083 |  | 18 | 86.7188 | 0.60938 |  |  |  |  | 14.443 | 13.441 | [6 empty] | 29.77 |  | 11.74
2013-07-22 | 5.635 | 5.37 |  |  |  |  | 7.135 | 2.15 |  |  |  |  | 25.5 |  |  |  | 0 | 2.8455 |  |  | 0.075 | 0.069 | [5 empty] | 27.85 |  |  |  |  | 55.7 |  | 25.05 |  | 6.15 | 0.076 |  | 17.95 | 83.3594 | 0.63469 |  |  |  |  | 15.382 | 14.353 | [6 empty] | 29.98
2013-07-23 | 5.82 | 5.12 |  |  |  |  | 7.76 | 2.06 |  |  |  |  | 33 |  |  |  | 0 | 2.06 |  |  | 0.073 | 0.075 | [5 empty] | 25.9 |  |  |  |  | 51.8 |  | 24.5 |  | 5.4 | 0.074 |  | 18 | 100 | 0.8 |  |  |  |  | 16.481 | 15.452 | [6 empty] | 30.83 |  | 11.11
2013-07-24 | 6.04 | 5.22 |  |  |  |  | 8.54 | 2.105 |  |  |  |  | 20 |  |  |  | 0 | 2.05 |  |  | 0.084 | 0.087 | [5 empty] | 27.3 |  |  |  |  | 54.6 |  | 25.6 |  | 5.7 | 0.061 |  | 18.1 | 91.6797 | 0.71734 |  |  |  |  | 16.737 | 16.663 | [6 empty] | 30.38
2013-07-25 | 6.11 | 5.23 |  |  |  |  | 8.23 | 1 |  |  |  |  | 26 |  |  |  | 0 | 0.51 |  |  | 0.13 | 0.084 | [5 empty] | 26.1 |  |  |  |  | 52.2 |  | 23.7 |  | 6.1 | 0.072 |  | 18.1 | 95.8398 | 0.75867 |  |  |  |  | 15.497 | 13.904 | [6 empty] | 28.96 |  | 11.91
2013-07-26 | 6.09 | 5.22 |  |  |  |  | 8.43 | 2.02 |  |  |  |  | 21 |  |  |  | 0 | 0.497 |  |  | 0.118 | 0.081 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 23.6 |  | 5.4 | 0.084 |  | 18.2 | 70 | 0.18 |  |  |  |  | 14.98 | 14.43 | [6 empty] | 29.77 |  | 12.41
2013-07-27 | 6.61 | 5.21 |  |  |  |  | 8.35 | 2.02 |  |  |  |  | 22 |  |  |  | 0 | 0.531 |  |  | 0.068 | 0.078 | [5 empty] | 31.4 |  |  |  |  | 62.8 |  | 25.7 |  | 6.2 | 0.076 |  | 18.4 | 80 | 0.63 |  |  |  |  | 15.21 | 13.73 | [6 empty] | 28.17 |  | 23.24
2013-07-28 | 6.37 | 5.59 |  |  |  |  | 7.78 | 2.02 |  |  |  |  | 23 |  |  |  | 0 | 0.528 |  |  | 0.064 | 0.061 | [5 empty] | 27.2 |  |  |  |  | 54.5 |  | 23.6 |  | 6.3 | 0.068 |  | 18.1 | 75 | 0.405 |  |  |  |  | 13.39 | 13.66 | [6 empty] | 28.64 |  | 12.65
2013-07-29 | 6.49 | 5.4 |  |  |  |  | 8.065 | 2.02 |  |  |  |  | 22.5 |  |  |  | 0 | 0.5295 |  |  | 0.066 | 0.0695 | [5 empty] | 29.3 |  |  |  |  | 58.65 |  | 24.65 |  | 6.25 | 0.072 |  | 18.25 | 77.5 | 0.5175 |  |  |  |  | 13.311 | 13.94 | [6 empty] | 28.405 |  | 17.945
2013-07-30 | 6.19 | 5.45 |  |  |  |  | 7.63 | 1.8 |  |  |  |  | 24 |  |  |  | 0 | 0.757 |  |  | 0.107 | 0.072 | [5 empty] | 28.3 |  |  |  |  | 56.6 |  | 22.8 |  | 7.1 | 0.057 |  | 18.2 | 90 | 1.03 |  |  |  |  | 15.98 | 14.05 | [6 empty] | 27.91 |  | 12.99
2013-07-31 | 6.68 | 5.42 |  |  |  |  | 7.75 | 1.94 |  |  |  |  | 26 |  |  |  | 0 | 0.569 |  |  | 0.143 | 0.08 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 28.2 |  | 8.5 | 0.107 |  | 18 | 90 | 1.03 |  |  |  |  | 15.12 | 13.74 | [6 empty] | 26.29 |  | 12.85
2013-08-01 | 6.48 | 5.34 |  |  |  |  | 7.24 | 2.08 |  |  |  |  | 27 |  |  |  | 0 | 0.675 |  |  | 0.067 | 0.068 | [5 empty] | 28.7 |  |  |  |  | 57.6 |  | 25.8 |  | 7.9 | 0.094 |  | 17.9 | 90 | 0.64 |  |  |  |  | 16.06 | 15.01 | [6 empty] | 26.29 |  | 13.84
2013-08-02 | 6.3 | 5.49 |  |  |  |  | 7.47 | 2.11 |  |  |  |  | 24 |  |  |  | 0 | 0.717 |  |  | 0.074 | 0.072 | [5 empty] | 28.6 |  |  |  |  | 57.2 |  | 23.9 |  | 8.2 | 0.091 |  | 18.2 | 90 | 0.54 |  |  |  |  | 16.458 | 15.418 | [6 empty] | 25.35 |  | 11.08
2013-08-03 | 6.24 | 5.59 |  |  |  |  | 7.88 | 2.14 |  |  |  |  | 21 |  |  |  | 0 | 0.709 |  |  | 0.098 | 0.084 | [5 empty] | 29.4 |  |  |  |  | 68.8 |  | 24.6 |  | 7.6 | 0.084 |  | 18.2 | 100 | 0.6 |  |  |  |  | 17.657 | 16.573 | [6 empty] | 24.54 |  | 11.87
2013-08-04 | 6.17 | 5.56 |  |  |  |  | 7.44 | 1.99 |  |  |  |  | 26 |  |  |  | 0 | 0.786 |  |  | 0.121 | 0.089 | [5 empty] | 27.1 |  |  |  |  | 54.2 |  | 22.3 |  | 7.2 | 0.074 |  | 18.3 | 90 | 0.56 |  |  |  |  | 16.1 | 14.08 | [6 empty] | 23.38 |  | 12.23
2013-08-05 | 6.205 | 5.575 |  |  |  |  | 7.66 | 2.065 |  |  |  |  | 23.5 |  |  |  | 0 | 0.7475 |  |  | 0.1095 | 0.0865 | [5 empty] | 28.25 |  |  |  |  | 61.5 |  | 23.45 |  | 7.4 | 0.079 |  | 18.25 | 95 | 0.58 |  |  |  |  | 16.8785 | 15.3265 | [6 empty] | 23.96 |  | 12.05
2013-08-06 | 6.44 | 5.55 |  |  |  |  | 7.26 | 2.24 |  |  |  |  | 29 |  |  |  | 0 | 0.708 |  |  | 0.382 | 0.095 | [5 empty] | 29.2 |  |  |  |  | 58.8 |  | 25.4 |  | 7.8 | 0.169 |  | 18.9 | 100 | 0.75 |  |  |  |  | 16.588 | 15.208 | [6 empty] | 24.88 |  | 14.61
2013-08-07 | 6.4 | 5.17 |  |  |  |  | 6.8 | 2.16 |  |  |  |  | 30 |  |  |  | 0 | 0.649 |  |  | 0.061 | 0.084 | [5 empty] | 27.6 |  |  |  |  | 55.2 |  | 26.1 |  | 6.8 | 0.046 |  | 18.7 | 110 | 1.04 |  |  |  |  | 16.224 | 15.607 | [6 empty] | 30.04 |  | 11.75
2013-08-08 | 6.32 | 5.34 |  |  |  |  | 7.05 | 2.08 |  |  |  |  | 27 |  |  |  | 0 | 0.817 |  |  | 0.074 | 0.089 | [5 empty] | 27.9 |  |  |  |  | 55.8 |  | 25.2 |  | 6.9 | 0.054 |  | 18.8 | 100 | 1.07 |  |  |  |  | 16.446 | 14.406 | [6 empty] | 29.94 |  | 12.15
2013-08-09 | 6.14 | 5.34 |  |  |  |  | 7.11 | 2.04 |  |  |  |  | 30 |  |  |  | 0 | 0.764 |  |  | 0.09 | 0.067 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 23.8 |  | 7.1 | 0.068 |  | 18.7 | 100 | 0.92 |  |  |  |  | 16.45 | 15.34 | [6 empty] | 30.13 |  | 12.91
2013-08-10 | 6.11 | 5.27 |  |  |  |  | 7.18 | 2.08 |  |  |  |  | 32 |  |  |  | 0 | 0.713 |  |  | 0.097 | 0.114 | [5 empty] | 27 |  |  |  |  | 54 |  | 24.4 |  | 6.8 | 0.073 |  | 19.4 | 100 | 0.92 |  |  |  |  | 16.172 | 15.143 | [6 empty] | 30.78 |  | 18.32
2013-08-11 | 6.09 | 5.38 |  |  |  |  | 7.51 | 2.06 |  |  |  |  | 30 |  |  |  | 0 | 0.627 |  |  | 0.086 | 0.117 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 25 |  | 6.9 | 0.081 |  | 19.4 | 100 | 0.92 |  |  |  |  | 15.79 | 14.13 | [6 empty] | 27.78 |  | 16.42
2013-08-12 | 6.1 | 5.325 |  |  |  |  | 7.345 | 2.07 |  |  |  |  | 31 |  |  |  | 0 | 0.67 |  |  | 0.0915 | 0.1155 | [5 empty] | 27.2 |  |  |  |  | 54.4 |  | 24.7 |  | 6.85 | 0.077 |  | 19.4 | 100 | 0.92 |  |  |  |  | 16.294 | 14.766 | [6 empty] | 29.28 |  | 17.37
2013-08-13 | 6.04 | 4.97 |  |  |  |  | 6.41 | 2.065 |  |  |  |  | 33 |  |  |  | 0 | 0.723 |  |  | 0.092 | 0.054 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 22.3 |  | 5.7 | 0.112 |  | 19.3 | 100 | 0.92 |  |  |  |  | 16.867 | 15.768 | [6 empty] | 28.34 |  | 16.73
2013-08-14 | 5.92 | 5.07 |  |  |  |  | 8.5 | 1.93 |  |  |  |  | 34 |  |  |  | 0 | 0.712 |  |  | 0.068 | 0.109 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 25.9 |  | 6.9 | 0.092 |  | 19.3 | 100 | 0.92 |  |  |  |  | 16.98 | 14.808 | [6 empty] | 31.02 |  | 16.23
2013-08-15 | 6.14 | 5.1 |  |  |  |  | 8.9 | 1.9975 |  |  |  |  | 35 |  |  |  | 0 | 0.698 |  |  | 0.093 | 0.098 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 24.9 |  | 7.8 | 0.098 |  | 18.5 | 100 | 0.92 |  |  |  |  | 15.712 | 14.629 | [6 empty] | 29.75 |  | 12.97
2013-08-16 | 6.17 | 5.57 |  |  |  |  | 7.44 | 1.9638 |  |  |  |  | 34 |  |  |  | 0 | 0.618 |  |  | 0.094 | 0.073 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 24.3 |  | 7.2 | 0.071 |  | 19.3 | 100 | 0.92 |  |  |  |  | 16.32 | 15.23 | [6 empty] | 28.32 |  | 12.2
2013-08-17 | 6.48 | 5.22 |  |  |  |  | 7.68 | 2.07 |  |  |  |  | 29 |  |  |  | 0 | 0.689 |  |  | 0.068 | 0.075 | [5 empty] | 28.7 |  |  |  |  | 57.5 |  | 26.3 |  | 7.6 | 0.068 |  | 18.3 | 100 | 0.92 |  |  |  |  | 15.804 | 14.671 | [6 empty] | 28.17 |  | 24.97
2013-08-18 | 6.63 | 5.35 |  |  |  |  | 7.34 | 2.27 |  |  |  |  | 27 |  |  |  | 0 | 0.528 |  |  | 0.059 | 0.068 | [5 empty] | 28.6 |  |  |  |  | 57.2 |  | 24.8 |  | 7.3 | 0.063 |  | 18.7 | 100 | 0.92 |  |  |  |  | 15.873 | 14.767 | [6 empty] | 28.17 |  | 15.09
2013-08-19 | 6.555 | 5.285 |  |  |  |  | 7.51 | 2.17 |  |  |  |  | 28 |  |  |  | 0 | 0.6085 |  |  | 0.0635 | 0.0715 | [5 empty] | 28.65 |  |  |  |  | 57.35 |  | 25.55 |  | 7.45 | 0.0655 |  | 18.5 | 100 | 0.92 |  |  |  |  | 16.653 | 14.598 | [6 empty] | 28.17 |  | 15.09
2013-08-20 | 6.16 | 5.12 |  |  |  |  | 6.26 | 2.22 |  |  |  |  | 28 |  |  |  | 0 | 0.468 |  |  | 0.097 | 0.064 | [5 empty] | 27.2 |  |  |  |  | 54.4 |  | 24.4 |  | 6.4 | 0.084 |  | 18.9 | 100 | 0.92 |  |  |  |  | 15.511 | 13.191 | [6 empty] | 27.18 |  | 9.65
2013-08-21 | 6.37 | 5.43 |  |  |  |  | 7.41 | 2.195 |  |  |  |  | 32 |  |  |  | 0 | 0.731 |  |  | 0.103 | 0.074 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 24.8 |  | 6.7 | 0.092 |  | 18.4 | 100 | 0.92 |  |  |  |  | 16.25 | 13.97 | [6 empty] | 30.71 |  | 11.31
2013-08-22 | 6.71 | 5.72 |  |  |  |  | 6.78 | 2.08 |  |  |  |  | 27 |  |  |  | 0 | 0.48 |  |  | 0.068 | 0.065 | [5 empty] | 27.8 |  |  |  |  | 55.6 |  | 25.2 |  | 5.9 | 0.071 |  | 17.6 | 100 | 0.92 |  |  |  |  | 14.859 | 13.742 | [6 empty] | 27.23 |  | 11.33
2013-08-23 | 6.55 | 4.68 |  |  |  |  | 6.96 | 2.26 |  |  |  |  | 26 |  |  |  | 0 | 0.433 |  |  | 0.061 | 0.067 | [5 empty] | 25.3 |  |  |  |  | 50.7 |  | 24.1 |  | 6.6 | 0.064 |  | 17.4 | 100 | 0.92 |  |  |  |  | 15.646 | 14.495 | [6 empty] | 27.7 |  | 12.45
2013-08-24 | 6.24 | 5.45 |  |  |  |  | 7.67 | 2.28 |  |  |  |  | 25 |  |  |  | 0 | 0.397 |  |  | 0.098 | 0.072 | [5 empty] | 27.1 |  |  |  |  | 54.2 |  | 23.1 |  | 6.4 | 0.069 |  | 17.5 | 100 | 0.92 |  |  |  |  | 15.073 | 14.429 | [6 empty] | 28.16 |  | 12.96
2013-08-25 | 6.39 | 5.51 |  |  |  |  | 7.73 | 2.27 |  |  |  |  | 29 |  |  |  | 0 | 0.427 |  |  | 0.079 | 0.06 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 23.3 |  | 7.1 | 0.054 |  | 17.4 | 100 | 0.92 |  |  |  |  | 14.33 | 12.66 | [6 empty] | 27.92 |  | 12.77
2013-08-26 | 6.315 | 5.48 |  |  |  |  | 7.7 | 2.275 |  |  |  |  | 27 |  |  |  | 0 | 0.412 |  |  | 0.0885 | 0.066 | [5 empty] | 27.6 |  |  |  |  | 55.2 |  | 23.2 |  | 6.75 | 0.0615 |  | 17.45 | 100 | 0.92 |  |  |  |  | 14.7015 | 13.5445 | [6 empty] | 28.04 |  | 12.865
2013-08-27 | 6.51 | 5.43 |  |  |  |  | 7.56 | 2.17 |  |  |  |  | 24 |  |  |  | 0 | 0.438 |  |  | 0.069 | 0.065 | [5 empty] | 27.6 |  |  |  |  | 55.3 |  | 21.9 |  | 7.4 | 0.066 |  | 18.4 | 100 | 0.92 |  |  |  |  | 15.121 | 13.918 | [6 empty] | 27.23 |  | 12.79
2013-08-28 | 6.63 | 5.47 |  |  |  |  | 6.86 | 2 |  |  |  |  | 24 |  |  |  | 0 | 0.411 |  |  | 0.06 | 0.066 | [5 empty] | 26.7 |  |  |  |  | 53.4 |  | 24.8 |  | 7.9 | 0.056 |  | 18.8 | 100 | 0.92 |  |  |  |  | 14.985 | 13.788 | [6 empty] | 26.29 |  | 12.11
2013-08-29 | 6.18 | 5.17 |  |  |  |  | 7.46 | 2.085 |  |  |  |  | 24 |  |  |  | 0 | 0.418 |  |  | 0.104 | 0.065 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 22.1 |  | 7.2 | 0.071 |  | 18.6 | 100 | 0.92 |  |  |  |  | 14.925 | 13.687 | [6 empty] | 26.76 |  | 12.45
2013-08-30 | 6.09 | 5.27 |  |  |  |  | 7.3 | 2 |  |  |  |  | 27 |  |  |  | 0 | 0.468 |  |  | 0.091 | 0.059 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 23.8 |  | 7.4 | 0.06 |  | 18.5 | 100 | 0.92 |  |  |  |  | 14.749 | 13.598 | [6 empty] | 28.87 |  | 12.12
2013-08-31 | 6.19 | 5.35 |  |  |  |  | 7.54 | 1.8 |  |  |  |  | 29 |  |  |  | 0 | 0.487 |  |  | 0.114 | 0.076 | [5 empty] | 27.6 |  |  |  |  | 55.2 |  | 24.4 |  | 7.2 | 0.057 |  | 17.4 | 100 | 0.92 |  |  |  |  | 14.126 | 12.856 | [6 empty] | 28.59 |  | 12.63
2013-09-01 | 6.15 | 5.05 |  |  |  |  | 7.71 | 1.86 |  |  |  |  | 26 |  |  |  | 0 | 0.415 |  |  | 0.076 | 0.067 | [5 empty] | 26.3 |  |  |  |  | 52.6 |  | 24.8 |  | 6.4 | 0.059 |  | 16.5 | 100 | 0.92 |  |  |  |  | 12.5 | 11.33 | [6 empty] | 25.14 |  | 18.22
2013-09-02 | 6.17 | 5.2 |  |  |  |  | 7.625 | 1.83 |  |  |  |  | 27.5 |  |  |  | 0 | 0.451 |  |  | 0.095 | 0.0715 | [5 empty] | 26.95 |  |  |  |  | 53.9 |  | 24.6 |  | 6.8 | 0.058 |  | 16.95 | 100 | 0.92 |  |  |  |  | 12.378 | 10.999 | [6 empty] | 26.865 |  | 15.425
2013-09-03 | 6.1 | 5.36 |  |  |  |  | 7.19 | 1.94 |  |  |  |  | 34 |  |  |  | 0 | 0.457 |  |  | 0.749 | 0.134 | [5 empty] | 25.8 |  |  |  |  | 51.6 |  | 24.1 |  | 5.9 | 0.153 |  | 16.6 | 100 | 0.92 |  |  |  |  | 13.847 | 11.684 | [6 empty] | 25.23 |  | 16.24
2013-09-04 | 6.24 | 5.32 |  |  |  |  | 7.62 | 1.89 |  |  |  |  | 33 |  |  |  | 0 | 0.455 |  |  | 0.327 | 0.09 | [5 empty] | 30.1 |  |  |  |  | 60.2 |  | 24.9 |  | 7.4 | 0.095 |  | 15.6 | 100 | 0.92 |  |  |  |  | 12.74 | 12.38 | [6 empty] | 28.43 |  | 16.59
2013-09-05 | 6.44 | 5.47 |  |  |  |  | 6.63 | 1.915 |  |  |  |  | 42 |  |  |  | 0 | 0.461 |  |  | 0.095 | 0.117 | [5 empty] | 27.8 |  |  |  |  | 55.7 |  | 26.4 |  |  | 0.086 |  |  | 100 | 0.92 |  |  |  |  | 15.708 | 12.034 | [6 empty] | 27.7 |  | 12.52
2013-09-06 | 6.39 | 5.05 |  |  |  |  | 6.88 | 2.64 |  |  |  |  | 42 |  |  |  | 0 | 0.397 |  |  | 0.201 | 0.14 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 25.1 |  | 6.2 | 0.071 |  | 14.9 | 100 | 0.92 |  |  |  |  | 15.42 | 14.05 | [6 empty] | 29.64 |  | 12.32
2013-09-07 | 6.35 | 5.03 |  |  |  |  | 8.2 | 2.11 |  |  |  |  | 42 |  |  |  | 0 | 0.37 |  |  | 0.12 | 0.08 | [5 empty] | 30.6 |  |  |  |  | 61.4 |  | 24.4 |  | 7.3 | 0.138 |  | 16 | 100 | 0.92 |  |  |  |  | 13.75 | 12.58 | [6 empty] | 29.34 |  | 12.49
2013-09-08 | 6.44 | 5.2 |  |  |  |  | 8.28 | 2.03 |  |  |  |  | 42 |  |  |  | 0 | 0.489 |  |  | 0.047 | 0.082 | [5 empty] | 30.8 |  |  |  |  | 61.8 |  | 25.6 |  | 7.2 | 0.144 |  | 15.7 | 100 | 0.92 |  |  |  |  | 13.35 | 12.21 | [6 empty] | 29.11 |  | 14.48
2013-09-09 | 6.395 | 5.115 |  |  |  |  | 8.24 | 1.81 |  |  |  |  | 42 |  |  |  | 0 | 0.4295 |  |  | 0.0835 | 0.081 | [5 empty] | 30.7 |  |  |  |  | 61.6 |  | 25 |  | 7.25 | 0.141 |  | 15.85 | 100 | 0.92 |  |  |  |  | 12.765 | 11.324 | [6 empty] | 29.11 |  | 14.48
2013-09-10 | 6.21 | 5.27 |  |  |  |  | 6.82 | 1.92 |  |  |  |  | 54 |  |  |  | 1 | 0.394 |  |  | 0.073 | 0.088 | [5 empty] | 27.2 |  |  |  |  | 54.4 |  | 24.7 |  | 6.9 | 0.032 |  | 15.7 | 100 | 0.92 |  |  |  |  | 14.361 | 12.036 | [6 empty] | 30.36 |  | 11.27
2013-09-11 | 6.01 | 4.95 |  |  |  |  | 7.13 | 1.865 |  |  |  |  | 55 |  |  |  | 0 | 0.368 |  |  | 0.076 | 0.074 | [5 empty] | 28.9 |  |  |  |  | 57.8 |  | 25.3 |  | 7.1 | 0.047 |  | 15 | 100 | 0.92 |  |  |  |  | 13.35 | 12.69 | [6 empty] | 29.34 |  | 10.82
2013-09-12 | 6.43 | 5.03 |  |  |  |  | 6.61 | 2.06 |  |  |  |  | 40 |  |  |  | 0 | 0.367 |  |  | 0.076 | 0.085 | [5 empty] | 29.8 |  |  |  |  | 59.6 |  | 25.5 |  | 7.3 | 0.11 |  | 15.2 | 100 | 0.92 |  |  |  |  | 13.75 | 12.104 | [6 empty] | 15.95 |  | 15.95
2013-09-13 | 6.39 | 5.04 |  |  |  |  | 7.09 | 2.08 |  |  |  |  | 39 |  |  |  | 0 | 0.953 |  |  | 0.068 | 0.072 | [5 empty] | 30.2 |  |  |  |  | 60.4 |  | 23.5 |  | 7.7 | 0.137 |  | 14.8 | 100 | 0.92 |  |  |  |  | 14.022 | 13.345 | [6 empty] | 31.45 |  | 13.03
2013-09-14 | 5.95 | 4.93 |  |  |  |  | 7.03 | 2.07 |  |  |  |  | 41 |  |  |  | 0 | 0.647 |  |  | 0.074 | 0.078 | [5 empty] | 31.4 |  |  |  |  | 62.8 |  | 22.8 |  | 7.2 | 0.107 |  | 14.9 | 100 | 0.92 |  |  |  |  | 14.491 | 12.839 | [6 empty] | 31.54 |  | 12.82
2013-09-15 | 6.04 | 4.9 |  |  |  |  | 6.9 | 2.13 |  |  |  |  | 40 |  |  |  | 0 | 0.617 |  |  | 0.089 | 0.071 | [5 empty] | 29.6 |  |  |  |  | 59.2 |  | 23.9 |  | 5.7 | 0.061 |  | 14.6 | 100 | 0.92 |  |  |  |  | 14.01 | 12.86 | [6 empty] | 30.09 |  | 12.41
2013-09-16 | 5.995 | 4.915 |  |  |  |  | 6.965 | 2.1 |  |  |  |  | 40.5 |  |  |  | 0 | 0.632 |  |  | 0.0815 | 0.0745 | [5 empty] | 30.5 |  |  |  |  | 61 |  | 23.35 |  | 6.45 | 0.084 |  | 14.75 | 100 | 0.92 |  |  |  |  | 14.2505 | 12.8495 | [6 empty] | 30.815 |  | 12.615
2013-09-17 | 6.64 | 4.92 |  |  |  |  | 7.44 | 2.2 |  |  |  |  | 33 |  |  |  | 0 | 0.67 |  |  | 0.065 | 0.071 | [5 empty] | 28.9 |  |  |  |  | 57.9 |  | 22.7 |  | 6.6 | 0.057 |  | 16.3 | 100 | 0.92 |  |  |  |  | 13.347 | 12.13 | [6 empty] | 28.64 |  | 12.95
2013-09-18 | 6.55 | 5.04 |  |  |  |  | 7.42 | 2.19 |  |  |  |  | 31 |  |  |  | 0 | 1.055 |  |  | 0.07 | 0.075 | [5 empty] | 29.8 |  |  |  |  | 59.7 |  | 23.1 |  | 7.3 | 0.064 |  | 16 | 100 | 0.92 |  |  |  |  | 14.198 | 13.035 | [6 empty] | 27.33 |  | 15.2
2013-09-19 | 6.595 | 4.98 |  |  |  |  | 7.43 | 2.195 |  |  |  |  | 32 |  |  |  | 0 | 0.8625 |  |  | 0.0675 | 0.073 | [5 empty] | 29.35 |  |  |  |  | 58.8 |  | 22.9 |  | 6.95 | 0.0605 |  | 16.15 | 100 | 0.92 |  |  |  |  | 13.7725 | 12.5825 | [6 empty] | 27.985 |  | 14.075
2013-09-20 | 6.4 | 4.93 |  |  |  |  | 7.84 | 2.12 |  |  |  |  | 43 |  |  |  | 0 | 1.368 |  |  | 0.081 | 0.072 | [5 empty] | 31.3 |  |  |  |  | 62.6 |  | 26.6 |  | 6.4 | 0.071 |  | 15.2 | 100 | 0.92 |  |  |  |  | 13.866 | 12.722 | [6 empty] | 30.08 |  | 14.01
2013-09-21 | 6.23 | 5.24 |  |  |  |  | 7.81 | 2.11 |  |  |  |  | 46 |  |  |  | 0 | 1.1153 |  |  | 0.086 | 0.074 | [5 empty] | 31 |  |  |  |  | 62 |  | 24.8 |  | 6.7 | 0.063 |  | 15.3 | 100 | 0.92 |  |  |  |  | 13.539 | 12.431 | [6 empty] | 31.44 |  | 14.69
2013-09-22 | 6.26 | 5.21 |  |  |  |  | 7.33 | 2.115 |  |  |  |  | 47 |  |  |  | 0 | 1.2416 |  |  | 0.103 | 0.086 | [5 empty] | 31.1 |  |  |  |  | 62.2 |  | 25.1 |  | 6.9 | 0.074 |  | 14.7 | 100 | 0.92 |  |  |  |  | 12.94 | 11.82 | [6 empty] | 31.21 |  | 10.63
2013-09-23 | 6.245 | 5.225 |  |  |  |  | 7.57 | 2.1125 |  |  |  |  | 46.5 |  |  |  | 0 | 1.1784 |  |  | 0.0945 | 0.08 | [5 empty] | 31.05 |  |  |  |  | 62.1 |  | 24.95 |  | 6.8 | 0.0685 |  | 15 | 100 | 0.92 |  |  |  |  | 14.115 | 12.738 | [6 empty] | 31.325 |  | 12.66
2013-09-24 | 6.3 | 5.27 |  |  |  |  | 7.45 | 2.1 |  |  |  |  | 51 |  |  |  | 0 | 1.21 |  |  | 0.114 | 0.081 | [5 empty] | 30.9 |  |  |  |  | 61.8 |  | 23.8 |  | 7.1 | 0.069 |  | 14.8 | 100 | 0.92 |  |  |  |  | 14.411 | 13.245 | [6 empty] | 32.53 |  | 11.51
2013-09-25 | 6.14 | 5.25 |  |  |  |  | 7.66 | 2.15 |  |  |  |  | 52 |  |  |  | 0 | 1.1942 |  |  | 0.089 | 0.072 | [5 empty] | 30.9 |  |  |  |  | 61.9 |  | 22 |  | 6.4 | 0.064 |  | 15 | 100 | 0.92 |  |  |  |  | 14.871 | 9.525 | [6 empty] | 29.9 |  | 11.05
2013-09-26 | 5.77 | 5.26 |  |  |  |  | 7.96 | 2.17 |  |  |  |  | 36 |  |  |  | 0 | 1.2021 |  |  | 0.099 | 0.078 | [5 empty] | 31.6 |  |  |  |  | 63.2 |  | 24.1 |  | 7.2 | 0.084 |  | 15.3 | 100 | 0.92 |  |  |  |  | 14.656 | 12.991 | [6 empty] | 29.62 |  | 12.97
2013-09-27 | 6.25 | 5.05 |  |  |  |  | 7.22 | 2.17 |  |  |  |  | 38 |  |  |  | 0 | 1.1982 |  |  | 0.096 | 0.074 | [5 empty] | 27.2 |  |  |  |  | 54.4 |  | 24.6 |  | 6.7 | 0.069 |  | 15.4 | 100 | 0.92 |  |  |  |  | 14.3 | 13.13 | [6 empty] | 30.68 |  | 11.71
2013-09-28 | 6.46 | 4.96 |  |  |  |  | 6.6 | 2.17 |  |  |  |  | 44 |  |  |  | 0 | 1.2002 |  |  | 0.062 | 0.073 | [5 empty] | 31.3 |  |  |  |  | 62.6 |  | 23.1 |  | 7.1 | 0.056 |  | 14.1 | 100 | 0.92 |  |  |  |  | 14.035 | 12.801 | [6 empty] | 30.98 |  | 13.4
2013-09-29 | 6.29 | 5.53 |  |  |  |  | 7.29 | 1.92 |  |  |  |  | 44 |  |  |  | 0 | 1.1992 |  |  | 0.134 | 0.085 | [5 empty] | 30.9 |  |  |  |  | 61.8 |  | 23.7 |  | 6.8 | 0.072 |  | 14 | 100 | 0.92 |  |  |  |  | 14.98 | 13.23 | [6 empty] | 29.74 |  | 13.51
2013-09-30 | 6.375 | 5.245 |  |  |  |  | 6.945 | 1.97 |  |  |  |  | 44 |  |  |  | 0 | 1.1997 |  |  | 0.098 | 0.079 | [5 empty] | 31.1 |  |  |  |  | 62.2 |  | 23.4 |  | 6.95 | 0.064 |  | 14.05 | 100 | 0.92 |  |  |  |  | 14.966 | 13.233 | [6 empty] | 29.74 |  | 13.51
2013-10-01 | 6.21 | 5.41 |  |  |  |  | 6.94 | 2 |  |  |  |  | 47 |  |  |  | 1 | 0.473 |  |  | 0.239 | 0.103 | [5 empty] | 27.6 |  |  |  |  | 55.2 |  | 23.9 |  | 6.7 | 0.099 |  | 13.7 | 100 | 0.92 |  |  |  |  | 14.683 | 13.504 | [6 empty] | 30.44 |  | 12.03
2013-10-02 | 6.06 | 5.37 |  |  |  |  | 6.67 | 1.985 |  |  |  |  | 46 |  |  |  | 0 | 0.83633 |  |  | 0.21 | 0.114 | [5 empty] | 28.6 |  |  |  |  | 57.2 |  | 24.6 |  | 6.5 | 0.084 |  | 14.3 | 100 | 0.92 |  |  |  |  | 15.31 | 13.52 | [6 empty] | 27.28 |  | 11.25
2013-10-03 | 6.35 | 5.04 |  |  |  |  | 6.39 | 2.06 |  |  |  |  | 42 |  |  |  | 0 | 1.867 |  |  | 0.091 | 0.114 | [5 empty] | 27.8 |  |  |  |  | 55.6 |  | 23.6 |  | 7.1 | 0.072 |  | 14.6 | 100 | 0.92 |  |  |  |  | 14.991 | 13.243 | [6 empty] | 28.64 |  | 13.29
2013-10-04 | 6.33 | 5.08 |  |  |  |  | 6.79 | 2.09 |  |  |  |  | 43 |  |  |  | 0 | 1.7 |  |  | 0.128 | 0.093 | [5 empty] | 28.99 |  |  |  |  | 57.9 |  | 27.5 |  | 7 | 0.075 |  | 14.9 | 100 | 0.92 |  |  |  |  | 14.689 | 13.979 | [6 empty] | 28.4 |  | 11.47
2013-10-05 | 6.13 | 4.86 |  |  |  |  | 5.47 | 2.075 |  |  |  |  | 51 |  |  |  | 0 | 1.855 |  |  | 0.204 | 0.221 | [5 empty] | 23.4 |  |  |  |  | 46.9 |  | 22.2 |  | 6 | 0.174 |  | 14.4 | 100 | 0.92 |  |  |  |  | 15.202 | 12.722 | [6 empty] | 30.08 |  | 11.77
2013-10-06 | 6.07 | 5.03 |  |  |  |  | 7.25 | 2.0825 |  |  |  |  | 49 |  |  |  | 0 | 1.7775 |  |  | 0.134 | 0.096 | [5 empty] | 26.2 |  |  |  |  | 52.4 |  | 23.7 |  | 6.4 | 0.093 |  | 14.4 | 100 | 0.92 |  |  |  |  | 14.9455 | 13.3505 | [6 empty] | 30.85 |  | 11.03
2013-10-07 | 6.1 | 4.945 |  |  |  |  | 6.36 | 2.0788 |  |  |  |  | 50 |  |  |  | 0 | 1.8162 |  |  | 0.169 | 0.1585 | [5 empty] | 24.8 |  |  |  |  | 49.65 |  | 22.95 |  | 6.2 | 0.1335 |  | 14.4 | 100 | 0.92 |  |  |  |  | 15.0738 | 13.0362 | [6 empty] | 30.465 |  | 11.4
2013-10-08 | 6.5 | 5.15 |  |  |  |  | 7.3 | 2.19 |  |  |  |  | 40 |  |  |  | 0 | 1.7969 |  |  | 0.08 | 0.08 | [5 empty] | 29.6 |  |  |  |  | 59.2 |  | 23.6 |  | 6.9 | 0.099 |  | 12.4 | 100 | 0.92 |  |  |  |  | 14.425 | 13.73 | [6 empty] | 28.17 |  | 18.42
2013-10-09 | 6.19 | 5.1 |  |  |  |  | 6.73 | 2.1344 |  |  |  |  | 41 |  |  |  | 0 | 0.765 |  |  | 0.125 | 0.095 | [5 empty] | 26.5 |  |  |  |  | 53 |  | 28.5 |  | 7.1 | 0.068 |  | 12.3 | 100 | 0.92 |  |  |  |  | 15.209 | 13.537 | [6 empty] | 31.48 |  | 14.22
2013-10-10 | 6.17 | 4.9 |  |  |  |  | 5.25 | 2.1622 |  |  |  |  | 47 |  |  |  | 0 | 0.656 |  |  | 0.144 | 0.084 | [5 empty] | 27.1 |  |  |  |  | 54.2 |  | 28.1 |  | 6.7 | 0.074 |  | 12.2 | 100 | 0.92 |  |  |  |  | 15.777 | 13.667 | [6 empty] | 30.09 |  | 13.27
2013-10-11 | 6.01 | 5.04 |  |  |  |  | 7.67 | 2.1483 |  |  |  |  | 43 |  |  |  | 0 | 0.594 |  |  | 0.109 | 0.086 | [5 empty] | 28.3 |  |  |  |  | 56.6 |  | 28.6 |  | 7.1 | 0.059 |  | 12.2 | 100 | 0.92 |  |  |  |  | 14.42 | 14.2 | [6 empty] | 30.52 |  | 13.08
2013-10-12 | 6.36 | 5.06 |  |  |  |  | 7.84 | 2.37 |  |  |  |  | 39 |  |  |  | 0 | 0.369 |  |  | 0.08 | 0.086 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 26.3 |  | 7.2 | 0.054 |  | 12 | 100 | 0.92 |  |  |  |  | 15.2 | 13.09 | [6 empty] | 30.04 |  | 13.98
2013-10-13 | 6.34 | 5.11 |  |  |  |  | 7.49 | 2.2591 |  |  |  |  | 38 |  |  |  | 0 | 0.412 |  |  | 0.076 | 0.087 | [5 empty] | 28.4 |  |  |  |  | 56.9 |  | 26.4 |  | 7 | 0.067 |  | 12 | 100 | 0.92 |  |  |  |  | 14.19 | 13.96 | [6 empty] | 30.04 |  | 17.43
2013-10-14 | 6.35 | 5.085 |  |  |  |  | 7.665 | 2.3146 |  |  |  |  | 38.5 |  |  |  | 0 | 0.3905 |  |  | 0.078 | 0.0865 | [5 empty] | 29.4 |  |  |  |  | 58.85 |  | 26.35 |  | 7.1 | 0.0605 |  | 12 | 100 | 0.92 |  |  |  |  | 13.945 | 12.658 | [6 empty] | 30.04
2013-10-15 | 6.29 | 5.26 |  |  |  |  | 7.35 | 2.2869 |  |  |  |  | 41 |  |  |  | 0 | 0.401 |  |  | 0.114 | 0.092 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 25.6 |  | 7.1 | 0.059 |  | 11.9 | 100 | 0.92 |  |  |  |  | 15.131 | 13.957 | [6 empty] | 30.04 |  | 14.29
2013-10-16 | 6.04 | 5.26 |  |  |  |  | 7.47 | 2.21 |  |  |  |  | 36 |  |  |  | 0 | 0.374 |  |  | 0.141 | 0.096 | [5 empty] | 28.7 |  |  |  |  | 57.4 |  | 25.9 |  | 6 | 0.071 |  | 11.9 | 100 | 0.92 |  |  |  |  | 14.745 | 13.426 | [6 empty] | 31.34 |  | 14.11
2013-10-17 | 5.96 | 5.25 |  |  |  |  | 7.36 | 2.2484 |  |  |  |  | 34 |  |  |  | 0 | 0.348 |  |  | 0.154 | 0.098 | [5 empty] | 29.7 |  |  |  |  | 59.4 |  | 25.3 |  | 6.3 | 0.084 |  | 10.6 | 100 | 0.92 |  |  |  |  | 15.311 | 13.153 | [6 empty] | 31.83 |  | 12.93
2013-10-18 | 6.1 | 5.07 |  |  |  |  | 6.85 | 2.22 |  |  |  |  | 36 |  |  |  | 0 | 0.368 |  |  | 0.153 | 0.114 | [5 empty] | 31.3 |  |  |  |  | 62.6 |  | 24.9 |  | 6.1 | 0.081 |  | 10.5 | 100 | 0.92 |  |  |  |  | 14.8 | 13.76 | [6 empty] | 30.44 |  | 12.14
2013-10-19 | 6.45 | 4.86 |  |  |  |  | 7.17 | 2.19 |  |  |  |  | 36 |  |  |  | 0 | 0.359 |  |  | 0.08 | 0.084 | [5 empty] | 32.3 |  |  |  |  | 64.7 |  | 23.7 |  | 7.4 | 0.072 |  | 10.3 | 100 | 0.92 |  |  |  |  | 14.609 | 13.433 | [6 empty] | 33.77 |  | 14.36
2013-10-20 | 6.34 | 4.76 |  |  |  |  | 6.46 | 2.18 |  |  |  |  | 35 |  |  |  | 0 | 0.393 |  |  | 0.139 | 0.088 | [5 empty] | 29.1 |  |  |  |  | 58 |  | 23.8 |  | 7.6 | 0.071 |  | 10.4 | 100 | 0.92 |  |  |  |  | 14.46 | 13.32 | [6 empty] | 30.98 |  | 14.78
2013-10-21 | 6.395 | 4.81 |  |  |  |  | 6.815 | 2.01 |  |  |  |  | 35.5 |  |  |  | 0 | 0.376 |  |  | 0.1095 | 0.086 | [5 empty] | 30.7 |  |  |  |  | 61.35 |  | 23.75 |  | 7.5 | 0.0715 |  | 10.35 | 100 | 0.92 |  |  |  |  | 14.184 | 12.992 | [6 empty] | 33.33 |  | 14.78
2013-10-22 | 5.67 | 5.23 |  |  |  |  | 7.48 | 2.095 |  |  |  |  | 36 |  |  |  | 0 | 0.337 |  |  | 0.186 | 0.094 | [5 empty] | 32.4 |  |  |  |  | 64.8 |  | 24.4 |  | 7.1 | 0.087 |  | 10.4 | 100 | 0.92 |  |  |  |  | 15.912 | 13.611 | [6 empty] | 33.33 |  | 15.16
2013-10-23 | 6.13 | 5.23 |  |  |  |  | 8.44 | 2.0525 |  |  |  |  | 37 |  |  |  | 0 | 1.184 |  |  | 0.107 | 0.096 | [5 empty] | 31.3 |  |  |  |  | 62.6 |  | 23.9 |  | 7.4 | 0.068 |  | 9.9 | 100 | 0.92 |  |  |  |  | 15.048 | 13.3015 | [6 empty] | 29.81 |  | 12.38
2013-10-24 | 6.32 | 5.13 |  |  |  |  | 6.93 | 2.0737 |  |  |  |  | 36 |  |  |  | 0 | 0.7605 |  |  | 0.112 | 0.083 | [5 empty] | 31.6 |  |  |  |  | 63.1 |  | 24.2 |  | 7.8 | 0.066 |  | 9.9 | 100 | 0.92 |  |  |  |  | 14.994 | 13.762 | [6 empty] | 32.51 |  | 14.79
2013-10-25 | 6.21 | 5.163 |  |  |  |  | 6.82 | 2.13 |  |  |  |  | 37 |  |  |  | 0 | 1.721 |  |  | 0.062 | 0.093 | [5 empty] | 31.3 |  |  |  |  | 62.6 |  | 25.6 |  | 7.4 | 0.071 |  | 9.5 | 100 | 0.92 |  |  |  |  | 14.705 | 13.991 | [6 empty] | 30.04 |  | 13.57
2013-10-26 | 6.12 | 5.17 |  |  |  |  | 7.58 | 2.1019 |  |  |  |  | 37 |  |  |  | 0 | 0.767 |  |  | 0.096 | 0.082 | [5 empty] | 32.4 |  |  |  |  | 64.8 |  | 26.2 |  | 6.9 | 0.063 |  | 9.5 | 100 | 0.92 |  |  |  |  | 14.642 | 7.58 | [6 empty] | 30.04 |  | 12.59
2013-10-27 | 6.37 | 5.16 |  |  |  |  | 7.88 | 2.12 |  |  |  |  | 30 |  |  |  | 0 | 0.854 |  |  | 0.078 | 0.086 | [5 empty] | 31.4 |  |  |  |  | 62.8 |  | 24.5 |  | 7.2 | 0.07 |  | 9.4 | 100 | 0.92 |  |  |  |  | 13.87 | 12.69 | [6 empty] | 30.82 |  | 30.68
2013-10-28 | 6.245 | 5.165 |  |  |  |  | 7.73 | 2.1109 |  |  |  |  | 33.5 |  |  |  | 0 | 0.8105 |  |  | 0.087 | 0.084 | [5 empty] | 31.9 |  |  |  |  | 63.8 |  | 25.35 |  | 7.05 | 0.0665 |  | 9.45 | 100 | 0.92 |  |  |  |  | 14.256 | 10.135 | [6 empty] | 13.51 |  | 21.635
2013-10-29 | 6.63 | 5.03 |  |  |  |  | 7.21 | 2.26 |  |  |  |  | 34 |  |  |  | 0 | 0.619 |  |  | 0.079 | 0.083 | [5 empty] | 31.5 |  |  |  |  | 62.9 |  | 25.3 |  | 8.6 | 0.146 |  | 8.4 | 100 | 0.92 |  |  |  |  | 14.317 | 13.143 | [6 empty] | 22.165 |  | 16.72
2013-10-30 | 6.54 | 4.99 |  |  |  |  | 6.76 | 2.21 |  |  |  |  | 32 |  |  |  | 0 | 0.756 |  |  | 0.069 | 0.13 | [5 empty] | 31 |  |  |  |  | 62 |  | 23.6 |  | 8.4 | 0.124 |  | 8.4 | 100 | 0.92 |  |  |  |  | 14.225 | 13.034 | [6 empty] | 29.11 |  | 11.28
2013-10-31 | 6.48 | 5.12 |  |  |  |  | 7.94 | 2.14 |  |  |  |  | 35 |  |  |  | 0 | 0.704 |  |  | 0.084 | 0.091 | [5 empty] | 31.4 |  |  |  |  | 62.8 |  | 22.4 |  | 7.9 | 0.099 |  | 8.4 | 100 | 0.92 |  |  |  |  | 13.815 | 12.6 | [6 empty] | 29.57 |  | 11.19
2013-11-01 | 6.41 | 5.15 |  |  |  |  | 8.13 | 2.18 |  |  |  |  | 30 |  |  |  | 0 | 0.671 |  |  | 0.074 | 0.088 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 23.3 |  | 6.9 | 0.1115 |  | 8.3 | 100 | 0.92 |  |  |  |  | 13.86 | 12.69 | [6 empty] | 30.29 |  | 13.95
2013-11-02 | 5.78 | 5.16 |  |  |  |  | 8.035 | 2.16 |  |  |  |  | 33 |  |  |  | 0 | 0.598 |  |  | 0.086 | 0.084 | [5 empty] | 31.6 |  |  |  |  | 63.2 |  | 23.7 |  | 6.7 | 0.047 |  | 7 | 100 | 0.92 |  |  |  |  | 13.626 | 12.422 | [6 empty] | 31.96 |  | 16.21
2013-11-03 | 5.8 | 5.16 |  |  |  |  | 7.43 | 2.17 |  |  |  |  | 34 |  |  |  | 0 | 0.847 |  |  | 0.089 | 0.084 | [5 empty] | 31 |  |  |  |  | 62 |  | 24.5 |  | 6.5 | 0.056 |  | 7.6 | 100 | 0.92 |  |  |  |  | 14.31 | 13.16 | [6 empty] | 31.15 |  | 16.05
2013-11-04 | 5.79 | 5.16 |  |  |  |  | 7.7325 | 2.165 |  |  |  |  | 33.5 |  |  |  | 0 | 0.7225 |  |  | 0.0875 | 0.084 | [5 empty] | 31.3 |  |  |  |  | 62.6 |  | 24.1 |  | 6.6 | 0.0515 |  | 7.3 | 100 | 0.92 |  |  |  |  | 13.037 | 11.834 | [6 empty] | 31.555 |  | 16.13
2013-11-05 | 5.99 | 5.17 |  |  |  |  | 7.48 | 2.1675 |  |  |  |  | 37 |  |  |  | 0 | 0.638 |  |  | 0.076 | 0.085 | [5 empty] | 31.5 |  |  |  |  | 63 |  | 23.6 |  | 7.1 | 0.074 |  | 8.4 | 100 | 0.92 |  |  |  |  | 14.173 | 12.953 | [6 empty] | 31.3525 |  | 14.29
2013-11-06 | 6.2 | 5.19 |  |  |  |  | 7.89 | 2.22 |  |  |  |  | 31 |  |  |  | 0 | 0.648 |  |  | 0.077 | 0.091 | [5 empty] | 30.9 |  |  |  |  | 61.8 |  | 23.8 |  | 7.1 | 0.069 |  | 7.6 | 100 | 0.92 |  |  |  |  | 14.342 | 13.076 | [6 empty] | 32.93 |  | 14.74
2013-11-07 | 6.14 | 5.19 |  |  |  |  | 8.01 | 2.1938 |  |  |  |  | 33 |  |  |  | 0 | 0.754 |  |  | 0.083 | 0.094 | [5 empty] | 31.4 |  |  |  |  | 62.8 |  | 24.5 |  | 7 | 0.058 |  | 7.1 | 100 | 0.92 |  |  |  |  | 13.283 | 12.599 | [6 empty] | 31.98 |  | 13.14
2013-11-08 | 6.09 | 5.31 |  |  |  |  | 8.1 | 2.15 |  |  |  |  | 36 |  |  |  | 0 | 0.654 |  |  | 0.112 | 0.097 | [5 empty] | 31 |  |  |  |  | 62 |  | 24 |  | 6.7 | 0.062 |  | 7 | 100 | 0.92 |  |  |  |  | 14.27 | 13.11 | [6 empty] | 30.16 |  | 12.64
2013-11-09 | 6.22 | 5.23 |  |  |  |  | 8.03 | 2.08 |  |  |  |  | 44 |  |  |  | 0 | 0.574 |  |  | 0.09 | 0.088 | [5 empty] | 31.7 |  |  |  |  | 63.5 |  | 22.7 |  | 7.1 | 0.071 |  | 6.9 | 100 | 0.92 |  |  |  |  | 14.284 | 12.608 | [6 empty] | 30.91 |  | 14.64
2013-11-10 | 6.55 | 5.19 |  |  |  |  | 8.19 | 2.11 |  |  |  |  | 39 |  |  |  | 0 | 0.579 |  |  | 0.076 | 0.092 | [5 empty] | 31.8 |  |  |  |  | 63.6 |  | 25.8 |  | 6.8 | 0.074 |  | 8 | 100 | 0.92 |  |  |  |  | 13.29 | 13.08 | [6 empty] | 28.64 |  | 14.5
2013-11-11 | 6.385 | 5.21 |  |  |  |  | 8.11 | 2.03 |  |  |  |  | 41.5 |  |  |  | 0 | 0.5765 |  |  | 0.083 | 0.09 | [5 empty] | 31.75 |  |  |  |  | 63.55 |  | 24.25 |  | 6.95 | 0.0725 |  | 7.45 | 100 | 0.92 |  |  |  |  | 12.45 | 10.811 | [6 empty] | 28.87 |  | 14.5
2013-11-12 | 5.86 | 5.18 |  |  |  |  | 7.69 | 2.07 |  |  |  |  | 38 |  |  |  | 0 | 0.387 |  |  | 0.084 | 0.083 | [5 empty] | 32.4 |  |  |  |  | 64.8 |  | 25.3 |  | 6.7 | 0.079 |  | 7.2 | 100 | 0.92 |  |  |  |  | 14.28 | 12.11 | [6 empty] | 28.87 |  | 13.09
2013-11-13 | 6.17 | 5.28 |  |  |  |  | 7.21 | 1.96 |  |  |  |  | 38 |  |  |  | 0 | 0.384 |  |  | 0.087 | 0.093 | [5 empty] | 32.4 |  |  |  |  | 64.8 |  | 24.9 |  | 6.5 | 0.081 |  | 6.2 | 100 | 0.92 |  |  |  |  | 13.05 | 12.83 | [6 empty] | 35.67 |  | 13.16
2013-11-14 | 6.12 | 5.23 |  |  |  |  | 7.05 | 2.15 |  |  |  |  | 36 |  |  |  | 0 | 0.454 |  |  | 0.064 | 0.088 | [5 empty] | 32.1 |  |  |  |  | 64.1 |  | 25.8 |  | 7.8 | 0.081 |  | 5.8 | 100 | 0.92 |  |  |  |  | 12.948 | 11.689 | [6 empty] | 33.39 |  | 14.14
2013-11-15 | 6.52 | 5.23 |  |  |  |  | 7.61 | 2.055 |  |  |  |  | 34 |  |  |  | 0 | 2.283 |  |  | 0.063 | 0.072 | [5 empty] | 30.8 |  |  |  |  | 61.6 |  | 23.4 |  | 7.3 | 0.068 |  | 5.5 | 100 | 0.92 |  |  |  |  | 13.083 | 12.948 | [6 empty] | 30.98 |  | 14.18
2013-11-16 | 6.41 | 5.14 |  |  |  |  | 7.23 | 2.1025 |  |  |  |  | 32 |  |  |  | 0 | 1.881 |  |  | 0.081 | 0.078 | [5 empty] | 31.2 |  |  |  |  | 62.4 |  | 24.1 |  | 7 | 0.057 |  | 5.4 | 100 | 0.92 |  |  |  |  | 13.457 | 12.636 | [6 empty] | 29.81 |  | 13.54
2013-11-17 | 6.24 | 5.09 |  |  |  |  | 7.19 | 2.0787 |  |  |  |  | 37 |  |  |  | 0 | 1.212 |  |  | 0.088 | 0.117 | [5 empty] | 30.2 |  |  |  |  | 60.4 |  | 23.8 |  | 6.7 | 0.076 |  | 5.1 | 100 | 0.92 |  |  |  |  | 13.27 | 12.792 | [6 empty] | 30.5 |  | 12.28
2013-11-18 | 6.325 | 5.115 |  |  |  |  | 7.21 | 2.0906 |  |  |  |  | 34.5 |  |  |  | 0 | 1.5465 |  |  | 0.0845 | 0.0975 | [5 empty] | 30.7 |  |  |  |  | 61.4 |  | 23.95 |  | 6.85 | 0.0665 |  | 5.25 | 100 | 0.92 |  |  |  |  | 13.3635 | 12.714 | [6 empty] | 29.17 |  | 12.91
2013-11-19 | 6.58 | 5.17 |  |  |  |  | 8.38 | 2.0847 |  |  |  |  | 39 |  |  |  | 0 | 0.445 |  |  | 0.069 | 0.088 | [5 empty] | 29.8 |  |  |  |  | 59.8 |  | 25.5 |  | 8.6 | 0.128 |  | 5 | 100 | 0.92 |  |  |  |  | 13.665 | 12.964 | [6 empty] | 29.835 |  | 14.95
2013-11-20 | 6.58 | 5.23 |  |  |  |  | 8.38 | 2.57 |  |  |  |  | 38 |  |  |  | 0 | 0.469 |  |  | 0.065 | 0.091 | [5 empty] | 32.6 |  |  |  |  | 64.6 |  | 26.3 |  | 7.9 | 0.116 |  | 5.5 | 100 | 0.92 |  |  |  |  | 14.194 | 12.491 | [6 empty] | 26.29 |  | 14.37
2013-11-21 | 6.37 | 5.22 |  |  |  |  | 7.68 | 2.3273 |  |  |  |  | 41 |  |  |  | 0 | 0.599 |  |  | 0.092 | 0.089 | [5 empty] | 30.6 |  |  |  |  | 61.3 |  | 23.6 |  | 6.9 | 0.072 |  | 5.6 | 100 | 0.92 |  |  |  |  | 14.153 | 12.435 | [6 empty] | 30.04 |  | 13.6
2013-11-22 | 6.19 | 5.29 |  |  |  |  | 7.33 | 2.16 |  |  |  |  | 43 |  |  |  | 0 | 0.574 |  |  | 0.084 | 0.108 | [5 empty] | 31.1 |  |  |  |  | 62.2 |  | 22.4 |  | 7.1 | 0.094 |  | 5.3 | 100 | 0.92 |  |  |  |  | 13.04 | 11.835 | [6 empty] | 29.57 |  | 14.22
2013-11-23 | 6.28 | 5.255 |  |  |  |  | 7.505 | 2.2437 |  |  |  |  | 42 |  |  |  | 0 | 0.5865 |  |  | 0.088 | 0.0985 | [5 empty] | 30.85 |  |  |  |  | 61.75 |  | 23 |  | 7 | 0.083 |  | 5.45 | 100 | 0.92 |  |  |  |  | 14.507 | 12.911 | [6 empty] | 29.82 | 5.8 | 7.3
2013-11-24 | 6.06 | 4.79 |  |  |  |  | 6.22 | 1.94 |  |  |  |  | 34 |  |  |  | 0 | 0.564 |  |  | 0.171 | 0.354 | [5 empty] | 25.7 |  |  |  |  | 51.4 |  | 22.7 |  | 6.5 | 0.071 |  | 3.9 | 100 | 0.92 |  |  |  |  | 13.764 | 12.548 | [6 empty] | 33.46 | 6 | 5.82
2013-11-25 | 6.17 | 5.0225 |  |  |  |  | 6.8625 | 2.0918 |  |  |  |  | 38 |  |  |  | 0 | 0.57525 |  |  | 0.1295 | 0.22625 | [5 empty] | 28.275 |  |  |  |  | 56.575 |  | 22.85 |  | 6.75 | 0.077 |  | 4.675 | 100 | 0.92 |  |  |  |  | 14.1355 | 12.7295 | [6 empty] | 29.99 | 5.9 | 6.56
2013-11-26 | 6.54 | 4.99 |  |  |  |  | 7.78 | 2.39 |  |  |  |  | 42 |  |  |  | 0 | 0.592 |  |  | 0.078 | 0.09 | [5 empty] | 31.4 |  |  |  |  | 62.8 |  | 22.3 |  | 7.1 | 0.094 |  | 3.9 | 100 | 0.92 |  |  |  |  | 14.508 | 12.794 | [6 empty] | 31.725 | 5.95 | 12.25
2013-11-27 | 6.41 | 5.43 |  |  |  |  | 6.73 | 2.57 |  |  |  |  | 33 |  |  |  | 0 | 0.655 |  |  | 0.133 | 0.385 | [5 empty] | 30.6 |  |  |  |  | 61.2 |  | 21.5 |  | 6.7 | 0.054 |  | 2.8 | 100 | 0.92 |  |  |  |  | 14.024 | 13.233 | [6 empty] | 31.38 | 5 | 9.405
2013-11-28 | 6.24 | 5.04 |  |  |  |  | 6.77 | 2.4 |  |  |  |  | 35 |  |  |  | 0 | 1.316 |  |  | 0.124 | 0.108 | [5 empty] | 31.6 |  |  |  |  | 63.2 |  | 22.4 |  | 6.9 | 0.061 |  | 2.8 | 100 | 0.92 |  |  |  |  | 14.434 | 12.753 | [6 empty] | 28.02 | 5 | 12.58
2013-11-29 | 6.25 | 4.89 |  |  |  |  | 6.94 | 2.38 |  |  |  |  | 36 |  |  |  | 0 | 1.108 |  |  | 0.186 | 0.104 | [5 empty] | 37.2 |  |  |  |  | 74.4 |  | 23.8 |  | 6.4 | 0.084 |  | 2.7 | 100 | 0.92 |  |  |  |  | 13.64 | 14.4 | [6 empty] | 29.19 | 5 | 13.95
2013-11-30 | 6.31 | 5.06 |  |  |  |  | 7.16 | 2.42 |  |  |  |  | 51 |  |  |  | 0 | 1.446 |  |  | 0.071 | 0.116 | [5 empty] | 33 |  |  |  |  | 66 |  | 26.6 |  | 8.1 | 0.072 |  | 3.6 | 100 | 0.92 |  |  |  |  | 13.428 | 12.169 | [6 empty] | 36.22 | 5 | 6.09
2013-12-01 | 6.22 | 5 |  |  |  |  | 6.84 | 2.26 |  |  |  |  | 56 |  |  |  | 0 | 1.006 |  |  | 0.077 | 0.166 | [5 empty] | 31.6 |  |  |  |  | 63.2 |  | 25.4 |  | 7.8 | 0.082 |  | 3.1 | 100 | 0.92 |  |  |  |  | 14.09 | 12.95 | [6 empty] | 34.27 | 5 | 10.02
2013-12-02 | 6.265 | 5.03 |  |  |  |  | 7 | 2.34 |  |  |  |  | 53.5 |  |  |  | 0 | 1.226 |  |  | 0.074 | 0.141 | [5 empty] | 32.3 |  |  |  |  | 64.6 |  | 26 |  | 7.95 | 0.077 |  | 3.35 | 100 | 0.92 |  |  |  |  | 13.445 | 12.112 | [6 empty] | 30.51 | 5 | 8.055
2013-12-03 | 5.94 | 4.82 |  |  |  |  | 4.42 | 2.03 |  |  |  |  | 43 |  |  |  | 0 | 0.724 |  |  | 0.386 | 0.094 | [5 empty] | 27.1 |  |  |  |  | 54.2 |  | 25.6 |  | 6 | 0.153 |  | 2.8 | 100 | 0.92 |  |  |  |  | 14.92 | 12.362 | [6 empty] | 32.39 | 5 | 9.0375
2013-12-04 | 5.87 | 4.96 |  |  |  |  | 6.57 | 2.1 |  |  |  |  | 52 |  |  |  | 0 | 0.636 |  |  | 0.113 | 0.18 | [5 empty] | 29.6 |  |  |  |  | 59.2 |  | 24.4 |  | 6.2 | 0.071 |  | 2.8 | 100 | 0.92 |  |  |  |  | 14.6 | 13.25 | [6 empty] | 24.58 | 5 | 8.5463
2013-12-05 | 6.22 | 4.7 |  |  |  |  | 4.99 | 2.27 |  |  |  |  | 59 |  |  |  | 0 | 0.616 |  |  | 0.202 | 0.087 | [5 empty] | 28.6 |  |  |  |  | 57.2 |  | 23.9 |  | 2.2 | 2 |  | 2.9 | 100 | 0.92 |  |  |  |  | 13.914 | 13.033 | [6 empty] | 28.485 | 5 | 7.22
2013-12-06 | 6.15 | 4.87 |  |  |  |  | 5.56 | 1.95 |  |  |  |  | 58 |  |  |  | 0 | 0.991 |  |  | 0.131 | 0.197 | [5 empty] | 25.9 |  |  |  |  | 51.9 |  | 12.4 |  | 2 | 0.207 |  | 3 | 100 | 0.92 |  |  |  |  | 13.28 | 12.596 | [6 empty] | 34.74 | 5 | 7.48
2013-12-07 | 6.21 | 5.06 |  |  |  |  | 7.59 | 2.11 |  |  |  |  | 47 |  |  |  | 0 | 1.018 |  |  | 0.101 | 0.141 | [5 empty] | 33.1 |  |  |  |  | 66.2 |  | 20.1 |  | 5.6 | 0.101 |  | 3.1 | 100 | 0.92 |  |  |  |  | 14.588 | 12.966 | [6 empty] | 32.29 | 5.7 | 9.5
2013-12-08 | 6.25 | 5.06 |  |  |  |  | 7.29 | 2.03 |  |  |  |  | 42 |  |  |  | 0 | 0.897 |  |  | 0.092 | 0.261 | [5 empty] | 32.6 |  |  |  |  | 65.2 |  | 18 |  | 5.4 | 0.073 |  | 3.2 | 100 | 0.92 |  |  |  |  | 13.934 | 12.781 | [6 empty] | 33.515 | 6 | 7
2013-12-09 | 6.23 | 5.06 |  |  |  |  | 7.44 | 2.07 |  |  |  |  | 44.5 |  |  |  | 0 | 0.9575 |  |  | 0.0965 | 0.201 | [5 empty] | 32.85 |  |  |  |  | 65.7 |  | 19.05 |  | 5.5 | 0.087 |  | 3.15 | 100 | 0.92 |  |  |  |  | 14.261 | 12.8735 | [6 empty] | 30.07 | 5.85 | 8.25
2013-12-10 | 5.92 | 5.26 |  |  |  |  | 7.25 | 2.05 |  |  |  |  | 56 |  |  |  | 0 | 0.803 |  |  | 0.079 | 0.205 | [5 empty] | 29.4 |  |  |  |  | 58.7 |  | 26.4 |  | 6.3 | 0.71 |  |  | 100 | 0.92 |  |  |  |  | 14.571 | 12.431 | [6 empty] | 31.7925 | 6 | 6.8
2013-12-11 | 5.93 | 4.94 |  |  |  |  | 7.12 | 2.06 |  |  |  |  | 53 |  |  |  | 0 | 0.842 |  |  | 0.07 | 0.174 | [5 empty] | 31.8 |  |  |  |  | 63.7 |  | 22.7 |  | 6.8 | 0.068 |  | 2.8 | 100 | 0.92 |  |  |  |  | 14.056 | 1.811 | [6 empty] | 32.86 | 6.7 | 6.8
2013-12-12 | 5.925 | 5.1 |  |  |  |  | 7.185 | 2.055 |  |  |  |  | 54.5 |  |  |  | 0 | 0.8225 |  |  | 0.0745 | 0.1895 | [5 empty] | 30.6 |  |  |  |  | 61.2 |  | 24.55 |  | 6.55 | 0.389 |  | 1.4 | 100 | 0.92 |  |  |  |  | 13.368 | 11.167 | [6 empty] | 32.87 | 6.35 | 6.8
2013-12-13 | 6.14 | 5.31 |  |  |  |  | 7.36 | 2.0575 |  |  |  |  | 38 |  |  |  | 0 | 0.794 |  |  | 0.077 | 0.119 | [5 empty] | 32 |  |  |  |  | 64 |  | 23.8 |  | 5.4 | 0.054 |  | 2.7 | 100 | 0.92 |  |  |  |  | 14.695 | 12.997 | [6 empty] | 32.865 | 7 | 7
2013-12-14 | 5.82 | 5.3 |  |  |  |  | 7.71 | 2.0562 |  |  |  |  | 37 |  |  |  | 0 | 0.896 |  |  | 0.083 | 0.094 | [5 empty] | 31.9 |  |  |  |  | 63.9 |  | 23.9 |  | 6.8 | 0.059 |  | 2.7 | 100 | 0.92 |  |  |  |  | 15.074 | 14.326 | [6 empty] | 31.71 | 7 | 6.8
2013-12-15 | 5.44 | 5.1 |  |  |  |  | 6.97 | 2.0569 |  |  |  |  | 37.5 |  |  |  | 0 | 0.843 |  |  | 0.08 | 0.167 | [5 empty] | 31.95 |  |  |  |  | 63.95 |  | 23.85 |  | 6.1 | 0.0565 |  | 2.7 | 100 | 0.92 |  |  |  |  | 14.618 | 13.356 | [6 empty] | 31.05 | 7 | 6.9
2013-12-16 | 5.63 | 5.2 |  |  |  |  | 7.34 | 2.0566 |  |  |  |  | 37.25 |  |  |  | 0 | 0.8695 |  |  | 0.0815 | 0.1305 | [5 empty] | 31.925 |  |  |  |  | 63.925 |  | 23.875 |  | 6.45 | 0.05775 |  | 2.7 | 100 | 0.92 |  |  |  |  | 14.846 | 13.841 | [6 empty] | 31.38 | 7 | 6.85
2013-12-17 | 5.94 | 5.14 |  |  |  |  | 7.3 | 2.0567 |  |  |  |  | 50 |  |  |  | 0 | 0.761 |  |  | 0.091 | 0.119 | [5 empty] | 31.6 |  |  |  |  | 63.2 |  | 24.4 |  | 7.9 | 0.064 |  | 2.6 | 100 | 0.92 |  |  |  |  | 14.866 | 13.598 | [6 empty] | 31.215 | 6.4 | 7.3
2013-12-18 | 6.29 | 5.2 |  |  |  |  | 7.62 | 2.0566 |  |  |  |  | 48 |  |  |  | 0 | 0.706 |  |  | 0.097 | 0.105 | [5 empty] | 29.8 |  |  |  |  | 59.6 |  | 21.8 |  | 7.7 | 0.072 |  | 2.7 | 100 | 0.92 |  |  |  |  | 15.657 | 14.455 | [6 empty] | 31.92 | 6.4 | 7.3
2013-12-19 | 6.17 | 5.37 |  |  |  |  | 7.26 | 2.0567 |  |  |  |  | 44 |  |  |  | 0 | 0.651 |  |  | 0.1 | 0.101 | [5 empty] | 32.4 |  |  |  |  | 64.8 |  | 22.5 |  | 6.9 | 0.069 |  | 2.7 | 100 | 0.92 |  |  |  |  | 14.571 | 13.567 | [6 empty] | 30.75 | 6.4 | 7.3
2013-12-20 | 5.9 | 5.39 |  |  |  |  | 7.37 | 2.0567 |  |  |  |  | 46 |  |  |  | 0 | 0.642 |  |  | 0.094 | 0.104 | [5 empty] | 30.8 |  |  |  |  | 61.6 |  | 22.5 |  | 7.4 | 0.061 |  | 2.6 | 100 | 0.92 |  |  |  |  | 15.239 | 14.252 | [6 empty] | 29.76 | 6.4 | 7.3
2013-12-21 | 6.24 | 5.42 |  |  |  |  | 7.33 | 2.0567 |  |  |  |  | 43 |  |  |  | 0 | 0.578 |  |  | 0.081 | 0.105 | [5 empty] | 32.1 |  |  |  |  | 64.3 |  | 23.1 |  | 6.8 | 0.066 |  | 2.7 | 100 | 0.92 |  |  |  |  | 15.549 | 13.993 | [6 empty] | 30.74 | 6.4 | 7.3
2013-12-22 | 6.31 | 5.25 |  |  |  |  | 7.23 | 2.0567 |  |  |  |  | 44 |  |  |  | 0 | 0.538 |  |  | 0.079 | 0.104 | [5 empty] | 31.2 |  |  |  |  | 62.5 |  | 23.6 |  | 7.3 | 0.072 |  | 2.6 | 100 | 0.92 |  |  |  |  | 15.394 | 14.1225 | [6 empty] | 30.28 | 5.8 | 7.3
2013-12-23 | 6.275 | 5.335 |  |  |  |  | 7.28 | 2.0567 |  |  |  |  | 43.5 |  |  |  | 0 | 0.558 |  |  | 0.08 | 0.1045 | [5 empty] | 31.65 |  |  |  |  | 63.4 |  | 23.35 |  | 7.05 | 0.069 |  | 2.65 | 100 | 0.92 |  |  |  |  | 15.4715 | 14.0578 | [6 empty] | 33.46 | 6.1 | 7.3
2013-12-24 | 5.92 | 5.3 |  |  |  |  | 6.8 | 2.0567 |  |  |  |  | 46 |  |  |  | 0 | 0.674 |  |  | 0.104 | 0.108 | [5 empty] | 29.9 |  |  |  |  | 59.8 |  | 23.8 |  | 7.1 | 0.064 |  | 2.7 | 100 | 0.92 |  |  |  |  | 15.637 | 14.384 | [6 empty] | 31.87 | 5.8 | 7.3
2013-12-25 | 5.99 | 5.26 |  |  |  |  | 7.33 | 2.0567 |  |  |  |  | 45 |  |  |  | 0 | 0.654 |  |  | 0.113 | 0.104 | [5 empty] | 31.3 |  |  |  |  | 62.6 |  | 22.3 |  | 7.3 | 0.071 |  | 2.6 | 100 | 0.92 |  |  |  |  | 15.5542 | 14.2209 | [6 empty] | 33.46 | 5.8 | 7.3
2013-12-26 | 6.3 | 5.41 |  |  |  |  | 7.11 | 2.0567 |  |  |  |  | 46 |  |  |  | 0 | 0.548 |  |  | 0.08 | [6 empty] | 31.4 |  |  |  |  | 62.9 |  | 23.8 |  | 7.4 | 0.074 |  | 2.4 | 100 | 0.92 |  |  |  |  | 15.5956 | 14.3024 | [6 empty] | 23.6 | 5.6 | 7.3
2013-12-27 | 6.35 | 5.39 |  |  |  |  | 6.91 | 2.0567 |  |  |  |  | 44 |  |  |  | 0 | 0.538 |  |  | 0.083 | 0.112 | [5 empty] | 30.6 |  |  |  |  | 61.2 |  | 22.5 |  | 6.8 | 0.069 |  | 2.5 | 100 | 0.92 |  |  |  |  | 15.5749 | 14.2617 | [6 empty] | 27.7 | 5.6 | 7.3
2013-12-28 | 6.29 | 5.31 |  |  |  |  | 6.87 | 2.0567 |  |  |  |  | 40 |  |  |  | 0 | 0.634 |  |  | 0.109 | 0.227 | [5 empty] | 31.3 |  |  |  |  | 62.6 |  | 22.7 |  | 6 | 0.056 |  | 2.4 | 100 | 0.92 |  |  |  |  | 15.5853 | 14.282 | [6 empty] | 27.7 | 5.6 | 7.3
2013-12-29 | 6.32 | 5.35 |  |  |  |  | 6.89 | 2.0567 |  |  |  |  | 42 |  |  |  | 0 | 0.586 |  |  | 0.096 | 0.1695 | [5 empty] | 30.95 |  |  |  |  | 61.9 |  | 22.6 |  | 6.4 | 0.0625 |  | 2.45 | 100 | 0.92 |  |  |  |  | 15.5801 | 14.2719 | [6 empty] | 28.55 | 5.6 | 7.3
2013-12-30 | 6.29 | 5.32 |  |  |  |  | 6.9 | 2.0567 |  |  |  |  | 41 |  |  |  | 0 | 0.547 |  |  | 0.137 | 0.202 | [5 empty] | 31.7 |  |  |  |  | 63.4 |  | 25.8 |  | 6.4 | 0.081 |  | 2.5 | 100 | 0.92 |  |  |  |  | 15.5827 | 14.2769 | [6 empty] | 28.125 | 5.8 | 7.6
2013-12-31 | 6.25 | 5.23 |  |  |  |  | 6.84 | 2.0567 |  |  |  |  | 46 |  |  |  | 0 | 0.465 |  |  | 0.073 | 0.238 | [5 empty] | 31.5 |  |  |  |  | 63.2 |  | 23.3 |  | 7.1 | 0.063 |  | 2.5 | 100 | 0.92 |  |  |  |  | 15.5814 | 14.2744 | [6 empty] | 28.68 | 5.8 | 8
| 5.01 | 5.12 |  |  |  |  | 7.08 | 2.0567 |  |  |  |  | 43 |  |  |  | 0 | 0.452 |  |  | 0.077 | 0.225 | [5 empty] | 31.5 |  |  |  |  | 63 |  | 26.8 |  | 6.8 | 0.034 |  | 2.5 | 100 | 0.92 |  |  |  |  | 15.582 | 14.2757 | [6 empty] | 31.45 | 5.8 | 8.3

## 2014
All of the data presented below was copied verbatim from spreadsheets transcribed by Debbie Rideout, Town PLO
| pH | [6 empty] | Chlorine |  |  |  | Colour | [5 empty] | Turbidity | [5 empty] | Total Dissolved Solids |  |  |  |  | Conductivity |  |  |  |  | Hardness |  | Alkalinity |  | Aluminum | Temperature |  | Cl Used | Cl Demand | UVT |  | UVA |  | Flows within plant |  |  |  | Flows from plant |  |  | Chemical Dosages |  |  |  |  | Dennis Penney
Date | Raw | PTC | PTC (OL) | SWC | Filter | Finish (OL) | Finish | Free | Total | Sample | Analyzer | Raw A | Raw T | SWC A | Filter A | Finish A | Finish T | Raw | Raw (OL) | SWC | Filter | Finish | Finish (OL) | Raw | PTC | SWC | Filter | Finish | Raw | PTC | SWC | Filter | Finish | Raw | Finish | Raw | Finish | Finish (Free) | Raw | Finish |  |  | Raw | Filter | Raw | Filter | Raw | Finish | Filter | Backwash | Bishop's | Botwood | GFW | Chlorine | Alum | Lime (Pre) | Lime (Post) |  | Jerry Loveless
2009-01-01 | 6.19 | 5.23 | [5 empty] | 1.7367 |  |  |  |  | 42 |  |  |  | 0 | 0.389 |  |  | 0.102 | 0.246 | [5 empty] | 30.9 |  |  |  |  | 61.8 |  | 25.7 |  | 6.4 | 0.052 |  | 2.5 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 29.99 | 5.8 | 8.3 | 2009-01-01 | Noland Simms
2009-01-02 | 6.31 | 5.23 | [5 empty] | 1.7367 |  |  |  |  | 43 |  |  |  | 0 | 0.429 |  |  | 0.097 | 0.231 | [5 empty] | 29.4 |  |  |  |  | 58.8 |  | 26.4 |  | 6.9 | 0.062 |  | 2.4 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 29.32 | 5.8 | 8.3 | 2009-01-02
2009-01-03 | 5.92 | 5.29 | [5 empty] | 1.7367 |  |  |  |  | 54 |  |  |  | 3 | 0.426 |  |  | 0.083 | 0.248 | [5 empty] | 31.2 |  |  |  |  | 62.4 |  | 25.8 |  | 6.3 | 0.106 |  | 2.4 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 32.28 | 5.8 | 8.3 | 2009-01-03
2009-01-04 | 6.43 | 5.33 | [5 empty] | 1.7367 |  |  |  |  | 55 |  |  |  | 1 | 0.416 |  |  | 0.092 | 0.205 | [5 empty] | 34 |  |  |  |  | 68 |  | 24.6 |  | 6.6 | 0.097 |  | 2.5 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 33.49 | 5.4 | 8.8 | 2009-01-04 | Continuous
2009-01-05 | 5.915 | 5.24 | [5 empty] | 1.7367 |  |  |  |  | 48.5 |  |  |  | 0 | 0.4135 |  |  | 0.151 | 0.2525 | [5 empty] | 33.8 |  |  |  |  | 67.6 |  | 23.15 |  | 6.35 | 0.092 |  | 2.5 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 32.885 | 5.6 | 8.55 | 2009-01-05 | Grab
2009-01-06 | 5.4 | 5.15 | [5 empty] | 1.7367 |  |  |  |  | 42 |  |  |  | 3 | 0.411 |  |  | 0.21 | 0.3 | [5 empty] | 33.6 |  |  |  |  | 67.2 |  | 21.7 |  | 6.1 | 0.087 |  | 2.5 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 33.1875 | 5.5 | 8.675 | 2009-01-06 | ^ Stuff for form dropdown menus
2009-01-07 | 6.18 | 5.29 | [5 empty] | 1.7367 |  |  |  |  | 37 |  |  |  | 0 | 0.476 |  |  | 0.097 | 0.276 | [5 empty] | 31.5 |  |  |  |  | 62.8 |  | 22.2 |  | 8.8 | 0.037 |  | 2.5 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 31.92 | 5.2 | 9 | 2009-01-07
2009-01-08 | 6.22 | 5.28 | [5 empty] | 1.7367 |  |  |  |  | 43 |  |  |  | 0 | 0.495 |  |  | 0.304 | 0.298 | [5 empty] | 33 |  |  |  |  | 66.1 |  | 24.1 |  | 8.5 | 0.03 |  | 3.1 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 31.69 | 5 | 9.7 | 2009-01-08
2009-01-09 | 6.13 | 5.25 | [5 empty] | 1.7367 |  |  |  |  | 47 |  |  |  | 3 | 0.493 |  |  | 0.111 | 0.299 | [5 empty] | 32.8 |  |  |  |  | 65.6 |  | 24.8 |  | 7.4 | 0.0711 |  | 2.6 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 29.13 | 4.5 | 9.7 | 2009-01-09
2009-01-10 | 6.28 | 5.19 | [5 empty] | 1.7367 |  |  |  |  | 43 |  |  |  | 0 | 0.48 |  |  | 0.118 | 0.247 | [5 empty] | 33.5 |  |  |  |  | 67.1 |  | 23.5 |  | 7.5 | 0.103 |  | 2.6 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 30.04 | 4.5 | 10.8 | 2009-01-10
2009-01-11 | 6.15 | 5.32 | [5 empty] | 1.7367 |  |  |  |  | 41 |  |  |  | 0 | 0.494 |  |  | 0.135 | 0.326 | [5 empty] | 33.4 |  |  |  |  | 66.7 |  | 22.8 |  | 8.4 | 0.112 |  | 2.7 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 31.69 | 4 | 10 | 2009-01-11
2009-01-12 | 6.095 | 5.27 | [5 empty] | 1.7367 |  |  |  |  | 45 |  |  |  | 0 | 0.4785 |  |  | 0.287 | 0.448 | [5 empty] | 33.6 |  |  |  |  | 67.15 |  | 22.8 |  | 7.4 | 0.1215 |  | 2.7 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 30.91 | 4 | 10 | 2009-01-12
2009-01-13 | 6.04 | 5.22 | [5 empty] | 1.7367 |  |  |  |  | 49 |  |  |  | 4 | 0.463 |  |  | 0.439 | 0.57 | [5 empty] | 33.8 |  |  |  |  | 67.6 |  | 22.8 |  | 6.4 | 0.131 |  | 2.7 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 30.13 | 4 | 10 | 2009-01-13
2009-01-14 | 6.12 | 5.1 | [5 empty] | 1.7367 |  |  |  |  | 30 |  |  |  | 0 | 0.413 |  |  | 0.222 | 0.42 | [5 empty] | 34.5 |  |  |  |  | 69 |  | 23.4 |  | 6.7 | 0.094 |  | 2.7 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 31.27 | 2.6 | 12.9 | 2009-01-14
2009-01-15 | 6.05 | 4.85 | [5 empty] | 1.7367 |  |  |  |  | 49 |  |  |  | 0 | 0.49 |  |  | 0.276 | 0.279 | [5 empty] | 35.2 |  |  |  |  | 70.6 |  | 22.9 |  | 11.5 | 0.147 |  | 2.7 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 29.1 | 2.2 | 14.2 | 2009-01-15
2009-01-16 | 6.22 | 5.07 | [5 empty] | 1.7367 |  |  |  |  | 34 |  |  |  | 0 | 0.456 |  |  | 0.081 | 0.433 | [5 empty] | 34.8 |  |  |  |  | 69.7 |  | 26.3 |  | 8.8 | 0.003 |  | 2.7 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 31.69 | 2.2 | 13.8 | 2009-01-16
2009-01-17 | 6.17 | 5.16 | [5 empty] | 1.7367 |  |  |  |  | 42 |  |  |  | 0 | 0.497 |  |  | 0.127 | 0.452 | [5 empty] | 32.1 |  |  |  |  | 64.2 |  | 28.3 |  | 8.1 | 0.061 |  | 2.8 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 32.24 | 2.7 | 14.4 | 2009-01-17
2009-01-18 | 6.09 | 5.37 | [5 empty] | 1.7367 |  |  |  |  | 38 |  |  |  | 0 | 0.488 |  |  | 0.107 | 0.471 | [5 empty] | 29.9 |  |  |  |  | 59.8 |  | 23.8 |  | 7.8 | 0.056 |  | 2.7 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 32.1 | 2.7 | 14.4 | 2009-01-18
2009-01-19 | 6.095 | 4.975 | [5 empty] | 1.7367 |  |  |  |  | 43 |  |  |  | 0 | 0.4855 |  |  | 0.1 | 0.4155 | [5 empty] | 33.05 |  |  |  |  | 66.1 |  | 23.75 |  | 9 | 0.065 |  | 2.85 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 32.48 | 2.85 | 14.4 | 2009-01-19
2009-01-20 | 6.1 | 4.58 | [5 empty] | 1.7367 |  |  |  |  | 48 |  |  |  | 0 | 0.483 |  |  | 0.093 | 0.36 | [5 empty] | 36.2 |  |  |  |  | 72.4 |  | 23.7 |  | 10.2 | 0.074 |  | 3 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 32.86 | 3 | 14.4 | 2009-01-20
2009-01-21 | 6.26 | 4.89 | [5 empty] | 1.7367 |  |  |  |  | 43 |  |  |  | 0 | 0.471 |  |  | 0.082 | 0.358 | [5 empty] | 36.9 |  |  |  |  | 73.8 |  | 21.6 |  | 9.8 | 0.111 |  | 3 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 32.86 | 3.2 | 13.8 | 2009-01-21
2009-01-22 | 6.2 | 5.05 | [5 empty] | 1.7367 |  |  |  |  | 39 |  |  |  | 0 | 0.452 |  |  | 0.109 | 0.3 | [5 empty] | 33.2 |  |  |  |  | 66.4 |  | 22.5 |  | 8.7 | 0.094 |  | 3 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 33.86 | 3.5 | 13.8 | 2009-01-22
2009-01-23 | 6.14 | 5.07 | [5 empty] | 1.7367 |  |  |  |  | 46 |  |  |  | 0 | 0.441 |  |  | 0.099 | 0.197 | [5 empty] | 34.7 |  |  |  |  | 69.4 |  | 23.8 |  | 7.7 | 0.054 |  | 2.9 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 33.12 | 3.8 | 13.8 | 2009-01-23
2009-01-24 | 6.07 | 5.04 | [5 empty] | 1.7367 |  |  |  |  | 44 |  |  |  | 0 | 0.413 |  |  | 0.104 | 0.264 | [5 empty] | 35.3 |  |  |  |  | 70.6 |  | 23.9 |  | 7.5 | 0.061 |  | 3 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 33.15 | 3.9 | 13.8 | 2009-01-24
2009-01-25 | 5.61 | 5.19 | [5 empty] | 1.7367 |  |  |  |  | 48 |  |  |  | 0 | 0.424 |  |  | 0.085 | 0.224 | [5 empty] | 35 |  |  |  |  | 70 |  | 23.5 |  | 8.4 | 0.096 |  | 2.8 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 32.57 | 4.5 | 13 | 2009-01-25
2009-01-26 | 5.735 | 5.3 | [5 empty] | 1.7367 |  |  |  |  | 45 |  |  |  | 0 | 0.4075 |  |  | 0.086 | 0.2235 | [5 empty] | 33.6 |  |  |  |  | 67.2 |  | 24.65 |  | 8.5 | 0.0785 |  | 2.75 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 33.14 | 4.95 | 12.7 | 2009-01-26
2009-01-27 | 5.86 | 5.41 | [5 empty] | 1.7367 |  |  |  |  | 42 |  |  |  | 0 | 0.391 |  |  | 0.087 | 0.223 | [5 empty] | 32.2 |  |  |  |  | 64.4 |  | 25.8 |  | 8.6 | 0.061 |  | 2.7 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 33.71 | 5.4 | 12.4 | 2009-01-27
2009-01-28 | 6.01 | 5.28 | [5 empty] | 1.7367 |  |  |  |  | 43 |  |  |  | 0 | 0.407 |  |  | 0.104 | 0.251 | [5 empty] | 30.5 |  |  |  |  | 61 |  | 22.3 |  | 7.8 | 0.079 |  | 2.9 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 32.89 | 5 | 11.6 | 2009-01-28
2009-01-29 | 5.68 | 5.13 | [5 empty] | 1.7367 |  |  |  |  | 44 |  |  |  | 0 | 0.39 |  |  | 0.11 | 0.199 | [5 empty] | 35.3 |  |  |  |  | 70.6 |  | 23.3 |  | 7.7 | 0.068 |  | 2.7 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 32.69 | 5.4 | 11.6 | 2009-01-29
2009-01-30 | 5.82 | 4.95 | [5 empty] | 1.7366 |  |  |  |  | 45 |  |  |  | 3 | 0.364 |  |  | 0.078 | 0.24 | [5 empty] | 33.9 |  |  |  |  | 67.8 |  | 23.8 |  | 7.4 | 0.097 |  | 2.8 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 31.49 | 5.5 | 11.6 | 2009-01-30
2009-01-31 | 6.03 | 5.23 | [5 empty] | 1.7368 |  |  |  |  | 44 |  |  |  | 0 | 0.372 |  |  | 0.077 | 0.263 | [5 empty] | 34.8 |  |  |  |  | 69.5 |  | 22.8 |  | 10.4 | 0.086 |  | 2.9 | 48.9089 | 0.12583 |  |  |  |  | 14.207 | 13.163 | [6 empty] | 29.11 | 6.4 | 13 | 2009-01-31
2009-02-01 | 6.12 | 5.01 | [5 empty] | 1.7364 |  |  |  |  | 44 |  |  |  | 0 | 0.382 |  |  | 0.078 | 0.162 | [5 empty] | 35.2 |  |  |  |  | 70.3 |  | 26.2 |  | 10.1 | 0.081 |  | 2.9 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 30.51 | 7 | 13
2009-02-02 | 6.115 | 5.21 | [5 empty] | 1.7372 |  |  |  |  | 44 |  |  |  | 0 | 0.377 |  |  | 0.107 | 0.159 | [5 empty] | 35.35 |  |  |  |  | 70.65 |  | 25.5 |  | 10 | 0.0775 |  | 2.8 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 31.185 | 7.25 | 12.5
2009-02-03 | 6.11 | 5.41 | [5 empty] | 1.7356 |  |  |  |  | 44 |  |  |  | 0 | 0.372 |  |  | 0.136 | 0.156 | [5 empty] | 35.5 |  |  |  |  | 71 |  | 24.8 |  | 9.9 | 0.074 |  | 2.7 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 31.86 | 7.5 | 12
2009-02-04 | 6.04 | 5.05 | [5 empty] | 1.7388 |  |  |  |  | 38 |  |  |  | 0 | 0.376 |  |  | 0.07 | 0.293 | [5 empty] | 36.3 |  |  |  |  | 72.7 |  | 25.4 |  | 7.6 | 0.051 |  | 2.7 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 35.18 | 7.8 | 11.2
2009-02-05 | 5.81 | 5.38 | [5 empty] | 1.7325 |  |  |  |  | 43 |  |  |  | 0 | 0.376 |  |  | 0.062 | 0.179 | [5 empty] | 35.5 |  |  |  |  | 71.1 |  | 22.4 |  | 8.2 | 0.064 |  | 3.1 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 30.51 | 7.8 | 10.2
2009-02-06 | 5.98 | 5.37 | [5 empty] | 1.745 |  |  |  |  | 46 |  |  |  | 0 | 0.399 |  |  | 0.06 | 0.186 | [5 empty] | 35.5 |  |  |  |  | 71.5 |  | 24.7 |  | 7.2 | 0.052 |  | 3.5 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 31.45 | 7.6 | 10.2
2009-02-07 | 6.04 | 5.42 | [5 empty] | 1.72 |  |  |  |  | 42 |  |  |  | 0 | 0.374 |  |  | 0.062 | 0.214 | [5 empty] | 34.5 |  |  |  |  | 69 |  | 25.8 |  | 7.4 | 0.049 |  | 3.4 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 35.02 | 6.8 | 10.2
2009-02-08 | 5.95 | 5.49 | [5 empty] | 1.77 |  |  |  |  | 40 |  |  |  | 0 | 0.354 |  |  | 0.089 | 0.227 | [5 empty] | 33.7 |  |  |  |  | 67.5 |  | 23.9 |  | 7.4 | 0.0505 |  | 3.45 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 35.46 | 6.8 | 10.2
2009-02-09 | 6.14 | 5.36 | [5 empty] | 1.71 |  |  |  |  | 42 |  |  |  | 0 | 0.3575 |  |  | 0.08 | 0.16 | [5 empty] | 29.8 |  |  |  |  | 59.65 |  | 22.75 |  | 7.5 | 0.04975 |  | 3.425 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 35.1 | 6.8 | 10.2
2009-02-10 | 6.33 | 5.23 | [5 empty] | 1.65 |  |  |  |  | 44 |  |  |  | 0 | 0.361 |  |  | 0.071 | 0.093 | [5 empty] | 25.9 |  |  |  |  | 51.8 |  | 21.6 |  | 7.6 | 0.074 |  | 3.1 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 34.74 | 6.8 | 10.2
2009-02-11 | 6.25 | 5.62 | [5 empty] | 1.65 |  |  |  |  | 46 |  |  |  | 0 | 0.359 |  |  | 0.062 | 0.139 | [5 empty] | 37.6 |  |  |  |  | 75.2 |  | 23.5 |  | 8.2 | 0.089 |  | 2.8 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 32.86 | 6.6 | 11.2
2009-02-12 | 6.14 | 5.56 | [5 empty] | 1.765 |  |  |  |  | 43 |  |  |  | 0 | 0.361 |  |  | 0.091 | 0.141 | [5 empty] | 35.2 |  |  |  |  | 70.4 |  | 23.5 |  | 7.9 | 0.08 |  | 2.8 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 33.38 | 6.4 | 10.8
2009-02-13 | 6.02 | 5.44 | [5 empty] | 1.88 |  |  |  |  | 43 |  |  |  | 0 | 0.361 |  |  | 0.096 | 0.192 | [5 empty] | 36.8 |  |  |  |  | 73.6 |  | 26.3 |  | 7.7 | 0.112 |  | 2.8 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 33.53 | 6.4 | 10.8
2009-02-14 | 5.84 | 5.07 | [5 empty] | 1.88 |  |  |  |  | 44 |  |  |  | 0 | 0.358 |  |  | 0.104 | 0.196 | [5 empty] | 36.4 |  |  |  |  | 72.8 |  | 25.9 |  | 7 | 0.106 |  | 2.8 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 36.93 | 6.6 | 10.8
2009-02-15 | 6.23 | 5.44 | [5 empty] | 1.88 |  |  |  |  | 44 |  |  |  | 0 | 0.356 |  |  | 0.087 | 0.214 | [5 empty] | 34.6 |  |  |  |  | 79.2 |  | 24.9 |  | 7.3 | 0.084 |  | 2.9 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 28.74 | 6.4 | 10.8
2009-02-16 | 5.97 | 5.275 | [5 empty] | 1.88 |  |  |  |  | 44.5 |  |  |  | 0 | 0.355 |  |  | 0.1 | 0.257 | [5 empty] | 34.35 |  |  |  |  | 73.7 |  | 24.15 |  | 7.2 | 0.079 |  | 2.85 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 31.92 | 6.45 | 10.9
2009-02-17 | 5.71 | 5.11 | [5 empty] | 1.88 |  |  |  |  | 45 |  |  |  | 0 | 0.354 |  |  | 0.113 | 0.3 | [5 empty] | 34.1 |  |  |  |  | 68.2 |  | 23.4 |  | 7.1 | 0.074 |  | 2.8 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 35.1 | 6.5 | 11
2009-02-18 | 5.89 | 5.4 | [5 empty] | 2.12 |  |  |  |  | 40 |  |  |  | 0 | 0.349 |  |  | 0.126 | 0.183 | [5 empty] | 37 |  |  |  |  | 74 |  | 25.6 |  | 6.9 | 0.062 |  | 2.9 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 35.07 | 6.3 | 11
2009-02-19 | 6.18 | 5.31 | [5 empty] | 2.15 |  |  |  |  | 42 |  |  |  | 0 | 0.342 |  |  | 0.114 | 0.154 | [5 empty] | 37.7 |  |  |  |  | 75.4 |  | 24.8 |  | 7 | 0.068 |  | 2.8 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 34.63 | 6.3 | 11
2009-02-20 | 6.22 | 5.64 | [5 empty] | 1.96 |  |  |  |  | 43 |  |  |  | 0 | 0.334 |  |  | 0.124 | 0.156 | [5 empty] | 35.1 |  |  |  |  | 71 |  | 24.8 |  | 7.1 | 0.091 |  | 3.2 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 22.61 | 6 | 11
2009-02-21 | 5.96 | 5.42 | [5 empty] | 2.46 |  |  |  |  | 40 |  |  |  | 0 | 0.348 |  |  | 0.076 | 0.148 | [5 empty] | 38.6 |  |  |  |  | 76.8 |  | 24.1 |  | 7.6 | 0.074 |  | 2.9 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 32.86 | 5.8 | 11
2009-02-22 | 6.23 | 5.55 | [5 empty] | 2.21 |  |  |  |  | 40 |  |  |  | 0 | 0.36 |  |  | 0.141 | 0.189 | [5 empty] | 36.8 |  |  |  |  | 73.7 |  | 26.3 |  | 9.7 | 0.017 |  | 2.9 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 33.33 | 5 | 11
2009-02-23 | 6.16 | 5.485 | [5 empty] | 2.335 |  |  |  |  | 44 |  |  |  | 0 | 0.362 |  |  | 0.112 | 0.227 | [5 empty] | 35.85 |  |  |  |  | 71.75 |  | 26.1 |  | 8.45 | 0.039 |  | 3 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 32.995 | 5 | 11
2009-02-24 | 6.09 | 5.42 | [5 empty] | 1.98 |  |  |  |  | 48 |  |  |  | 3 | 0.364 |  |  | 0.083 | 0.265 | [5 empty] | 34.9 |  |  |  |  | 69.8 |  | 25.9 |  | 7.2 | 0.061 |  | 3.1 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 32.66 | 5 | 11
2009-02-25 | 6.2 | 5.24 | [5 empty] | 1.94 |  |  |  |  | 44 |  |  |  | 0 | 0.37 |  |  | 0.116 | 0.22 | [5 empty] | 37.7 |  |  |  |  | 75.4 |  | 24.4 |  | 7.3 | 0.043 |  | 3.1 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 33.47 | 4.8 | 11.6
2009-02-26 | 6.01 | 5.41 | [5 empty] | 1.93 |  |  |  |  | 42 |  |  |  | 0 | 0.356 |  |  | 0.106 | 0.274 | [5 empty] | 35.8 |  |  |  |  | 71.6 |  | 23 |  | 9.9 | 0.039 |  | 3 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 32.39 | 4.3 | 12
2009-02-27 | 6.23 | 5.37 | [5 empty] | 1.96 |  |  |  |  | 43 |  |  |  | 0 | 0.306 |  |  | 0.088 | 0.203 | [5 empty] | 37 |  |  |  |  | 74 |  | 25.3 |  | 9.2 | 0.037 |  | 3 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 31.92 | 5 | 12.7
2009-02-28 | 6.11 | 5.37 | [5 empty] | 1.945 |  |  |  |  | 35 |  |  |  | 0 | 0.277 |  |  | 0.099 | 0.174 | [5 empty] | 37.3 |  |  |  |  | 74.6 |  | 25.2 |  | 8.6 | 0.049 |  | 3 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 33.16 | 5.3 | 12.7
2009-03-01 | 6.1 | 5.395 | [5 empty] | 1.9525 |  |  |  |  | 37.5 |  |  |  | 0 | 0.2635 |  |  | 0.097 | 0.1705 | [5 empty] | 36.25 |  |  |  |  | 72.5 |  | 26.3 |  | 8.75 | 0.0405 |  | 3 | 48.9089 | 0.12583 |  |  |  |  | 15.168 | 13.952 | [6 empty] | 32.77 | 5.3 | 12.7
2009-03-02 | 6.09 | 5.42 | [5 empty] | 1.9487 |  |  |  |  | 40 |  |  |  | 0 | 0.25 |  |  | 0.095 | 0.167 | [5 empty] | 35.2 |  |  |  |  | 70.4 |  | 27.4 |  | 8.9 | 0.032 |  | 3 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 32.38 | 5.3 | 12.7
2009-03-03 | 6.135 | 5.4 | [5 empty] | 1.9506 |  |  |  |  | 39.5 |  |  |  | 0 | 0.249 |  |  | 0.256 | 0.162 | [5 empty] | 36.7 |  |  |  |  | 73.4 |  | 26.1 |  | 9.95 | 0.0365 |  | 3.6 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 31.68 | 5.3 | 12.7
2009-03-04 | 6.18 | 5.38 | [5 empty] | 2.02 |  |  |  |  | 39 |  |  |  | 0 | 0.248 |  |  | 0.417 | 0.157 | [5 empty] | 38.2 |  |  |  |  | 76.4 |  | 24.8 |  | 11 | 0.041 |  | 4.2 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 30.98 | 5.3 | 12.7
2009-03-05 | 5.98 | 5.59 | [5 empty] | 1.81 |  |  |  |  | 40 |  |  |  | 0 | 0.25 |  |  | 0.06 | 0.153 | [5 empty] | 37.9 |  |  |  |  | 75.8 |  | 25.3 |  | 10.6 | 0.044 |  | 3.2 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 30.98 | 5.3 | 12.4
2009-03-06 | 6.24 | 5.64 | [5 empty] | 1.915 |  |  |  |  | 36 |  |  |  | 0 | 0.257 |  |  | 0.091 | 0.134 | [5 empty] | 36.1 |  |  |  |  | 72.2 |  | 23 |  | 9.4 | 0.051 |  | 3.5 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 31.19 | 5.3 | 12
2009-03-07 | 6.19 | 5.63 | [5 empty] | 1.94 |  |  |  |  | 32 |  |  |  | 0 | 0.274 |  |  | 0.09 | 0.147 | [5 empty] | 35.7 |  |  |  |  | 71.4 |  | 22.3 |  | 8.9 | 0.046 |  | 3.4 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 31.57 | 5.3 | 12
2009-03-08 | 5.73 | 5.66 | [5 empty] | 1.89 |  |  |  |  | 32 |  |  |  | 0 | 0.356 |  |  | 0.092 | 0.164 | [5 empty] | 35.1 |  |  |  |  | 70.2 |  | 23.7 |  | 8.1 | 0.049 |  | 3.3 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 30.91 | 5.3 | 12
2009-03-09 | 6.1 | 5.14 | [5 empty] | 1.915 |  |  |  |  | 35 |  |  |  | 0 | 0.336 |  |  | 0.099 | 0.234 | [5 empty] | 36.7 |  |  |  |  | 73.4 |  | 23.5 |  | 7.3 | 0.053 |  | 3.2 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 33.38 | 5.3 | 12.7
2009-03-10 | 5.84 | 5.135 | [5 empty] | 1.9025 |  |  |  |  | 38.5 |  |  |  | 0 | 0.301 |  |  | 0.096 | 0.2265 | [5 empty] | 37.35 |  |  |  |  | 74.7 |  | 23.6 |  | 7.4 | 0.055 |  | 3.2 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 33.86 | 5.35 | 12.8
2009-03-11 | 5.58 | 5.13 | [5 empty] | 1.9087 |  |  |  |  | 42 |  |  |  | 0 | 0.266 |  |  | 0.093 | 0.219 | [5 empty] | 38 |  |  |  |  | 76 |  | 23.7 |  | 7.5 | 0.057 |  | 3.2 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 34.34 | 5.4 | 12.9
2009-03-12 | 5.94 | 5.2 | [5 empty] | 1.91 |  |  |  |  | 40 |  |  |  | 0 | 0.254 |  |  | 0.107 | 0.176 | [5 empty] | 37.5 |  |  |  |  | 75 |  | 24 |  | 7 | 0.76 |  | 3.2 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 32.79 | 5.7 | 12.9
2009-03-13 | 6.05 | 5.26 | [5 empty] | 1.9094 |  |  |  |  | 42 |  |  |  | 0 | 0.256 |  |  | 0.113 | 0.198 | [5 empty] | 36.7 |  |  |  |  | 73.4 |  | 23.7 |  | 6.8 | 0.068 |  | 3.1 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 31.19 | 6 | 12.9
2009-03-14 | 5.965 | 5.315 | [5 empty] | 1.9097 |  |  |  |  | 40.5 |  |  |  | 0 | 0.261 |  |  | 0.092 | 0.1865 | [5 empty] | 36.35 |  |  |  |  | 72.7 |  | 23.9 |  | 7.2 | 0.0625 |  | 3 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 31.085 | 6 | 12.9
2009-03-15 | 5.88 | 5.37 | [5 empty] | 1.74 |  |  |  |  | 39 |  |  |  | 0 | 0.266 |  |  | 0.071 | 0.175 | [5 empty] | 36 |  |  |  |  | 72 |  | 24.1 |  | 7.6 | 0.057 |  | 2.9 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 30.98 | 6 | 12.9
2009-03-16 | 6.13 | 5.6 | [5 empty] | 1.99 |  |  |  |  | 39 |  |  |  | 0 | 0.273 |  |  | 0.072 | 0.137 | [5 empty] | 39.1 |  |  |  |  | 78.2 |  | 25.3 |  | 7.4 | 0.057 |  | 3 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 31.22 | 6 | 12.9
2009-03-17 | 6.085 | 5.615 | [5 empty] | 1.91 |  |  |  |  | 37.5 |  |  |  | 0 | 0.271 |  |  | 0.0825 | 0.1425 | [5 empty] | 38.9 |  |  |  |  | 77.8 |  | 25.1 |  | 7.5 | 0.0595 |  | 3.05 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 31.57 | 5.85 | 12.9
2009-03-18 | 6.04 | 5.63 | [5 empty] | 1.83 |  |  |  |  | 36 |  |  |  | 0 | 0.269 |  |  | 0.093 | 0.148 | [5 empty] | 38.7 |  |  |  |  | 77.4 |  | 24.9 |  | 7.6 | 0.062 |  | 3.1 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 31.92 | 5.7 | 12.9
2009-03-19 | 6.32 | 5.45 | [5 empty] | 1.94 |  |  |  |  | 37 |  |  |  | 0 | 0.28 |  |  | 0.104 | 0.194 | [5 empty] | 40.5 |  |  |  |  | 81 |  | 24.7 |  | 6.8 | 0.046 |  | 3.3 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 31.71 | 5.5 | 12.5
2009-03-20 | 5.96 | 5.45 | [5 empty] | 1.93 |  |  |  |  | 39 |  |  |  | 0 | 0.282 |  |  | 0.068 | 0.211 | [5 empty] | 40.5 |  |  |  |  | 81.1 |  | 25.5 |  | 7.8 | 0.057 |  | 5.2 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 30.98 | 5.5 | 12.7
2009-03-21 | 5.83 | 5.44 | [5 empty] | 1.55 |  |  |  |  | 37 |  |  |  | 0 | 0.43 |  |  | 0.082 | 0.239 | [5 empty] | 38.3 |  |  |  |  | 76.7 |  | 22.6 |  | 7.2 | 0.059 |  | 3.1 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 31.45 | 5.5 | 12.7
2009-03-22 | 5.9 | 5.45 | [5 empty] | 1.74 |  |  |  |  | 40 |  |  |  | 0 | 0.411 |  |  | 0.093 | 0.217 | [5 empty] | 37.6 |  |  |  |  | 75.2 |  | 24.4 |  | 6.9 | 0.064 |  | 3.2 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 30.51 | 5.7 | 12.7
2009-03-23 | 5.84 | 5.16 | [5 empty] | 1.645 |  |  |  |  | 43 |  |  |  | 0 | 0.417 |  |  | 0.13 | 0.137 | [5 empty] | 34.9 |  |  |  |  | 69.8 |  | 23.6 |  | 6.1 | 0.054 |  | 3.1 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 31.35 | 5.7 | 12.7
2009-03-24 | 5.94 | 5.305 | [5 empty] | 1.6925 |  |  |  |  | 43 |  |  |  | 0 | 0.404 |  |  | 0.1165 | 0.1765 | [5 empty] | 36.65 |  |  |  |  | 73.3 |  | 25 |  | 6.65 | 0.059 |  | 3.2 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 28.82 | 5.7 | 12.7
2009-03-25 | 6.04 | 5.45 | [5 empty] | 1.81 |  |  |  |  | 43 |  |  |  | 0 | 0.391 |  |  | 0.103 | 0.216 | [5 empty] | 38.4 |  |  |  |  | 76.8 |  | 26.4 |  | 7.2 | 0.064 |  | 3.3 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 26.29 | 5.7 | 12.7
2009-03-26 | 6.15 | 5.36 | [5 empty] | 1.92 |  |  |  |  | 41 |  |  |  | 0 | 0.38 |  |  | 0.09 | 0.157 | [5 empty] | 38.7 |  |  |  |  | 77.4 |  | 21.7 |  | 7.2 | 0.059 |  | 3 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 28.17 | 5.4 | 12.7
2009-03-27 | 6.17 | 5.53 | [5 empty] | 1.865 |  |  |  |  | 47 |  |  |  | 0 | 0.37 |  |  | 0.113 | 0.26 | [5 empty] | 36.8 |  |  |  |  | 73.6 |  | 22 |  | 5.9 | 0.054 |  | 3.1 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 30 | 5.4 | 12.4
2009-03-28 | 6.29 | 5.54 | [5 empty] | 1.84 |  |  |  |  | 49 |  |  |  | 0 | 0.377 |  |  | 0.126 | 0.274 | [5 empty] | 35.4 |  |  |  |  | 70.8 |  | 23.9 |  | 6.4 | 0.062 |  | 3.2 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 30.8 | 5.4 | 12.4
2009-03-29 | 5.92 | 5.63 | [5 empty] | 1.91 |  |  |  |  | 47 |  |  |  | 0 | 0.375 |  |  | 0.114 | 0.249 | [5 empty] | 34.2 |  |  |  |  | 68.4 |  | 23.5 |  | 6.8 | 0.084 |  | 3 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 29.37 | 5.4 | 12.4
2009-03-30 | 5.74 | 5.31 | [5 empty] | 1.875 |  |  |  |  | 48 |  |  |  | 0 | 0.356 |  |  | 0.104 | 0.283 | [5 empty] | 36.6 |  |  |  |  | 72.6 |  | 24.4 |  | 7.6 | 0.073 |  | 3.5 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 34.45 | 5.6 | 12.6
2009-03-31 | 5.955 | 5.205 | [5 empty] | 1.8925 |  |  |  |  | 45 |  |  |  | 0 | 0.3325 |  |  | 0.114 | 0.2835 | [5 empty] | 37.8 |  |  |  |  | 75.3 |  | 22.95 |  | 7.15 | 0.0635 |  | 3.25 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 33.765 | 5.75 | 12.7
2009-04-01 | 6.17 | 5.1 | [5 empty] | 1.8838 |  |  |  |  | 42 |  |  |  | 0 | 0.309 |  |  | 0.124 | 0.284 | [5 empty] | 39 |  |  |  |  | 78 |  | 21.5 |  | 6.7 | 0.054 |  | 3 | 48.9089 | 0.12583 |  |  |  |  | 14.977 | 13.804 | [6 empty] | 33.08 | 5.9 | 12.8
2009-04-02 | 5.97 | 5.45 | [5 empty] | 1.96 |  |  |  |  | 41 |  |  |  | 0 | 0.285 |  |  | 0.142 | 0.252 | [5 empty] | 35.5 |  |  |  |  | 71 |  | 22.3 |  | 7.4 | 0.074 |  | 3.1 | 48.9089 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 31.55 | 5.6 | 12.8
2009-04-03 | 5.68 | 5.29 | [5 empty] | 2.04 |  |  |  |  | 44 |  |  |  | 0 | 0.264 |  |  | 0.168 | 0.267 | [5 empty] | 37.8 |  |  |  |  | 75.6 |  | 23.6 |  | 7.1 | 0.069 |  | 3 | 48.9089 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 31.45 | 5.6 | 13.4
2009-04-04 | 6.22 | 5.35 | [5 empty] | 1.97 |  |  |  |  | 44 |  |  |  | 0 | 0.259 |  |  | 0.073 | 0.195 | [5 empty] | 38 |  |  |  |  | 76 |  | 23.7 |  | 7.1 | 0.068 |  | 3 | 48.9089 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 30.48 | 5.6 | 13.6
2009-04-05 | 5.95 | 5.5 | [5 empty] | 1.9 |  |  |  |  | 40 |  |  |  | 0 | 0.257 |  |  | 0.076 | 0.186 | [5 empty] | 39 |  |  |  |  | 78 |  | 22.1 |  | 11.4 | 0.163 |  | 3 | 48.9089 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 30.98 | 5.5 | 13.6
2009-04-06 | 6.14 | 5.32 | [5 empty] | 1.9 |  |  |  |  | 38 |  |  |  | 0 | 0.262 |  |  | 0.069 | 0.209 | [5 empty] | 39.1 |  |  |  |  | 78.2 |  | 22 |  | 10.8 | 0.133 |  | 3 | 48.9089 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 31.22 | 5.7 | 13.6
2009-04-07 | 6.025 | 5.375 | [5 empty] | 1.87 |  |  |  |  | 42.5 |  |  |  | 0 | 0.259 |  |  | 0.075 | 0.185 | [5 empty] | 38.5 |  |  |  |  | 77 |  | 22 |  | 9.6 | 0.1155 |  | 3 | 48.9089 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 31.54 | 5.7 | 13.6
2009-04-08 | 5.91 | 5.43 | [5 empty] | 1.84 |  |  |  |  | 47 |  |  |  | 0 | 0.256 |  |  | 0.081 | 0.161 | [5 empty] | 37.9 |  |  |  |  | 75.8 |  | 22 |  | 8.4 | 0.098 |  | 3 | 48.9089 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 31.86 | 5.7 | 13.6
2009-04-09 | 5.73 | 5.53 | [5 empty] | 1.73 |  |  |  |  | 44 |  |  |  | 2 | 0.991 |  |  | 0.117 | 0.22 | [5 empty] | 36.5 |  |  |  |  | 73 |  | 23.4 |  | 6.8 | 0.098 |  | 2.5 | 48.9088 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 29.53 | 5.7 | 13.2
2009-04-10 | 5.79 | 5.23 | [5 empty] | 1.71 |  |  |  |  | 45 |  |  |  | 0 | 1.532 |  |  | 0.105 | 0.21 | [5 empty] | 38.4 |  |  |  |  | 76.9 |  | 25.1 |  | 7.2 | 0.068 |  | 2.5 | 48.909 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 28.17 | 5.9 | 13.4
2009-04-11 | 6.07 | 5.4 | [5 empty] | 1.68 |  |  |  |  | 46 |  |  |  | 0 | 1.2615 |  |  | 0.123 | 0.181 | [5 empty] | 39.1 |  |  |  |  | 78.2 |  | 23.8 |  | 6.9 | 0.051 |  | 2.6 | 48.9087 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 28.64 | 5.4 | 13.4
2009-04-12 | 5.99 | 5.61 | [5 empty] | 1.63 |  |  |  |  | 49 |  |  |  | 0 | 0.75025 |  |  | 0.136 | 0.21 | [5 empty] | 38.6 |  |  |  |  | 77.2 |  | 24.3 |  | 7 | 0.062 |  | 2.7 | 48.9092 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 28.63 | 5.4 | 13.4
2009-04-13 | 6.01 | 5.46 | [5 empty] | 1.58 |  |  |  |  | 41 |  |  |  | 0 | 0.239 |  |  | 0.124 | 0.218 | [5 empty] | 39.7 |  |  |  |  | 79.4 |  | 22.9 |  | 7.4 | 0.047 |  | 2.7 | 48.9082 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 31.15 | 5.4 | 13.4
2009-04-14 | 6.075 | 5.505 | [5 empty] | 1.58 |  |  |  |  | 44.5 |  |  |  | 0 | 0.31212 |  |  | 0.1305 | 0.2545 | [5 empty] | 38.55 |  |  |  |  | 77.05 |  | 23.35 |  | 7.3 | 0.049 |  | 2.8 | 48.9103 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 30.595 | 5.3 | 13.5
2009-04-15 | 6.14 | 5.55 | [5 empty] | 1.58 |  |  |  |  | 48 |  |  |  | 0 | 0.38525 |  |  | 0.137 | 0.291 | [5 empty] | 37.4 |  |  |  |  | 74.7 |  | 23.8 |  | 7.2 | 0.051 |  | 2.9 | 48.9061 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 30.04 | 5.2 | 13.6
2009-04-16 | 5.85 | 5.36 | [5 empty] | 1.58 |  |  |  |  | 50 |  |  |  | 0 | 0.3925 |  |  | 0.162 | 0.246 | [5 empty] | 39.2 |  |  |  |  | 78.4 |  | 24.9 |  | 11.6 | 0.08 |  | 3.1 | 48.9146 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 31.22 | 5.2 | 13.8
2009-04-17 | 6.02 | 5.51 | [5 empty] | 1.735 |  |  |  |  | 41 |  |  |  | 0 | 0.378 |  |  | 0.131 | 0.228 | [5 empty] | 37.1 |  |  |  |  | 74.2 |  | 24.3 |  | 10.7 | 0.047 |  | 2.8 | 48.8976 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 32.4 | 5.5 | 14
2009-04-18 | 6.01 | 5.05 | [5 empty] | 1.68 |  |  |  |  | 43 |  |  |  | 0 | 0.407 |  |  | 0.132 | 0.18 | [5 empty] | 37.9 |  |  |  |  | 75.8 |  | 21.9 |  | 9.8 | 0.069 |  | 2.9 | 48.9316 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 32.85 | 5.7 | 14
2009-04-19 | 5.5 | 4.94 | [5 empty] | 1.79 |  |  |  |  | 48 |  |  |  | 0 | 0.4185 |  |  | 0.07 | 0.202 | [5 empty] | 35.7 |  |  |  |  | 71.4 |  | 22.5 |  | 9.1 | 0.071 |  | 2.5 | 48.8635 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 31.49 | 5.9 | 14
2009-04-20 | 6.03 | 5.36 | [5 empty] | 1.8912 |  |  |  |  | 48 |  |  |  | 0 | 0.43 |  |  | 0.083 | 0.132 | [5 empty] | 34.4 |  |  |  |  | 68.8 |  | 21.8 |  | 9.9 | 0.06 |  | 2.9 | 48.9996 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 33.86 | 6.1 | 14
2009-04-21 | 6.01 | 5.325 | [5 empty] | 1.9275 |  |  |  |  | 47.5 |  |  |  | 0 | 0.5685 |  |  | 0.095 | 0.1195 | [5 empty] | 33.55 |  |  |  |  | 67.1 |  | 21.45 |  | 9.25 | 0.0585 |  | 2.95 | 48.7275 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 33.485 | 6.2 | 13.5
2009-04-22 | 5.99 | 5.29 | [5 empty] | 1.855 |  |  |  |  | 47 |  |  |  | 0 | 0.707 |  |  | 0.107 | 0.107 | [5 empty] | 32.7 |  |  |  |  | 65.4 |  | 21.1 |  | 8.6 | 0.057 |  | 3 | 49.2717 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 33.11 | 6.3 | 13
2009-04-23 | 5.67 | 5.24 | [5 empty] | 2 |  |  |  |  | 51 |  |  |  | 0 | 0.421 |  |  | 0.072 | 0.178 | [5 empty] | 29.6 |  |  |  |  | 59.2 |  | 25 |  | 9 | 0.049 |  | 3 | 48.1833 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 31.26 | 6.3 | 13
2009-04-24 | 5.96 | 5.49 | [5 empty] | 1.71 |  |  |  |  | 54 |  |  |  | 2 | 0.407 |  |  | 0.067 | 0.115 | [5 empty] | 34 |  |  |  |  | 68 |  | 24.3 |  | 9.6 | 0.051 |  | 2.9 | 50.36 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 30.91 | 6 | 11.8
2009-04-25 | 5.82 | 5.08 | [5 empty] | 1.98 |  |  |  |  | 55 |  |  |  | 3 | 0.455 |  |  | 0.072 | 0.156 | [5 empty] | 31.6 |  |  |  |  | 63.2 |  | 24.2 |  | 7.4 | 0.071 |  | 2.9 | 46.0067 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 30.24 | 6.2 | 9.6
2009-04-26 | 5.99 | 5.58 | [5 empty] | 2.25 |  |  |  |  | 45 |  |  |  | 0 | 0.44 |  |  | 0.072 | 0.166 | [5 empty] | 31.2 |  |  |  |  | 62.5 |  | 24.6 |  | 7 | 0.075 |  | 3.3 | 46.0067 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 28.17 | 6.2 | 9.6
2009-04-27 | 5.81 | 5.18 | [5 empty] | 1.93 |  |  |  |  | 44 |  |  |  | 0 | 0.434 |  |  | 0.085 | 0.218 | [5 empty] | 31.7 |  |  |  |  | 63.5 |  | 26.5 |  | 8 | 0.082 |  | 3 | 46.0067 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 30.04 | 6.2 | 9.6
2009-04-28 | 5.87 | 5.26 | [5 empty] | 1.92 |  |  |  |  | 45.5 |  |  |  | 0 | 0.426 |  |  | 0.078 | 0.1635 | [5 empty] | 31.4 |  |  |  |  | 62.85 |  | 26.15 |  | 8.2 | 0.073 |  | 2.95 | 46.0067 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 30.715 | 6.2 | 9.6
2009-04-29 | 5.93 | 5.34 | [5 empty] | 1.91 |  |  |  |  | 47 |  |  |  | 1 | 0.418 |  |  | 0.071 | 0.109 | [5 empty] | 31.1 |  |  |  |  | 62.2 |  | 25.8 |  | 8.4 | 0.064 |  | 2.9 | 46.0067 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 31.39 | 6.2 | 9.6
2009-04-30 | 5.92 | 5.26 | [5 empty] | 1.88 |  |  |  |  | 56 |  |  |  | 0 | 0.402 |  |  | 0.077 | 0.189 | [5 empty] | 31.2 |  |  |  |  | 62.4 |  | 24.9 |  | 7.7 | 0.084 |  | 3.1 | 46.0067 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 31.73 | 6.2 | 9.5
2009-05-01 | 5.95 | 5.33 | [5 empty] | 1.96 |  |  |  |  | 43 |  |  |  | 0 | 0.404 |  |  | 0.087 | 0.137 | [5 empty] | 30.5 |  |  |  |  | 61.1 |  | 23.8 |  | 7.6 | 0.142 |  | 3.3 | 46.0067 | 0.12583 |  |  |  |  | 14.146 | 12.984 | [6 empty] | 29.11 | 6.2 | 9.5
2009-05-02 | 5.88 | 5.46 | [5 empty] | 2.07 |  |  |  |  | 42 |  |  |  | 0 | 0.403 |  |  | 0.115 | 0.189 | [5 empty] | 31.2 |  |  |  |  | 62.6 |  | 25.4 |  | 7.4 | 0.113 |  | 3.3 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 29.11 | 6.2 | 9.5
2009-05-03 | 5.93 | 5.37 | [5 empty] | 2.015 |  |  |  |  | 40 |  |  |  | 0 | 0.401 |  |  | 0.102 | 0.196 | [5 empty] | 30.9 |  |  |  |  | 61.8 |  | 24.8 |  | 6.8 | 0.1 |  | 3.4 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 29.46 | 6.2 | 9.5
2009-05-04 | 6.01 | 5.31 | [5 empty] | 2.0425 |  |  |  |  | 39 |  |  |  | 0 | 0.377 |  |  | 0.104 | 0.199 | [5 empty] | 32.7 |  |  |  |  | 65.4 |  | 25.1 |  | 6.2 | 0.091 |  | 3.5 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 29.44 | 6.2 | 9.5
2009-05-05 | 6.085 | 5.285 | [5 empty] | 2.0287 |  |  |  |  | 39.5 |  |  |  | 0 | 0.3805 |  |  | 0.0975 | 0.225 | [5 empty] | 31.7 |  |  |  |  | 63.4 |  | 24.3 |  | 5.65 | 0.0815 |  | 3.75 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 30.21 | 6.2 | 9.5
2009-05-06 | 6.16 | 5.26 | [5 empty] | 1.75 |  |  |  |  | 40 |  |  |  | 0 | 0.384 |  |  | 0.091 | 0.251 | [5 empty] | 30.7 |  |  |  |  | 61.4 |  | 23.5 |  | 5.1 | 0.072 |  | 4 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 30.98 | 6.2 | 9.5
2009-05-07 | 6.11 | 5.38 | [5 empty] | 1.95 |  |  |  |  | 43 |  |  |  | 0 | 0.37 |  |  | 0.074 | 0.098 | [5 empty] | 30.3 |  |  |  |  | 60.7 |  | 22.5 |  | 5.5 | 0.009 |  | 4.1 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 30.04 | 6.2 | 9.1
2009-05-08 | 6.04 | 5.39 | [5 empty] | 1.85 |  |  |  |  | 46 |  |  |  | 0 | 0.367 |  |  | 0.081 | 0.134 | [5 empty] | 30.05 |  |  |  |  | 61 |  | 23.2 |  | 5.9 | 0.072 |  | 4.1 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 30.56 | 6.2 | 9.1
2009-05-09 | 6.1 | 5.42 | [5 empty] | 1.9 |  |  |  |  | 39 |  |  |  | 0 | 0.371 |  |  | 0.091 | 0.094 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 20.9 |  | 5.7 | 0.053 |  | 3.7 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 29.69 | 6.2 | 9.1
2009-05-10 | 6.1 | 5.3 | [5 empty] | 1.875 |  |  |  |  | 48 |  |  |  | 1 | 0.376 |  |  | 0.062 | 0.11 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 21.6 |  | 6.4 | 0.061 |  | 3 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 31.45 | 6.2 | 9.1
2009-05-11 | 5.76 | 5.31 | [5 empty] | 1.8875 |  |  |  |  | 49 |  |  |  | 0 | 0.365 |  |  | 0.074 | 0.088 | [5 empty] | 28.9 |  |  |  |  | 57.8 |  | 22.4 |  | 6.1 | 0.059 |  | 3.9 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 32.61 | 6.2 | 9.1
2009-05-12 | 5.885 | 5.38 | [5 empty] | 1.8813 |  |  |  |  | 48 |  |  |  | 0 | 0.3845 |  |  | 0.0835 | 0.086 | [5 empty] | 30.75 |  |  |  |  | 61.5 |  | 23.55 |  | 5.95 | 0.054 |  | 3.75 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 30.995 | 6.4 | 9.05
2009-05-13 | 6.01 | 5.45 | [5 empty] | 1.8844 |  |  |  |  | 47 |  |  |  | 0 | 0.404 |  |  | 0.093 | 0.084 | [5 empty] | 32.6 |  |  |  |  | 65.2 |  | 24.7 |  | 5.8 | 0.049 |  | 3.6 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 29.38 | 6.6 | 9
2009-05-14 | 5.88 | 5.45 | [5 empty] | 2.25 |  |  |  |  | 41 |  |  |  | 0 | 0.418 |  |  | 0.08 | 0.087 | [5 empty] | 29.7 |  |  |  |  | 59.4 |  | 22.9 |  | 7.2 | 0.047 |  | 3.8 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 32.656 | 6.6 | 8.8
2009-05-15 | 6.15 | 5.04 | [5 empty] | 2.31 |  |  |  |  | 43 |  |  |  | 0 | 0.398 |  |  | 0.393 | 0.115 | [5 empty] | 36.2 |  |  |  |  | 73.4 |  | 22 |  | 6.9 | 0.051 |  | 12.9 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 30.51 | 6.6 | 8.8
2009-05-16 | 6.43 | 5.08 | [5 empty] | 2.34 |  |  |  |  | 41 |  |  |  | 0 | 0.4 |  |  | 0.08 | 0.177 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 22.4 |  | 8.7 | 0.051 |  | 5.6 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 28.64 | 6.6 | 8.8
2009-05-17 | 6.35 | 4.95 | [5 empty] | 2.17 |  |  |  |  | 42 |  |  |  | 0 | 0.388 |  |  | 0.084 | 0.158 | [5 empty] | 28.6 |  |  |  |  | 57.4 |  | 23.7 |  | 6.9 | 0.044 |  | 6.5 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 31.92 | 6.6 | 8
2009-05-18 | 6.14 | 5.05 | [5 empty] | 2.19 |  |  |  |  | 42 |  |  |  | 0 | 0.389 |  |  | 0.068 | 0.126 | [5 empty] | 29.5 |  |  |  |  | 59 |  | 24.9 |  | 7 | 0.055 |  | 7.5 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 31.92 | 6.6 | 8
2009-05-19 | 6.14 | 5.01 | [5 empty] | 2.09 |  |  |  |  | 44 |  |  |  | 0 | 0.3925 |  |  | 0.082 | 0.141 | [5 empty] | 30.65 |  |  |  |  | 61.3 |  | 24.9 |  | 6.9 | 0.059 |  | 10.45 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 34.69 | 6.7 | 8
2009-05-20 | 6.14 | 4.97 | [5 empty] | 1.99 |  |  |  |  | 46 |  |  |  | 0 | 0.396 |  |  | 0.096 | 0.156 | [5 empty] | 31.8 |  |  |  |  | 63.6 |  | 24.9 |  | 6.8 | 0.063 |  | 13.4 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 37.46 | 6.8 | 8
2009-05-21 | 6.26 | 4.87 | [5 empty] | 2.41 |  |  |  |  | 22 |  |  |  | 0 | 0.404 |  |  | 0.058 | 0.209 | [5 empty] | 29.4 |  |  |  |  | 58.8 |  | 23.9 |  | 8.2 | 0.071 |  | 10.3 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 36.075 | 7 | 8.1
2009-05-22 | 6.28 | 5.14 | [5 empty] | 1.94 |  |  |  |  | 35 |  |  |  | 0 | 0.401 |  |  | 0.145 | 0.106 | [5 empty] | 28 |  |  |  |  | 56 |  | 22.6 |  | 7.4 | 0.062 |  | 9.9 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 33.8 | 6.8 | 7.8
2009-05-23 | 6.41 | 5.07 | [5 empty] | 2.175 |  |  |  |  | 33 |  |  |  | 0 | 0.392 |  |  | 0.074 | 0.092 | [5 empty] | 28.3 |  |  |  |  | 56.5 |  | 23.5 |  | 5.7 | 0.088 |  | 10.5 | 46.0066 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 33.33 | 6.8 | 7.6
2009-05-24 | 6.3 | 5.39 | [5 empty] | 2.0575 |  |  |  |  | 31 |  |  |  | 0 | 0.425 |  |  | 0.081 | 0.098 | [5 empty] | 28.5 |  |  |  |  | 57 |  | 24.4 |  | 5.9 | 0.074 |  | 10.1 | 46.0067 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 32.67 | 7 | 6.6
2009-05-25 | 6.19 | 5.49 | [5 empty] | 2.1162 |  |  |  |  | 32 |  |  |  | 0 | 0.427 |  |  | 0.093 | 0.123 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 22 |  | 5.4 | 0.081 |  | 10.3 | 46.0065 | 0.12583 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 33 | 6.9 | 7.1
2009-05-26 | 6.21 | 5.51 | [5 empty] | 2.0869 |  |  |  |  | 33.5 |  |  |  | 0 | 0.4235 |  |  | 0.0795 | 0.1315 | [5 empty] | 29 |  |  |  |  | 57.95 |  | 22.55 |  | 5.45 | 0.0775 |  | 10.2 | 46.0069 | 0.12584 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 32.835 | 6.95 | 6.85
2009-05-27 | 6.23 | 5.53 | [5 empty] | 2.1016 |  |  |  |  | 35 |  |  |  | 0 | 0.42 |  |  | 0.066 | 0.14 | [5 empty] | 27.6 |  |  |  |  | 55.1 |  | 23.1 |  | 5.5 | 0.143 |  | 8.6 | 46.0062 | 0.12582 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 30.51 | 6.6 | 7
2009-05-28 | 6.29 | 6.29 | [5 empty] | 2.0942 |  |  |  |  | 34 |  |  |  | 0 | 0.402 |  |  | 0.062 | 0.108 | [5 empty] | 28.1 |  |  |  |  | 56 |  | 24.4 |  | 5.4 | 0.091 |  | 9.9 | 46.0077 | 0.12585 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 31.45 | 7 | 6
2009-05-29 | 5.99 | 5.48 | [5 empty] | 2.0979 |  |  |  |  | 11 |  |  |  | 0 | 0.427 |  |  | 0.056 | 0.117 | [5 empty] | 26.8 |  |  |  |  | 53.5 |  | 24.8 |  | 5.9 | 0.066 |  | 7.6 | 46.0047 | 0.1258 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 28.51 | 6.8 | 5.8
2009-05-30 | 6.09 | 5.01 | [5 empty] | 2.0961 |  |  |  |  | 20 |  |  |  | 0 | 0.421 |  |  | 0.069 | 0.124 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 23.6 |  | 6.1 | 0.052 |  | 7.8 | 46.0106 | 0.1259 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 29.59 | 6.8 | 5.8
2009-05-31 | 6.2 | 4.92 | [5 empty] | 1.73 |  |  |  |  | 21 |  |  |  | 0 | 0.366 |  |  | 0.064 | 0.119 | [5 empty] | 26.7 |  |  |  |  | 53.4 |  | 24.5 |  | 6.3 | 0.059 |  | 8.1 | 45.9988 | 0.12569 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 32.06 | 7.7 | 5.8
2009-06-01 | 5.85 | 5.27 | [5 empty] | 1.913 |  |  |  |  | 36 |  |  |  | 0 | 0.458 |  |  | 0.072 | 0.126 | [5 empty] | 28.9 |  |  |  |  | 57.8 |  | 24.1 |  | 6.8 | 0.054 |  | 8.9 | 46.0224 | 0.12611 |  |  |  |  | 14.735 | 13.242 | [6 empty] | 34.96 | 7.2 | 5.8
2009-06-02 | 5.945 | 5.21 | [5 empty] | 1.8215 |  |  |  |  | 30 |  |  |  | 0 | 0.446 |  |  | 0.0805 | 0.118 | [5 empty] | 28.65 |  |  |  |  | 57.3 |  | 23.9 |  | 6.2 | 0.0575 |  | 8.95 | 45.9752 | 0.12527 |  |  |  |  | 13.994 | 12.93 | [6 empty] | 33.51 | 7.45 | 5.8
2009-06-03 | 6.04 | 5.15 | [5 empty] | 1.8673 |  |  |  |  | 24 |  |  |  | 0 | 0.434 |  |  | 0.089 | 0.11 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 23.7 |  | 5.6 | 0.061 |  | 9 | 46.0697 | 0.12695 |  |  |  |  | 13.994 | 12.93 | [6 empty] | 30.6 | 7.2 | 5.6
2009-06-04 | 5.97 | 5.22 | [5 empty] | 1.78 |  |  |  |  | 20 |  |  |  | 0 | 0.459 |  |  | 0.062 | 0.182 | [5 empty] | 27.7 |  |  |  |  | 55.4 |  | 23.6 |  | 5.9 | 0.047 |  | 11.5 | 45.8806 | 0.12359 |  |  |  |  | 13.994 | 12.93 | [6 empty] | 30.8 | 7.2 | 5.4
2009-06-05 | 6.04 | 5.17 | [5 empty] | 2 |  |  |  |  | 31 |  |  |  | 0 | 0.429 |  |  | 0.077 | 0.154 | [5 empty] | 16.8 |  |  |  |  | 33.6 |  | 24.4 |  | 6 | 0.058 |  | 11.8 | 46.2587 | 0.13031 |  |  |  |  | 13.994 | 12.93 | [6 empty] | 30.7 | 7.2 | 5.5
2009-06-06 | 6.04 | 5.17 | [5 empty] | 2 |  |  |  |  | 31 |  |  |  | 0 | 0.429 |  |  | 0.077 | 0.154 | [5 empty] | 19.4 |  |  |  |  | 38.75 |  | 24.05 |  | 3.85 | 0.118 |  | 12.5 | 45.5025 | 0.11687 |  |  |  |  | 13.994 | 12.93 | [6 empty] | 30.75 | 7.2 | 5.45
2009-06-07 | 6.28 | 5.32 | [5 empty] | 1.85 |  |  |  |  | 30 |  |  |  | 0 | 0.423 |  |  | 0.064 | 0.044 | [5 empty] | 22 |  |  |  |  | 43.9 |  | 23.7 |  | 1.7 | 0.178 |  | 13.2 | 47.015 | 0.14375 |  |  |  |  | 13.75 | 13.92 | [6 empty] | 30.98 | 7.2 | 5.4
2009-06-08 | 6.61 | 5.11 | [5 empty] | 1.59 |  |  |  |  | 34 |  |  |  | 0 | 0.407 |  |  | 0.054 | 0.5 | [5 empty] | 25 |  |  |  |  | 50 |  | 23.6 |  | 5.7 | 0.121 |  | 13.3 | 43.99 | 0.09 |  |  |  |  | 12.74 | 11.86 | [6 empty] | 30.51 | 7.2 | 6
2009-06-09 | 6.43 | 5.25 | [5 empty] | 1.645 |  |  |  |  | 35 |  |  |  | 0.5 | 0.409 |  |  | 0.0615 | 0.2845 | [5 empty] | 23.5 |  |  |  |  | 46.95 |  | 23.65 |  | 3.7 | 0.1495 |  | 13.25 | 50.04 | 0.1975 |  |  |  |  | 13.7365 | 12.3635 | [6 empty] | 30.745 | 7.2 | 5.7
2009-06-10 | 6.25 | 5.39 | [5 empty] | 1.7 |  |  |  |  | 36 |  |  |  | 1 | 0.411 |  |  | 0.069 | 0.069 | [5 empty] | 24.25 |  |  |  |  | 48.475 |  | 23.625 |  | 4.7 | 0.13525 |  | 13.275 | 50.03 | 0.165 |  |  |  |  | 14.733 | 12.867 | [6 empty] | 30.6275 | 7.2 | 5.85
2009-06-11 | 6.35 | 5.47 | [5 empty] | 1.84 |  |  |  |  | 33 |  |  |  | 0 | 0.398 |  |  | 0.059 | 0.091 | [5 empty] | 25.9 |  |  |  |  | 51.8 |  | 24.9 |  | 6 | 0.073 |  | 11.4 | 50.05 | 0.23 |  |  |  |  | 12.971 | 10.981 | [6 empty] | 33.81 | 6.8 | 6.2
2009-06-12 | 7.09 | 5.15 | [5 empty] | 1.79 |  |  |  |  | 32 |  |  |  | 0 | 0.407 |  |  | 0.059 | 0.131 | [5 empty] | 25.1 |  |  |  |  | 50.2 |  | 23.8 |  | 6.7 | 0.052 |  | 11.6 | 50.01 | 0.1 |  |  |  |  | 12.921 | 11.992 | [6 empty] | 33.81 | 6.6 | 6.2
2009-06-13 | 6.03 | 5.16 | [5 empty] | 1.62 |  |  |  |  | 32 |  |  |  | 0 | 0.404 |  |  | 0.061 | 0.119 | [5 empty] | 25.5 |  |  |  |  | 51 |  | 24.1 |  | 6.1 | 0.063 |  | 11 | 34.82 | 0.165 |  |  |  |  | 13.614 | 12.67 | [6 empty] | 33.81 | 6.6 | 6.7
2009-06-14 | 6.39 | 5.26 | [5 empty] | 1.81 |  |  |  |  | 38 |  |  |  | 0 | 0.393 |  |  | 0.066 | 0.099 | [5 empty] | 25.3 |  |  |  |  | 50.6 |  | 24.5 |  | 5.6 | 0.096 |  | 11.4 | 65.14 | 0.61 |  |  |  |  | 13.187 | 12.211 | [6 empty] | 30.29 | 6.7 | 6.8
2009-06-15 | 6.17 | 5.24 | [5 empty] | 1.8 |  |  |  |  | 37 |  |  |  | 0 | 0.369 |  |  | 0.056 | 0.112 | [5 empty] | 26.4 |  |  |  |  | 52.8 |  | 22.5 |  | 5.7 | 0.08 |  | 11.5 | 53.56 | 0.19 |  |  |  |  | 13.187 | 12.211 | [6 empty] | 30.29 | 6.7 | 6.8
2009-06-16 | 6.095 | 5.245 | [5 empty] | 1.0705 |  |  |  |  | 35.5 |  |  |  | 0 | 0.355 |  |  | 0.058 | 0.0965 | [5 empty] | 25.75 |  |  |  |  | 51.45 |  | 23.05 |  | 5.95 | 0.077 |  | 12.7 | 59.35 | 0.4 |  |  |  |  | 13.5985 | 12.3495 | [6 empty] | 28.29 | 6.7 | 6.8
2009-06-17 | 6.02 | 5.25 | [5 empty] | 0.341 |  |  |  |  | 34 |  |  |  | 0 | 0.341 |  |  | 0.06 | 0.081 | [5 empty] | 25.1 |  |  |  |  | 50.1 |  | 23.6 |  | 6.2 | 0.074 |  | 13.9 | 56.455 | 0.295 |  |  |  |  | 14.01 | 12.488 | [6 empty] | 26.29 | 6.7 | 6.8
2009-06-18 | 6.3 | 5.06 | [5 empty] | 1.92 |  |  |  |  | 32 |  |  |  | 0 | 0.356 |  |  | 0.089 | 0.063 | [5 empty] | 25.8 |  |  |  |  | 51.6 |  | 22.1 |  | 6.6 | 0.063 |  | 13.7 | 60.73 | 0.11 |  |  |  |  | 14.046 | 13.58 | [6 empty] | 28.87 | 6.7 | 6.8
2009-06-19 | 6.31 | 5.01 | [5 empty] | 1.84 |  |  |  |  | 31 |  |  |  | 0 | 0.351 |  |  | 0.074 | 0.076 | [5 empty] | 27.2 |  |  |  |  | 54.4 |  | 22.8 |  | 6.2 | 0.054 |  | 13.5 | 65.75 | 0.39 |  |  |  |  | 13.872 | 13.409 | [6 empty] | 29.41 | 6.7 | 6.8
2009-06-20 | 6.24 | 5 | [5 empty] | 1.89 |  |  |  |  | 28 |  |  |  | 0 | 0.387 |  |  | 0.079 | 0.077 | [5 empty] | 27.2 |  |  |  |  | 54.4 |  | 22.1 |  | 6.4 | 0.067 |  | 14.5 | 66.64 | 0.54 |  |  |  |  | 13.382 | 12.447 | [6 empty] | 29.45 | 6.7 | 6.8
2009-06-21 | 5.87 | 5.05 | [5 empty] | 2.41 |  |  |  |  | 30 |  |  |  | 0 | 0.357 |  |  | 0.078 | 0.061 | [5 empty] | 25.8 |  |  |  |  | 51.6 |  | 22.9 |  | 6.7 | 0.071 |  | 13.3 | 82.05 | 0.7 |  |  |  |  | 12.919 | 11.964 | [6 empty] | 27.14 | 6.7 | 6.8
2009-06-22 | 6.24 | 5.08 | [5 empty] | 2.55 |  |  |  |  | 36 |  |  |  | 0 | 0.381 |  |  | 0.059 | 0.072 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 23.7 |  | 6.1 | 0.053 |  | 13.5 | 102.18 | 1.49 |  |  |  |  | 12.748 | 11.482 | [6 empty] | 32.06 | 6.7 | 6.8
2009-06-23 | 6.22 | 5.085 | [5 empty] | 2.3 |  |  |  |  | 33 |  |  |  | 0 | 0.3625 |  |  | 0.063 | 0.0775 | [5 empty] | 27 |  |  |  |  | 54 |  | 23.45 |  | 5.9 | 0.051 |  | 13.45 | 72.52 | 0.59 |  |  |  |  | 12.699 | 11.395 | [6 empty] | 31.725 | 6.7 | 6.9
2009-06-24 | 6.2 | 5.09 | [5 empty] | 2.47 |  |  |  |  | 30 |  |  |  | 0 | 0.344 |  |  | 0.067 | 0.083 | [5 empty] | 27.2 |  |  |  |  | 54.4 |  | 23.2 |  | 5.7 | 0.049 |  | 13.4 | 90.3 | 0.64 |  |  |  |  | 14.054 | 13.174 | [6 empty] | 31.39 | 6.7 | 7
2009-06-25 | 6.31 | 5.07 | [5 empty] | 2.36 |  |  |  |  | 29 |  |  |  | 0 | 0.337 |  |  | 0.076 | 0.073 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 23.7 |  | 6.5 | 0.072 |  | 13.5 | 73.49 | 0.01 |  |  |  |  | 14.974 | 14.085 | [6 empty] | 29.86 | 6.7 | 7
2009-06-26 | 6.38 | 4.97 | [5 empty] | 2.15 |  |  |  |  | 33 |  |  |  | 0 | 0.731 |  |  | 0.071 | 0.077 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 23.9 |  | 6 | 0.053 |  | 15.3 | 79.12 | 0.23 |  |  |  |  | 15.04 | 15.114 | [6 empty] | 27.57 | 6.8 | 7
2009-06-27 | 5.89 | 5.3 | [5 empty] | 2.16 |  |  |  |  | 36 |  |  |  | 0 | 0.401 |  |  | 0.057 | 0.109 | [5 empty] | 27.3 |  |  |  |  | 54.6 |  | 23.3 |  | 5.8 | 0.063 |  | 14 | 90.41 | 1.04 |  |  |  |  | 13.68 | 12.82 | [6 empty] | 34.35 | 6.8 | 7
2009-06-28 | 6.29 | 5.01 | [5 empty] | 2.38 |  |  |  |  | 34 |  |  |  | 0 | 0.375 |  |  | 0.059 | 0.089 | [5 empty] | 27.6 |  |  |  |  | 55.1 |  | 22.7 |  | 6.2 | 0.057 |  | 14.2 | 83.8 | 0.43 |  |  |  |  | 13.52 | 13.56 | [6 empty] | 30.98 | 6.8 | 7.2
2009-06-29 | 6.16 | 5.04 | [5 empty] | 2.56 |  |  |  |  | 32 |  |  |  | 0 | 0.418 |  |  | 0.061 | 0.081 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 21.8 |  | 6.1 | 0.06 |  | 14.3 | 99.36 | 0.66 |  |  |  |  | 14.96 | 14.03 | [6 empty] | 30.51 | 6.8 | 7.2
2009-06-30 | 6.1 | 5.05 | [5 empty] | 2.77 |  |  |  |  | 34 |  |  |  | 0 | 0.372 |  |  | 0.065 | 0.077 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 22.15 |  | 6 | 0.0585 |  | 15.9 | 109.405 | 0.55 |  |  |  |  | 16.2445 | 14.941 | [6 empty] | 31.14 | 6.8 | 7.2
2009-07-01 | 6.04 | 5.06 | [5 empty] | 2.98 |  |  |  |  | 36 |  |  |  | 0 | 0.326 |  |  | 0.069 | 0.073 | [5 empty] | 28.7 |  |  |  |  | 57.4 |  | 22.5 |  | 5.9 | 0.057 |  | 17.5 | 119.45 | 0.44 |  |  |  |  | 17.529 | 15.852 | [6 empty] | 31.77 | 6.8 | 7.2
2009-07-02 | 6.12 | 5.04 | [5 empty] | 2.63 |  |  |  |  | 32 |  |  |  | 0 | 0.329 |  |  | 0.057 | 0.082 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 24.5 |  | 6.4 | 0.051 |  | 17.6 | 101.85 | 0.28 |  |  |  |  | 15.79 | 15.88 | [6 empty] | 30.88 | 6.8 | 7.2
2009-07-03 | 6.14 | 4.92 | [5 empty] | 2.68 |  |  |  |  | 31 |  |  |  | 0 | 0.345 |  |  | 0.064 | 0.081 | [5 empty] | 28.1 |  |  |  |  | 56.1 |  | 21.9 |  | 6.6 | 0.061 |  | 17.8 | 104.83 | 0.37 |  |  |  |  | 16.366 | 15.611 | [6 empty] | 33.33 | 6.9 | 7.2
2009-07-04 | 6.15 | 5.24 | [5 empty] | 2.3 |  |  |  |  | 32 |  |  |  | 0 | 0.399 |  |  | 0.059 | 0.073 | [5 empty] | 27.1 |  |  |  |  | 54.1 |  | 22.7 |  | 6.8 | 0.023 |  | 18.5 | 106.44 | 0.46 |  |  |  |  | 18.364 | 17.511 | [6 empty] | 30.51 | 6.9 | 7.2
2009-07-05 | 6.08 | 4.89 | [5 empty] | 1.55 |  |  |  |  | 29 |  |  |  | 0 | 0.419 |  |  | 0.059 | 0.114 | [5 empty] | 26.9 |  |  |  |  | 53.8 |  | 21.3 |  | 6 | 0.051 |  | 19.4 | 73.93 | 0.34 |  |  |  |  | 18.541 | 18.743 | [6 empty] | 30.82 | 6.9 | 7.2
2009-07-06 | 6.01 | 5 | [5 empty] | 1.77 |  |  |  |  | 43 |  |  |  | 0 | 0.467 |  |  | 0.117 | 0.147 | [5 empty] | 27.5 |  |  |  |  | 55 |  | 24.7 |  | 5.4 | 0.069 |  | 19.9 | 83.79 | 0.6 |  |  |  |  | 16.92 | 16.06 | [6 empty] | 31.09 | 6.9 | 7.2
2009-07-07 | 6.04 | 5.04 | [5 empty] | 1.955 |  |  |  |  | 38 |  |  |  | 0 | 0.5075 |  |  | 0.0905 | 0.121 | [5 empty] | 26.5 |  |  |  |  | 53 |  | 23.2 |  | 5.65 | 0.064 |  | 18.95 | 90.295 | 0.63 |  |  |  |  | 16.938 | 15.866 | [6 empty] | 30.33 | 6.9 | 7.2
2009-07-08 | 6.07 | 5.08 | [5 empty] | 2.14 |  |  |  |  | 33 |  |  |  | 0 | 0.548 |  |  | 0.064 | 0.095 | [5 empty] | 25.5 |  |  |  |  | 51 |  | 21.7 |  | 5.9 | 0.059 |  | 18 | 96.8 | 0.66 |  |  |  |  | 16.956 | 15.672 | [6 empty] | 29.57 | 6.9 | 7.2
2009-07-09 | 6.47 | 5.47 | [5 empty] | 2.14 |  |  |  |  | 32 |  |  |  | 0 | 0.53 |  |  | 0.06 | 0.081 | [5 empty] | 27.8 |  |  |  |  | 55.6 |  | 15.2 |  | 7.3 | 0.039 |  | 18.2 | 88.24 | 0.69 |  |  |  |  | 17.347 | 14.14 | [6 empty] | 29.11 | 6.8 | 6.9
2009-07-10 | 6.39 | 5.42 | [5 empty] | 2.05 |  |  |  |  | 31 |  |  |  | 0 | 0.561 |  |  | 0.126 | 0.097 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 17.5 |  | 6.9 | 0.057 |  | 18.3 | 88.51 | 0.72 |  |  |  |  | 18.687 | 14.482 | [6 empty] | 29 | 6.7 | 6.9
2009-07-11 | 6.31 | 5.16 | [5 empty] | 2.18 |  |  |  |  | 33 |  |  |  | 0 | 0.558 |  |  | 0.147 | 0.147 | [5 empty] | 29.4 |  |  |  |  | 58.8 |  | 22.6 |  | 6.8 | 0.057 |  | 18.4 | 108.76 | 0.57 |  |  |  |  | 18.802 | 17.98 | [6 empty] | 28.75 | 6.7 | 6.9
2009-07-12 | 6.23 | 5.19 | [5 empty] | 2.22 |  |  |  |  | 36 |  |  |  | 0 | 0.548 |  |  | 0.054 | 0.163 | [5 empty] | 27.1 |  |  |  |  | 54.2 |  | 22.7 |  | 6.7 | 0.053 |  | 19.5 | 91.93 | 0.61 |  |  |  |  | 15.657 | 14.754 | [6 empty] | 29.88 | 6.7 | 6.9
2009-07-13 | 6.16 | 5.15 | [5 empty] | 2.19 |  |  |  |  | 35 |  |  |  | 0 | 0.567 |  |  | 0.048 | 0.12 | [5 empty] | 23.8 |  |  |  |  | 49.6 |  | 23.7 |  | 6.4 | 0.048 |  | 19.9 | 87.63 | 0.72 |  |  |  |  | 14.56 | 13.65 | [6 empty] | 30.38 | 6.6 | 6.9
2009-07-14 | 6.365 | 5.085 | [5 empty] | 2.16 |  |  |  |  | 30.5 |  |  |  | 0 | 0.524 |  |  | 0.0485 | 0.098 | [5 empty] | 25.2 |  |  |  |  | 51.4 |  | 22.35 |  | 6.45 | 0.0495 |  | 19.75 | 92.325 | 0.645 |  |  |  |  | 15.673 | 14.996 | [6 empty] | 28.1 | 6.55 | 6.9
2009-07-15 | 6.57 | 5.02 | [5 empty] | 2.13 |  |  |  |  | 26 |  |  |  | 0 | 0.481 |  |  | 0.049 | 0.076 | [5 empty] | 26.6 |  |  |  |  | 53.2 |  | 21 |  | 6.5 | 0.051 |  | 19.6 | 97.02 | 0.57 |  |  |  |  | 16.786 | 16.342 | [6 empty] | 25.82 | 6.5 | 6.9
2009-07-16 | 6.45 | 5.19 | [5 empty] | 2.11 |  |  |  |  | 30 |  |  |  | 0 | 0.51 |  |  | 0.051 | 0.076 | [5 empty] | 26.9 |  |  |  |  | 53.8 |  | 21.6 |  | 5 | 0.047 |  | 20.1 | 108.88 | 0.62 |  |  |  |  | 19.002 | 18.117 | [6 empty] | 28.17 | 6.5 | 6.9
2009-07-17 | 6.01 | 5.15 | [5 empty] | 2.1 |  |  |  |  | 37 |  |  |  | 0 | 0.494 |  |  | 0.054 | 0.08 | [5 empty] | 26.7 |  |  |  |  | 53.4 |  | 21.8 |  | 6.1 | 0.053 |  | 21.6 | 101.85 | 0.59 |  |  |  |  | 18.063 | 17.207 | [6 empty] | 31.1 | 6.5 | 6.9
2009-07-18 | 6.16 | 5.31 | [5 empty] | 2.12 |  |  |  |  | 31 |  |  |  | 0 | 0.471 |  |  | 0.054 | 0.12 | [5 empty] | 26.5 |  |  |  |  | 53 |  | 22.1 |  | 5.8 | 0.047 |  | 19.6 | 105.84 | 0.5 |  |  |  |  | 19.19 | 18.36 | [6 empty] | 22.82 | 6.6 | 7.1
2009-07-19 | 6.29 | 5.05 | [5 empty] | 2.08 |  |  |  |  | 35 |  |  |  | 0 | 0.561 |  |  | 0.053 | 0.08 | [5 empty] | 26.3 |  |  |  |  | 52.5 |  | 20.4 |  | 6 | 0.053 |  | 20.3 | 89.48 | 0.64 |  |  |  |  | 15.802 | 14.916 | [6 empty] | 30.51 | 6.6 | 7.3
2009-07-20 | 6.3 | 5.31 | [5 empty] | 2.07 |  |  |  |  | 33 |  |  |  | 0 | 0.574 |  |  | 0.06 | 0.09 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 21.5 |  | 5.8 | 0.052 |  | 20.4 | 88.49 | 0.73 |  |  |  |  | 15.307 | 14.342 | [6 empty] | 29.57 | 6.9 | 7.6
2009-07-21 | 6.21 | 5.23 | [5 empty] | 2.07 |  |  |  |  | 32 |  |  |  | 0 | 0.5855 |  |  | 0.059 | 0.0855 | [5 empty] | 26.75 |  |  |  |  | 53.5 |  | 21.9 |  | 5.95 | 0.0505 |  | 20.35 | 97.165 | 0.65 |  |  |  |  | 17.1285 | 16.261 | [6 empty] | 30.715 | 7 | 7.6
2009-07-22 | 6.12 | 5.15 | [5 empty] | 2.07 |  |  |  |  | 31 |  |  |  | 0 | 0.597 |  |  | 0.058 | 0.081 | [5 empty] | 26.7 |  |  |  |  | 53.4 |  | 22.3 |  | 6.1 | 0.049 |  | 20.3 | 105.84 | 0.57 |  |  |  |  | 18.95 | 18.18 | [6 empty] | 31.86 | 7.1 | 7.6
2009-07-23 | 6.38 | 5.33 | [5 empty] | 2.07 |  |  |  |  | 29 |  |  |  | 0 | 0.481 |  |  | 0.06 | 0.088 | [5 empty] | 27.4 |  |  |  |  | 54.7 |  | 21.5 |  | 6 | 0.08 |  | 20.3 | 107.56 | 0.57 |  |  |  |  | 19.319 | 18.513 | [6 empty] | 28.17 | 7.1 | 7.7
2009-07-24 | 6.34 | 5.59 | [5 empty] | 2.12 |  |  |  |  | 28 |  |  |  | 0 | 0.481 |  |  | 0.062 | 0.121 | [5 empty] | 25.5 |  |  |  |  | 51 |  | 19.7 |  | 5.9 | 0.072 |  | 21.4 | 110.99 | 0.6 |  |  |  |  | 20.086 | 18.514 | [6 empty] | 29.11 | 7.1 | 7.7
2009-07-25 | 6.35 | 5.24 | [5 empty] | 2.02 |  |  |  |  | 26 |  |  |  | 0 | 0.472 |  |  | 0.061 | 0.085 | [5 empty] | 26.7 |  |  |  |  | 53.4 |  | 23 |  | 6.2 | 0.05 |  | 20.7 | 103.81 | 0.6 |  |  |  |  | 18.656 | 17.96 | [6 empty] | 28.17 | 7.1 | 7.7
2009-07-26 | 6.28 | 5.35 | [5 empty] | 1.99 |  |  |  |  | 23 |  |  |  | 0 | 0.497 |  |  | 0.075 | 0.078 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 23.8 |  | 5.9 | 0.059 |  | 20.8 | 88.57 | 0.77 |  |  |  |  | 15.795 | 14.547 | [6 empty] | 28.92 | 7.1 | 7
2009-07-27 | 6.29 | 5.23 | [5 empty] | 1.98 |  |  |  |  | 20 |  |  |  | 0 | 0.487 |  |  | 0.107 | 0.126 | [5 empty] | 28 |  |  |  |  | 56 |  | 22.6 |  | 6 | 0.061 |  | 20.8 | 88.99 | 0.88 |  |  |  |  | 14.98 | 14.11 | [6 empty] | 29.32 | 7.1 | 7
2009-07-28 | 6.37 | 5.17 | [5 empty] | 1.905 |  |  |  |  | 22 |  |  |  | 0 | 0.4985 |  |  | 0.099 | 0.1135 | [5 empty] | 27.65 |  |  |  |  | 55.3 |  | 22.9 |  | 6.05 | 0.055 |  | 20.75 | 88.78 | 0.825 |  |  |  |  | 16.4895 | 15.1555 | [6 empty] | 30.15 | 7.1 | 7.25
2009-07-29 | 6.45 | 5.11 | [5 empty] | 1.83 |  |  |  |  | 24 |  |  |  | 0 | 0.51 |  |  | 0.091 | 0.101 | [5 empty] | 27.3 |  |  |  |  | 54.6 |  | 23.2 |  | 6.1 | 0.049 |  | 20.7 | 88.885 | 0.8525 |  |  |  |  | 17.999 | 16.201 | [6 empty] | 30.98 | 7.1 | 7.5
2009-07-30 | 6.55 | 5.27 | [5 empty] | 1.76 |  |  |  |  | 24 |  |  |  | 0 | 0.474 |  |  | 0.055 | 0.073 | [5 empty] | 27.5 |  |  |  |  | 55 |  | 23.2 |  | 5.8 | 0.052 |  | 20.6 | 88.8325 | 0.83875 |  |  |  |  | 16.651 | 15.816 | [6 empty] | 31.92 | 7.3 | 7.8
2009-07-31 | 6.41 | 5.1 | [5 empty] | 1.95 |  |  |  |  | 21 |  |  |  | 0 | 0.471 |  |  | 0.063 | 0.087 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 23.6 |  | 6 | 0.059 |  | 20.7 | 88.8587 | 0.84563 |  |  |  |  | 17.633 | 16.835 | [6 empty] | 32.04 | 7.3 | 7.8
2009-08-01 | 6.39 | 5.1 | [5 empty] | 2.1 |  |  |  |  | 32 |  |  |  | 0 | 0.527 |  |  | 0.092 | 0.074 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 24.8 |  | 6.4 | 0.074 |  | 20.8 | 99.91 | 0.51 |  |  |  |  | 18.103 | 17.36 | [6 empty] | 28.26 | 7.3 | 7.8
2009-08-02 | 6.34 | 5.03 | [5 empty] | 2.11 |  |  |  |  | 27 |  |  |  | 0 | 0.482 |  |  | 0.055 | 0.026 | [5 empty] | 27 |  |  |  |  | 54 |  | 24.6 |  | 6.6 | 0.063 |  | 21.5 | 90.6 | 0.54 |  |  |  |  | 16.252 | 15.509 | [6 empty] | 31.54 | 7.3 | 7.8
2009-08-03 | 6.24 | 4.95 | [5 empty] | 2.27 |  |  |  |  | 26 |  |  |  | 0 | 0.498 |  |  | 0.053 | 0.078 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 24.5 |  | 5.9 | 0.056 |  | 21.6 | 89.08 | 0.5 |  |  |  |  | 15.619 | 14.605 | [6 empty] | 30.75 | 7.7 | 8
2009-08-04 | 6.305 | 5.13 | [5 empty] | 2.12 |  |  |  |  | 26 |  |  |  | 0 | 0.502 |  |  | 0.0555 | 0.076 | [5 empty] | 28.25 |  |  |  |  | 56.5 |  | 24.85 |  | 6.15 | 0.0725 |  | 21.4 | 92.75 | 0.555 |  |  |  |  | 16.7645 | 15.7925 | [6 empty] | 30.63 | 7.8 | 8
2009-08-05 | 6.37 | 5.31 | [5 empty] | 1.97 |  |  |  |  | 26 |  |  |  | 0 | 0.506 |  |  | 0.058 | 0.074 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 25.2 |  | 6.4 | 0.089 |  | 21.2 | 96.42 | 0.61 |  |  |  |  | 17.91 | 16.98 | [6 empty] | 30.51 | 7.9 | 8
2009-08-06 | 6.43 | 5.21 | [5 empty] | 1.8 |  |  |  |  | 23 |  |  |  | 0 | 0.484 |  |  | 0.057 | 0.079 | [5 empty] | 27.6 |  |  |  |  | 55.1 |  | 24.5 |  | 6.2 | 0.056 |  | 21.3 | 80.68 | 0.8 |  |  |  |  | 15.1 | 14.081 | [6 empty] | 32.86 | 7.9 | 8
2009-08-07 | 6.43 | 5.22 | [5 empty] | 1.79 |  |  |  |  | 24 |  |  |  | 0 | 0.516 |  |  | 0.063 | 0.068 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 24.6 |  | 6.1 | 0.063 |  | 21.1 | 77.24 | 0.77 |  |  |  |  | 14.679 | 13.677 | [6 empty] | 34.68 | 7.9 | 8
2009-08-08 | 6.61 | 5.06 | [5 empty] | 1.76 |  |  |  |  | 27 |  |  |  | 0 | 0.541 |  |  | 0.055 | 0.075 | [5 empty] | 27.3 |  |  |  |  | 54.6 |  | 24.7 |  | 6.4 | 0.047 |  | 20.8 | 73.49 | 0.84 |  |  |  |  | 13.92 | 12.84 | [6 empty] | 32.04 | 7.9 | 8
2009-08-09 | 6.4 | 5.3 | [5 empty] | 1.76 |  |  |  |  | 25 |  |  |  | 0 | 0.493 |  |  | 0.061 | 0.063 | [5 empty] | 28.3 |  |  |  |  | 56.5 |  | 23.3 |  | 6.2 | 0.057 |  | 20.9 | 75.63 | 0.9 |  |  |  |  | 13.96 | 12.93 | [6 empty] | 30.04 | 7.9 | 8
2009-08-10 | 6.69 | 5.49 | [5 empty] | 1.71 |  |  |  |  | 19 |  |  |  | 0 | 0.489 |  |  | 0.054 | 0.18 | [5 empty] | 40.2 |  |  |  |  | 80.4 |  | 22.4 |  | 5.8 | 0.049 |  | 20.1 | 69.52 | 0.95 |  |  |  |  | 12.903 | 11.884 | [6 empty] | 31.92 | 7.9 | 8.2
2009-08-11 | 6.505 | 5.255 | [5 empty] | 1.685 |  |  |  |  | 18.5 |  |  |  | 0 | 0.5085 |  |  | 0.0525 | 0.2425 | [5 empty] | 39.65 |  |  |  |  | 79.3 |  | 23.15 |  | 6 | 0.058 |  | 19.75 | 73.81 | 0.975 |  |  |  |  | 13.6485 | 12.613 | [6 empty] | 33.865 | 7.9 | 8.2
2009-08-12 | 6.32 | 5.02 | [5 empty] | 1.66 |  |  |  |  | 18 |  |  |  | 0 | 0.528 |  |  | 0.051 | 0.305 | [5 empty] | 39.1 |  |  |  |  | 78.2 |  | 23.9 |  | 6.2 | 0.067 |  | 19.4 | 78.1 | 1 |  |  |  |  | 14.394 | 13.342 | [6 empty] | 35.81 | 7.9 | 8.2
2009-08-13 | 6.65 | 5.15 | [5 empty] | 1.6 |  |  |  |  | 27 |  |  |  | 0 | 0.518 |  |  | 0.051 | 0.302 | [5 empty] | 36.8 |  |  |  |  | 73.6 |  | 23.9 |  | 6.1 | 0.058 |  | 18.7 | 73.82 | 1 |  |  |  |  | 13.86 | 12.87 | [6 empty] | 31.91 | 7.6 | 7.8
2009-08-14 | 6.67 | 5.17 | [5 empty] | 1.85 |  |  |  |  | 22 |  |  |  | 0 | 0.512 |  |  | 0.062 | 0.334 | [5 empty] | 35.7 |  |  |  |  | 71.4 |  | 25 |  | 8.9 | 0.103 |  | 18.4 | 75.3 | 0.84 |  |  |  |  | 13.909 | 12.668 | [6 empty] | 32.39 | 7.8 | 7.3
2009-08-15 | 6.23 | 5.21 | [5 empty] | 1.83 |  |  |  |  | 23 |  |  |  | 0 | 0.501 |  |  | 0.063 | 0.315 | [5 empty] | 36.2 |  |  |  |  | 72.4 |  | 24.7 |  | 8.7 | 0.65 |  | 18.3 | 74.9 | 0.81 |  |  |  |  | 13.884 | 12.877 | [6 empty] | 31.45 | 7.5 | 7.2
2009-08-16 | 6.4 | 5.21 | [5 empty] | 1.81 |  |  |  |  | 27 |  |  |  | 0 | 0.476 |  |  | 0.057 | 0.253 | [5 empty] | 32.6 |  |  |  |  | 65.2 |  | 23.4 |  | 7.2 | 0.057 |  | 18.3 | 75.1 | 0.86 |  |  |  |  | 13.495 | 12.376 | [6 empty] | 31.92 | 7.5 | 7.1
2009-08-17 | 6.315 | 5.21 | [5 empty] | 1.82 |  |  |  |  | 25 |  |  |  | 0 | 0.4885 |  |  | 0.06 | 0.284 | [5 empty] | 34.4 |  |  |  |  | 68.8 |  | 24.05 |  | 7.95 | 0.3535 |  | 18.3 | 75 | 0.835 |  |  |  |  | 14.11 | 13.18 | [6 empty] | 31.685 | 7.5 | 7.15
2009-08-18 | 6.67 | 5.205 | [5 empty] | 1.745 |  |  |  |  | 19.5 |  |  |  | 0 | 0.4565 |  |  | 0.0545 | 0.284 | [5 empty] | 43.1 |  |  |  |  | 46.1 |  | 23.1 |  | 8.15 | 0.06 |  | 18.75 | 75.13 | 0.975 |  |  |  |  | 17.167 | 12.247 | [6 empty] | 31.57 | 7.5 | 7.25
2009-08-19 | 6.81 | 5.26 | [5 empty] | 1.73 |  |  |  |  | 21 |  |  |  | 0 | 0.462 |  |  | 0.053 | 0.224 | [5 empty] | 44.2 |  |  |  |  | 8.3 |  | 23.6 |  | 8.4 | 0.066 |  | 19 | 75.87 | 1.08 |  |  |  |  | 15.864 | 12.854 | [6 empty] | 31.69 | 7.5 | 7.1
2009-08-20 | 6.53 | 5.15 | [5 empty] | 1.76 |  |  |  |  | 18 |  |  |  | 0 | 0.451 |  |  | 0.056 | 0.344 | [5 empty] | 42 |  |  |  |  | 83.9 |  | 22.6 |  | 7.9 | 0.054 |  | 18.5 | 74.39 | 0.87 |  |  |  |  | 14.813 | 12.735 | [6 empty] | 31.45 | 7.5 | 7.4
2009-08-21 | 6.32 | 5.22 | [5 empty] | 1.71 |  |  |  |  | 16 |  |  |  | 0 | 0.451 |  |  | 0.052 | 0.217 | [5 empty] | 41.7 |  |  |  |  | 83.4 |  | 23.7 |  | 8.2 | 0.041 |  | 18.6 | 73.43 | 0.93 |  |  |  |  | 13.762 | 12.616 | [6 empty] | 29.25 | 7.5 | 7.2
2009-08-22 | 6.39 | 5.22 | [5 empty] | 1.69 |  |  |  |  | 26 |  |  |  | 0 | 0.487 |  |  | 0.057 | 0.163 | [5 empty] | 43.8 |  |  |  |  | 87.6 |  | 23.9 |  | 7.8 | 0.054 |  | 18.6 | 72.37 | 1.12 |  |  |  |  | 12.809 | 11.703 | [6 empty] | 30.46 | 7.5 | 7.2
2009-08-23 | 6.25 | 5.22 | [5 empty] | 1.78 |  |  |  |  | 20 |  |  |  | 0 | 0.597 |  |  | 0.072 | 0.184 | [5 empty] | 40 |  |  |  |  | 80 |  | 22 |  | 6.8 | 0.067 |  | 18.6 | 78.21 | 1.16 |  |  |  |  | 13.125 | 12.065 | [6 empty] | 29.52 | 7.5 | 7.2
2009-08-24 | 5.97 | 5.23 | [5 empty] | 1.85 |  |  |  |  | 22 |  |  |  | 0 | 0.481 |  |  | 0.049 | 0.196 | [5 empty] | 43.5 |  |  |  |  | 87 |  | 21.4 |  | 6.5 | 0.067 |  | 18.4 | 74.95 | 1.03 |  |  |  |  | 12.9 | 11.8 | [6 empty] | 29.6 | 7.5 | 7.2
2009-08-25 | 6.11 | 5.225 | [5 empty] | 1.815 |  |  |  |  | 21 |  |  |  | 0 | 0.539 |  |  | 0.0605 | 0.19 | [5 empty] | 41.75 |  |  |  |  | 83.5 |  | 21.7 |  | 6.65 | 0.067 |  | 18.5 | 76.58 | 1.095 |  |  |  |  | 12.213 | 11.102 | [6 empty] | 29.56 | 7.5 | 7.2
2009-08-26 | 6.24 | 5.33 | [5 empty] | 1.88 |  |  |  |  | 24 |  |  |  | 0 | 0.441 |  |  | 0.084 | 0.156 | [5 empty] | 39.9 |  |  |  |  | 79.8 |  | 25.1 |  | 7.7 | 0.062 |  | 18.3 | 96.53 | 1.61 |  |  |  |  | 14.525 | 12.532 | [6 empty] | 31.09 | 7.8 | 7.4
2009-08-27 | 6.32 | 5.17 | [5 empty] | 1.88 |  |  |  |  | 20 |  |  |  | 0 | 0.486 |  |  | 0.057 | 0.113 | [5 empty] | 41.4 |  |  |  |  | 82.8 |  | 25.2 |  | 7 | 0.044 |  |  | 94.82 | 1.14 |  |  |  |  | 14.36 | 14.24 | [6 empty] | 32.13 | 7.8 | 7.4
2009-08-28 | 6.44 | 5.12 | [5 empty] | 2 |  |  |  |  | 36 |  |  |  | 0 | 0.477 |  |  | 0.057 | 0.166 | [5 empty] | 28.8 |  |  |  |  | 57.6 |  | 22 |  | 6.8 | 0.056 |  | 16.9 | 90.41 | 1.21 |  |  |  |  | 14.74 | 12.78 | [6 empty] | 34.72 | 7.8 | 7.4
2009-08-29 | 6.7 | 5 | [5 empty] | 2.08 |  |  |  |  | 34 |  |  |  | 0 | 0.52 |  |  | 0.062 | 0.1 | [5 empty] | 27.1 |  |  |  |  | 54.3 |  | 23.5 |  | 6.6 | 0.059 |  | 17.4 | 83.79 | 0.96 |  |  |  |  | 12.62 | 12.52 | [6 empty] | 34.27 | 7.8 | 7.4
2009-08-30 | 6.57 | 5.06 | [5 empty] | 2.04 |  |  |  |  | 35 |  |  |  | 0 | 0.4985 |  |  | 0.0595 | 0.133 | [5 empty] | 27.95 |  |  |  |  | 55.95 |  | 22.75 |  | 6.7 | 0.0575 |  | 17.15 | 87.1 | 1.085 |  |  |  |  | 12.76 | 11.69 | [6 empty] | 34.495 | 7.8 | 7.4
2009-08-31 | 6.73 | 5.24 | [5 empty] | 1.87 |  |  |  |  | 33 |  |  |  | 0 | 0.686 |  |  | 0.06 | 0.179 | [5 empty] | 32.9 |  |  |  |  | 65.9 |  | 26.1 |  | 6.4 | 0.058 |  | 15.4 | 77.11 | 1.18 |  |  |  |  | 12.57 | 11.49 | [6 empty] | 32.86 | 7.8 | 7.7
2009-09-01 | 6.65 | 5.15 | [5 empty] | 1.97 |  |  |  |  | 34 |  |  |  | 0 | 0.59225 |  |  | 0.05975 | 0.156 | [5 empty] | 30.425 |  |  |  |  | 60.925 |  | 24.425 |  | 6.55 | 0.05775 |  | 16.275 | 69.26 | 0.96 |  |  |  |  | 11.867 | 10.744 | [6 empty] | 33.6775 | 7.8 | 7.55
2009-09-02 | 6.41 | 5.22 | [5 empty] | 1.98 |  |  |  |  | 39 |  |  |  | 0 | 0.567 |  |  | 0.059 | 0.123 | [5 empty] | 32.5 |  |  |  |  | 65 |  | 25.1 |  | 7 | 0.069 |  | 15.2 | 83.79 | 1.24 |  |  |  |  | 13.89 | 11.91 | [6 empty] | 32.01 | 7.8 | 7.5
2009-09-03 | 6.75 | 5.2 | [5 empty] | 2.07 |  |  |  |  | 32 |  |  |  | 0 | 0.379 |  |  | 0.062 | 0.066 | [5 empty] | 27.6 |  |  |  |  | 55.2 |  | 25.9 |  | 6.8 | 0.092 |  | 16 | 83.79 | 0.85 |  |  |  |  | 13.41 | 13.29 | [6 empty] | 31.22 | 7.8 | 7.5
2009-09-04 | 6.74 | 5.19 | [5 empty] | 1.97 |  |  |  |  | 28 |  |  |  | 0 | 0.511 |  |  | 0.06 | 0.068 | [5 empty] | 28.4 |  |  |  |  | 56.7 |  | 24.9 |  | 6.7 | 0.089 |  | 16.5 | 77.18 | 0.93 |  |  |  |  | 13.16 | 12.07 | [6 empty] | 33.33 | 7.8 | 7.6
2009-09-05 | 6.93 | 5.17 | [5 empty] | 2.04 |  |  |  |  | 33 |  |  |  | 0 | 0.518 |  |  | 0.056 | 0.066 | [5 empty] | 28.6 |  |  |  |  | 57.2 |  | 22.4 |  | 6.9 | 0.088 |  | 16.4 | 77.88 | 0.88 |  |  |  |  | 13.231 | 12.123 | [6 empty] | 29.57 | 7.8 | 7.8
2009-09-06 | 6.8 | 6.8 | [5 empty] | 2.13 |  |  |  |  | 34 |  |  |  | 0 | 0.497 |  |  | 0.052 | 0.087 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 21.7 |  | 7.4 | 0.079 |  | 16.5 | 83.61 | 0.84 |  |  |  |  | 13.805 | 12.769 | [6 empty] | 29.96 | 7.8 | 7.8
2009-09-07 | 6.34 | 5.09 | [5 empty] | 2.08 |  |  |  |  | 31 |  |  |  | 0 | 0.486 |  |  | 0.061 | 0.069 | [5 empty] | 29.9 |  |  |  |  | 59.8 |  | 21.1 |  | 6.7 | 0.074 |  | 16.4 | 77.18 | 0.76 |  |  |  |  | 13.38 | 12.34 | [6 empty] | 29.81 | 7.8 | 7.8
2009-09-08 | 6.57 | 5.945 | [5 empty] | 2.105 |  |  |  |  | 32.5 |  |  |  | 0 | 0.4915 |  |  | 0.0565 | 0.078 | [5 empty] | 28.65 |  |  |  |  | 57.3 |  | 21.9 |  | 7.2 | 0.0865 |  | 16.75 | 79.735 | 1.03 |  |  |  |  | 13.672 | 11.668 | [6 empty] | 30.16 | 7.8 | 7.65
2009-09-09 | 6.74 | 5.12 | [5 empty] | 1.9 |  |  |  |  | 28 |  |  |  | 0 | 0.547 |  |  | 0.061 | 0.175 | [5 empty] | 28.2 |  |  |  |  | 56.5 |  | 22.7 |  | 7.7 | 0.099 |  | 17.1 | 82.29 | 1.3 |  |  |  |  | 13.4225 | 11.378 | [6 empty] | 30.51 | 7.8 | 7.5
2009-09-10 | 6.56 | 5.33 | [5 empty] | 1.91 |  |  |  |  | 30 |  |  |  | 0 | 0.695 |  |  | 0.06 | 0.107 | [5 empty] | 29 |  |  |  |  | 58 |  | 21.6 |  | 7.4 | 0.082 |  | 16.5 | 88.64 | 1.72 |  |  |  |  | 13.173 | 11.088 | [6 empty] | 30.98 | 7.8 | 7.5
2009-09-11 | 6.18 | 5.32 | [5 empty] | 1.95 |  |  |  |  | 26 |  |  |  | 0 | 0.662 |  |  | 0.056 | 0.104 | [5 empty] | 27.9 |  |  |  |  | 55.9 |  | 22.3 |  | 7.2 | 0.087 |  | 16.7 | 76.91 | 0.87 |  |  |  |  | 13.523 | 12.372 | [6 empty] | 29.85 | 7.8 | 7.5
2009-09-12 | 6.2 | 5.31 | [5 empty] | 2 |  |  |  |  | 29 |  |  |  | 0 | 0.647 |  |  | 0.061 | 0.114 | [5 empty] | 27.7 |  |  |  |  | 55.4 |  | 21.6 |  | 7 | 0.074 |  | 16.5 | 71.95 | 0.77 |  |  |  |  | 12.884 | 11.786 | [6 empty] | 29.83 | 7.8 | 7.5
2009-09-13 | 5.59 | 5.25 | [5 empty] | 1.99 |  |  |  |  | 30 |  |  |  | 0 | 0.637 |  |  | 0.064 | 0.081 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 21.9 |  | 6.9 | 0.063 |  | 16.4 | 80.84 | 0.81 |  |  |  |  | 14.193 | 13.107 | [6 empty] | 31.18 | 7.8 | 7.7
2009-09-14 | 6.64 | 5.27 | [5 empty] | 2.05 |  |  |  |  | 31 |  |  |  | 0 | 0.758 |  |  | 0.061 | 0.103 | [5 empty] | 30.9 |  |  |  |  | 61.8 |  | 23.3 |  | 6.7 | 0.063 |  | 16.3 | 77.99 | 0.99 |  |  |  |  | 13.16 | 11.66 | [6 empty] | 30.65 | 7.8 | 7.9
2009-09-15 | 6.115 | 5.26 | [5 empty] | 2.02 |  |  |  |  | 30.5 |  |  |  | 0 | 0.6975 |  |  | 0.0625 | 0.092 | [5 empty] | 29.15 |  |  |  |  | 58.3 |  | 23.5 |  | 6.75 | 0.0675 |  | 16.25 | 72.37 | 0.84 |  |  |  |  | 12.61 | 11.86 | [6 empty] | 31.06 | 7.8 | 7.9
2009-09-16 | 6.39 | 5.32 | [5 empty] | 1.84 |  |  |  |  | 29 |  |  |  | 0 | 0.694 |  |  | 0.057 | 0.077 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 23.7 |  | 6.8 | 0.072 |  | 16.2 | 79.95 | 0.94 |  |  |  |  | 14.146 | 13.038 | [6 empty] | 31.47 | 7.8 | 7.9
2009-09-17 | 6.47 | 5.35 | [5 empty] | 1.72 |  |  |  |  | 31 |  |  |  | 0 | 0.667 |  |  | 0.062 | 0.084 | [5 empty] | 31.7 |  |  |  |  | 63.4 |  | 23.7 |  | 6.4 | 0.054 |  | 16.3 | 63.9 | 0.64 |  |  |  |  | 13.435 | 12.317 | [6 empty] | 29.6 | 7.8 | 7.9
2009-09-18 | 6.22 | 5.29 | [5 empty] | 1.64 |  |  |  |  | 32 |  |  |  | 0 | 0.618 |  |  | 0.064 | 0.073 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 23.7 |  | 6.7 | 0.057 |  | 15 | 38.23 | 0.67 |  |  |  |  | 13.527 | 12.151 | [6 empty] | 30.12 | 7.3 | 8
2009-09-19 | 6.27 | 5.32 | [5 empty] | 1.77 |  |  |  |  | 32 |  |  |  | 0 | 0.616 |  |  | 0.067 | 0.079 | [5 empty] | 27.2 |  |  |  |  | 54.4 |  | 23.4 |  | 6.9 | 0.059 |  | 14.8 | 70.41 | 0.7 |  |  |  |  | 13.07 | 12.95 | [6 empty] | 32.09 | 7.3 | 8
2009-09-20 | 7.05 | 5.31 | [5 empty] | 1.64 |  |  |  |  | 31 |  |  |  | 0 | 0.606 |  |  | 0.073 | 0.089 | [5 empty] | 27.6 |  |  |  |  | 55.3 |  | 24.3 |  | 6.7 | 0.061 |  | 15 | 74.46 | 1.33 |  |  |  |  | 13.379 | 11.368 | [6 empty] | 32.83 | 7.2 | 8
2009-09-21 | 6.63 | 5.44 | [5 empty] | 1.79 |  |  |  |  | 25 |  |  |  | 0 | 0.584 |  |  | 0.061 | 0.106 | [5 empty] | 27.8 |  |  |  |  | 55.7 |  | 26.3 |  | 6.9 | 0.059 |  | 14.2 | 63.97 | 1.13 |  |  |  |  | 12.058 | 9.931 | [6 empty] | 31.92 | 7.2 | 8
2009-09-22 | 6.84 | 5.375 | [5 empty] | 1.715 |  |  |  |  | 28 |  |  |  | 0 | 0.595 |  |  | 0.067 | 0.0975 | [5 empty] | 27.7 |  |  |  |  | 55.5 |  | 26.05 |  | 6.8 | 0.0615 |  | 14 | 67.73 | 1.045 |  |  |  |  | 12.834 | 10.931 | [6 empty] | 32.755 | 7.2 | 8
2009-09-23 | 6.11 | 5.41 | [5 empty] | 1.96 |  |  |  |  | 33 |  |  |  | 0 | 0.869 |  |  | 0.07 | 0.128 | [5 empty] | 31.2 |  |  |  |  | 62.4 |  | 25.8 |  | 6.7 | 0.064 |  | 13.8 | 71.49 | 0.96 |  |  |  |  | 13.61 | 11.931 | [6 empty] | 33.59 | 7.2 | 8
2009-09-24 | 6.59 | 5.19 | [5 empty] | 1.95 |  |  |  |  | 32 |  |  |  | 0 | 1.713 |  |  | 0.065 | 0.117 | [5 empty] | 27.5 |  |  |  |  | 55 |  | 25.6 |  | 6.9 | 0.058 |  | 14.5 | 77.18 | 0.86 |  |  |  |  | 13.56 | 12.47 | [6 empty] | 31.66 | 7.1 | 8.1
2009-09-25 | 6.49 | 5.18 | [5 empty] | 1.96 |  |  |  |  | 35 |  |  |  | 0 | 1.307 |  |  | 0.065 | 0.122 | [5 empty] | 27.6 |  |  |  |  | 55.3 |  | 26.4 |  | 6.6 | 0.071 |  | 14.3 | 76.8 | 0.88 |  |  |  |  | 13.404 | 12.278 | [6 empty] | 32.86 | 6.7 | 8.2
2009-09-26 | 6.56 | 5.21 | [5 empty] | 2.03 |  |  |  |  | 36 |  |  |  | 0 | 1.099 |  |  | 0.057 | 0.099 | [5 empty] | 25.2 |  |  |  |  | 50.4 |  | 26.7 |  | 7.1 | 0.072 |  | 13.5 | 73.34 | 0.64 |  |  |  |  | 13.581 | 12.474 | [6 empty] | 31.92 | 6.5 | 7.7
2009-09-27 | 6.44 | 5.19 | [5 empty] | 2.14 |  |  |  |  | 31 |  |  |  | 0 | 1.131 |  |  | 0.079 | 0.088 | [5 empty] | 26.3 |  |  |  |  | 52.6 |  | 26.2 |  | 6.9 | 0.061 |  | 13.5 | 77.73 | 0.58 |  |  |  |  | 14.136 | 13.024 | [6 empty] | 30.97 | 6.5 | 7.9
2009-09-28 | 6.31 | 5.14 | [5 empty] | 2.16 |  |  |  |  | 31 |  |  |  | 0 | 0.984 |  |  | 0.098 | 0.123 | [5 empty] | 27.7 |  |  |  |  | 55.4 |  | 25.9 |  | 5.7 | 0.067 |  | 13.4 | 74.97 | 0.74 |  |  |  |  | 14.54 | 11.75 | [6 empty] | 30.52 | 6.5 | 7.9
2009-09-29 | 6.375 | 5.165 | [5 empty] | 2.15 |  |  |  |  | 31 |  |  |  | 0 | 1.0575 |  |  | 0.0885 | 0.1055 | [5 empty] | 27 |  |  |  |  | 54 |  | 24.85 |  | 5.75 | 0.069 |  | 13.35 | 77.085 | 0.825 |  |  |  |  | 14.3695 | 11.9475 | [6 empty] | 30.045 | 6.5 | 7.9
2009-09-30 | 6.45 | 5.12 | [5 empty] | 2.05 |  |  |  |  | 30 |  |  |  | 0 | 0.864 |  |  | 0.061 | 0.085 | [5 empty] | 27.9 |  |  |  |  | 55.8 |  | 23.8 |  | 5.8 | 0.071 |  | 13.3 | 79.2 | 0.91 |  |  |  |  | 14.199 | 12.145 | [6 empty] | 29.57 | 6.5 | 7.9
2009-10-01 | 6.67 | 5.24 | [5 empty] | 1.98 |  |  |  |  | 27 |  |  |  | 0 | 0.885 |  |  | 0.06 | 0.098 | [5 empty] | 25.5 |  |  |  |  | 51.1 |  | 24.4 |  | 5.9 | 0.008 |  | 12.6 | 76.62 | 0.071 |  |  |  |  | 15.189 | 12.928 | [6 empty] | 29.57 | 6.5 | 8.2
2009-10-02 | 6.56 | 5.18 | [5 empty] | 2.015 |  |  |  |  | 28.5 |  |  |  | 0 | 0.8745 |  |  | 0.0605 | 0.0915 | [5 empty] | 26.7 |  |  |  |  | 53.45 |  | 24.2 |  | 5.95 | 0.011 |  | 12.55 | 77.425 | 0.1605 |  |  |  |  | 14.7 | 13.0155 | [6 empty] | 29.725 | 6.5 | 8.2
2009-10-03 | 6.4 | 5.13 | [5 empty] | 2.46 |  |  |  |  | 21 |  |  |  | 0 | 0.0972 |  |  | 0.077 | 0.106 | [5 empty] | 26 |  |  |  |  | 52 |  | 24 |  | 6 | 0.014 |  | 12.5 | 78.23 | 0.25 |  |  |  |  | 14.211 | 13.103 | [6 empty] | 29.88 | 6.5 | 8.2
2009-10-04 | 5.74 | 4.87 | [5 empty] | 2.27 |  |  |  |  | 22 |  |  |  | 0 | 0.762 |  |  | 0.073 | 0.157 | [5 empty] | 26.2 |  |  |  |  | 52.4 |  | 24.9 |  | 6.2 | 0.043 |  | 11.8 | 74.97 | 0.37 |  |  |  |  | 14.238 | 13.124 | [6 empty] | 33.13 | 6.7 | 8.4
2009-10-05 | 6.74 | 4.94 | [5 empty] | 1.99 |  |  |  |  | 23 |  |  |  | 0 | 0.651 |  |  | 0.076 | 0.193 | [5 empty] | 27.1 |  |  |  |  | 54.2 |  | 23.7 |  | 5.9 | 0.038 |  | 12 | 68.36 | 0.44 |  |  |  |  | 13.61 | 12.77 | [6 empty] | 31.91 | 6.7 | 8.8
2009-10-06 | 6.24 | 4.905 | [5 empty] | 2.13 |  |  |  |  | 22.5 |  |  |  | 0 | 0.7065 |  |  | 0.0745 | 0.175 | [5 empty] | 26.65 |  |  |  |  | 53.3 |  | 23.25 |  | 5.65 | 0.056 |  | 6.95 | 71.88 | 0.64 |  |  |  |  | 13.502 | 12.665 | [6 empty] | 32.52 | 6.8 | 9.2
2009-10-07 | 6.31 | 4.95 | [5 empty] | 1.92 |  |  |  |  | 30 |  |  |  | 0 | 0.6 |  |  | 0.054 | 0.207 | [5 empty] | 26.5 |  |  |  |  | 53 |  | 22.8 |  | 5.4 | 0.074 |  | 1.9 | 74.79 | 0.675 |  |  |  |  | 14.715 | 13.62 | [6 empty] | 32.215 | 6.8 | 9.5
2009-10-08 | 6.24 | 4.99 | [5 empty] | 1.92 |  |  |  |  | 32 |  |  |  | 0 | 0.595 |  |  | 0.077 | 0.197 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 23.3 |  | 5 | 0.064 |  | 11.8 | 77.59 | 0.71 |  |  |  |  | 14.446 | 13.374 | [6 empty] | 30.52 | 6.8 | 9.8
2009-10-09 | 6.09 | 4.96 | [5 empty] | 1.98 |  |  |  |  | 33 |  |  |  | 0 | 0.597 |  |  | 0.087 | 0.146 | [5 empty] | 28.6 |  |  |  |  | 57.2 |  | 23.9 |  | 6.2 | 0.058 |  | 12.8 | 71.86 | 0.62 |  |  |  |  | 13.656 | 12.527 | [6 empty] | 31.3675 | 6.8 | 9.8
2009-10-10 | 6.26 | 4.97 | [5 empty] | 2.02 |  |  |  |  | 33 |  |  |  | . | 0.579 |  |  | 0.084 | 0.85 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 24.3 |  | 6.9 | 0.069 |  | 12.4 | 72.77 | 0.47 |  |  |  |  | 14.31 | 13.25 | [6 empty] | 32.06 | 6.9 | 9.8
2009-10-11 | 6.39 | 4.97 | [5 empty] | 2.03 |  |  |  |  | 23 |  |  |  | 0 | 0.585 |  |  | 0.052 | 0.086 | [5 empty] | 28 |  |  |  |  | 56.1 |  | 23.3 |  | 6.7 | 0.064 |  | 12.4 | 72.77 | 0.44 |  |  |  |  | 13.46 | 13.38 | [6 empty] | 30.98 | 6.9 | 9.8
2009-10-12 | 6.58 | 5.07 | [5 empty] | 1.99 |  |  |  |  | 24 |  |  |  | 0 | 0.728 |  |  | 0.059 | 0.116 | [5 empty] | 27.5 |  |  |  |  | 55 |  | 24.6 |  | 6.9 | 0.033 |  | 12.2 | 69.44 | 0.6 |  |  |  |  | 13.273 | 12.159 | [6 empty] | 30.04 | 6.9 | 9.5
2009-10-13 | 6.485 | 5.02 | [5 empty] | 2.01 |  |  |  |  | 23.5 |  |  |  | 0 | 0.6565 |  |  | 0.0555 | 0.101 | [5 empty] | 27.75 |  |  |  |  | 55.55 |  | 24.25 |  | 6.8 | 0.04 |  | 11.85 | 75.225 | 0.68 |  |  |  |  | 14.4045 | 12.808 | [6 empty] | 30.46 | 6.9 | 9.5
2009-10-14 | 6.31 | 5.03 | [5 empty] | 1.97 |  |  |  |  | 23 |  |  |  | 0 | 0.638 |  |  | 0.063 | 0.114 | [5 empty] | 25.1 |  |  |  |  | 50.2 |  | 23.9 |  | 6.7 | 0.047 |  | 11.5 | 81.01 | 0.76 |  |  |  |  | 15.536 | 13.457 | [6 empty] | 30.88 | 6.9 | 9.5
2009-10-15 | 6.42 | 5.06 | [5 empty] | 1.68 |  |  |  |  | 24 |  |  |  | 0 | 0.594 |  |  | 0.065 | 0.091 | [5 empty] | 23.5 |  |  |  |  | 47 |  | 26.4 |  | 5.7 | 0.041 |  | 11 | 74.97 | 0.99 |  |  |  |  | 13.86 | 12.77 | [6 empty] | 31.86 | 7.1 | 10
2009-10-16 | 6.4 | 4.95 | [5 empty] | 1.87 |  |  |  |  | 19 |  |  |  | 0 | 0.58 |  |  | 0.11 | 0.137 | [5 empty] | 26.6 |  |  |  |  | 53.2 |  | 25.4 |  | 6.2 | 0.038 |  | 11.1 | 60.13 | 0.25 |  |  |  |  | 13.968 | 12.869 | [6 empty] | 28.64 | 7.6 | 11.6
2009-10-17 | 6.56 | 4.92 | [5 empty] | 1.75 |  |  |  |  | 19 |  |  |  | 0 | 0.766 |  |  | 0.065 | 0.1 | [5 empty] | 29.4 |  |  |  |  | 59 |  | 21.9 |  | 6 | 0.041 |  | 11.4 | 71.53 | 0.81 |  |  |  |  | 13.781 | 12.665 | [6 empty] | 30.51 | 7.8 | 12.1
2009-10-18 | 6.42 | 5.09 | [5 empty] | 1.63 |  |  |  |  | 23 |  |  |  | 0 | 0.656 |  |  | 0.098 | 0.196 | [5 empty] | 26.1 |  |  |  |  | 52.2 |  | 22.5 |  | 5.7 | 0.046 |  | 11 | 73.36 | 0.96 |  |  |  |  | 14.522 | 13.376 | [6 empty] | 31.02 | 7.5 | 12
2009-10-19 | 6.4 | 5.09 | [5 empty] | 1.63 |  |  |  |  | 27 |  |  |  | 0 | 0.637 |  |  | 0.113 | 0.221 | [5 empty] | 27.9 |  |  |  |  | 55.9 |  | 22.1 |  | 5.4 | 0.067 |  | 10.9 | 67.15 | 0.99 |  |  |  |  | 12.799 | 11.655 | [6 empty] | 29.84 | 7.5 | 12.5
2009-10-20 | 6.41 | 5.09 | [5 empty] | 1.63 |  |  |  |  | 25 |  |  |  | 0 | 0.6465 |  |  | 0.1055 | 0.2085 | [5 empty] | 27 |  |  |  |  | 54.05 |  | 23.1 |  | 4.95 | 0.0335 |  | 11.45 | 71.045 | 0.965 |  |  |  |  | 13.1595 | 12.029 | [6 empty] | 29.475 | 7.5 | 12.75
2009-10-21 | 6.36 | 5.03 | [5 empty] | 1.8 |  |  |  |  | 20 |  |  |  | 0 | 0.62 |  |  | 0.094 | 0.273 | [5 empty] | 25.1 |  |  |  |  | 50.3 |  | 24.1 |  | 4.5 | 0 |  | 12 | 74.94 | 0.94 |  |  |  |  | 13.52 | 12.403 | [6 empty] | 29.11 | 7.5 | 13
2009-10-22 | 6.54 | 5.2 | [5 empty] | 1.84 |  |  |  |  | 22 |  |  |  | 0 | 2.261 |  |  | 0.062 | 0.354 | [5 empty] | 28.6 |  |  |  |  | 57.3 |  | 25 |  | 4.6 | 0.035 |  | 11.3 | 77.75 | 0.9 |  |  |  |  | 14.007 | 12.903 | [6 empty] | 29.57 | 7.5 | 13.3
2009-10-23 | 6.49 | 5.01 | [5 empty] | 1.77 |  |  |  |  | 20 |  |  |  | 0 | 1.927 |  |  | 0.109 | 0.337 | [5 empty] | 29 |  |  |  |  | 58.1 |  | 26.4 |  | 4.8 | 0.07 |  | 11.3 | 76.82 | 0.95 |  |  |  |  | 14.011 | 12.813 | [6 empty] | 29.88 | 7.5 | 13.3
2009-10-24 | 6.37 | 4.97 | [5 empty] | 1.69 |  |  |  |  | 21 |  |  |  | 0 | 1.384 |  |  | 0.099 | 0.421 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 24.5 |  | 5.1 | 0.064 |  | 11.3 | 75.63 | 1.05 |  |  |  |  | 13.618 | 12.521 | [6 empty] | 32.3 | 7.5 | 13.3
2009-10-25 | 6.43 | 4.99 | [5 empty] | 1.73 |  |  |  |  | 20.5 |  |  |  | 0 | 1.6555 |  |  | 0.104 | 0.379 | [5 empty] | 29.7 |  |  |  |  | 59.45 |  | 24.05 |  | 5.5 | 0.0795 |  | 11.3 | 76.225 | 1 |  |  |  |  | 13.374 | 12.0555 | [6 empty] | 31.09 | 7.5 | 13.3
2009-10-26 | 5.92 | 4.96 | [5 empty] | 1.66 |  |  |  |  | 40 |  |  |  | 0 | 1.554 |  |  | 0.137 | 0.459 | [5 empty] | 29.1 |  |  |  |  | 58.2 |  | 23.6 |  | 5.9 | 0.095 |  | 11.3 | 75.9275 | 1.025 |  |  |  |  | 13.13 | 11.59 | [6 empty] | 31.695 | 7.5 | 13.3
2009-10-27 | 6.175 | 4.975 | [5 empty] | 1.695 |  |  |  |  | 30.25 |  |  |  | 0 | 1.6048 |  |  | 0.1205 | 0.419 | [5 empty] | 29.4 |  |  |  |  | 58.825 |  | 22.35 |  | 5.8 | 0.0865 |  | 11.3 | 77.05 | 0.97 |  |  |  |  | 13.882 | 12.967 | [6 empty] | 31.3925 | 7.8 | 13.3
2009-10-28 | 6.24 | 5.16 | [5 empty] | 1.64 |  |  |  |  | 48 |  |  |  | 0 | 1.082 |  |  | 0.153 | 0.42 | [5 empty] | 29.3 |  |  |  |  | 58.7 |  | 21.1 |  | 5.7 | 0.078 |  | 9 | 79.38 | 1.36 |  |  |  |  | 14.56 | 12 | [6 empty] | 31.14 | 7.8 | 13.3
2009-10-29 | 6.2075 | 5.0675 | [5 empty] | 1.6675 |  |  |  |  | 39.125 |  |  |  | 0 | 1.3434 |  |  | 0.13675 | 0.4195 | [5 empty] | 29.35 |  |  |  |  | 58.7625 |  | 21.35 |  | 6.3 | 0.354 |  | 8.65 | 76.315 | 1.185 |  |  |  |  | 14.0345 | 11.9565 | [6 empty] | 30.06 | 7.8 | 12.8
2009-10-30 | 6.31 | 5.09 | [5 empty] | 1.78 |  |  |  |  | 34 |  |  |  | 0 | 1.654 |  |  | 0.068 | 0.211 | [5 empty] | 29.4 |  |  |  |  | 58.8 |  | 21.6 |  | 6.9 | 0.63 |  | 8.3 | 73.25 | 1.01 |  |  |  |  | 13.509 | 11.913 | [6 empty] | 28.98 | 7.8 | 12.3
2009-10-31 | 6.19 | 4.99 | [5 empty] | 1.73 |  |  |  |  | 32 |  |  |  | 0 | 1.48 |  |  | 0.091 | 0.215 | [5 empty] | 29.4 |  |  |  |  | 59.8 |  | 21.6 |  | 6.8 | 0.062 |  | 8.8 | 66.15 | 0.86 |  |  |  |  | 12.97 | 11.58 | [6 empty] | 29.16 | 7.8 | 12
2009-11-01 | 6.48 | 5.11 | [5 empty] | 1.76 |  |  |  |  | 36 |  |  |  | 0 | 1.399 |  |  | 0.077 | 0.252 | [5 empty] | 26.1 |  |  |  |  | 52.2 |  | 23.3 |  | 5.9 | 0.036 |  | 8.4 | 69.57 | 0.97 |  |  |  |  | 13.865 | 11.555 | [6 empty] | 29.34 | 7.8 | 12
2009-11-02 | 6.56 | 6.56 | [5 empty] | 1.65 |  |  |  |  | 34 |  |  |  | 0 | 1.298 |  |  | 0.084 | 0.222 | [5 empty] | 28.6 |  |  |  |  | 57.2 |  | 24.4 |  | 6.1 | 0.033 |  | 8.2 | 67.47 | 1.15 |  |  |  |  | 12.168 | 10.936 | [6 empty] | 28.87 | 7.8 | 12.4
2009-11-03 | 6.52 | 5.835 | [5 empty] | 1.705 |  |  |  |  | 35 |  |  |  | 0 | 1.3485 |  |  | 0.0805 | 0.237 | [5 empty] | 27.35 |  |  |  |  | 54.7 |  | 24.55 |  | 6.4 | 0.0395 |  | 8.05 | 68.77 | 1.16 |  |  |  |  | 12.6565 | 10.9915 | [6 empty] | 29.56 | 7.8 | 12.4
2009-11-04 | 6.36 | 5.08 | [5 empty] | 1.71 |  |  |  |  | 36 |  |  |  | 0 | 1.41 |  |  | 0.096 | 0.238 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 24.7 |  | 6.7 | 0.046 |  | 7.9 | 70.07 | 1.17 |  |  |  |  | 13.145 | 11.047 | [6 empty] | 30.25 | 7.8 | 12.4
2009-11-05 | 6.44 | 5.4575 | [5 empty] | 1.7075 |  |  |  |  | 35.5 |  |  |  | 0 | 1.3792 |  |  | 0.08825 | 0.2375 | [5 empty] | 27.075 |  |  |  |  | 54.15 |  | 24 |  | 6.55 | 0.049 |  | 7.65 | 70.115 | 1.09 |  |  |  |  | 15.5965 | 11.6375 | [6 empty] | 29.905 | 7.8 | 12.2
2009-11-06 | 6.6 | 5.03 | [5 empty] | 1.6 |  |  |  |  | 48 |  |  |  | 0 | 1.793 |  |  | 0.095 | 0.296 | [5 empty] | 29.8 |  |  |  |  | 59.6 |  | 23.3 |  | 6.4 | 0.052 |  | 7.4 | 70.16 | 1.01 |  |  |  |  | 18.048 | 12.228 | [6 empty] | 30.0775 | 7.8 | 12
2009-11-07 | 6.45 | 6.45 | [5 empty] | 1.63 |  |  |  |  | 44 |  |  |  | 0 | 1.641 |  |  | 0.146 | 0.334 | [5 empty] | 27.2 |  |  |  |  | 54.4 |  | 23.4 |  | 6.6 | 0.059 |  | 7.2 | 70.56 | 1.03 |  |  |  |  | 14.302 | 12.038 | [6 empty] | 29.9913 | 7.8 | 12
2009-11-08 | 6.39 | 4.97 | [5 empty] | 1.56 |  |  |  |  | 47 |  |  |  | 0 | 1.584 |  |  | 0.134 | 0.401 | [5 empty] | 28 |  |  |  |  | 56 |  | 23.7 |  | 6.8 | 0.067 |  | 7.2 | 70.255 | 1.25 |  |  |  |  | 12.95 | 11.334 | [6 empty] | 31.71 | 7.8 | 12.2
2009-11-09 | 6.24 | 4.99 | [5 empty] | 1.67 |  |  |  |  | 44 |  |  |  | 0 | 1.711 |  |  | 0.113 | 0.344 | [5 empty] | 27.7 |  |  |  |  | 55.4 |  | 22.3 |  | 5.1 | 0.092 |  | 7.1 | 68.36 | 1.04 |  |  |  |  | 12.52 | 11.45 | [6 empty] | 30.43 | 7.8 | 12
2009-11-10 | 6.315 | 4.98 | [5 empty] | 1.615 |  |  |  |  | 45.5 |  |  |  | 0 | 1.6475 |  |  | 0.1235 | 0.3725 | [5 empty] | 27.85 |  |  |  |  | 55.7 |  | 23 |  | 5.9 | 0.145 |  | 6.85 | 69.515 | 0.985 |  |  |  |  | 12.7225 | 11.6215 | [6 empty] | 29.3 | 7.8 | 11.8
2009-11-11 | 6.97 | 5.09 | [5 empty] | 1.79 |  |  |  |  | 65 |  |  |  | 0 | 2.47 |  |  | 0.0239 | 0.475 | [5 empty] | 29.3 |  |  |  |  | 58.7 |  | 23.7 |  | 6.7 | 0.198 |  | 6.6 | 70.67 | 0.93 |  |  |  |  | 12.925 | 11.793 | [6 empty] | 28.17 | 7.8 | 11.6
2009-11-12 | 6.31 | 5.09 | [5 empty] | 1.65 |  |  |  |  | 51 |  |  |  | 0 | 0.989 |  |  | 0.634 | 0.46 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 23.1 |  | 5.8 | 0.006 |  | 6.3 | 49.17 | 0.33 |  |  |  |  | 12.397 | 11.292 | [6 empty] | 32.86 | 7.8 | 11.4
2009-11-13 | 6.58 | 5.05 | [5 empty] | 1.56 |  |  |  |  | 47 |  |  |  | 0 | 0.789 |  |  | 0.199 | 0.534 | [5 empty] | 28.7 |  |  |  |  | 57.4 |  | 22.9 |  | 6.2 | 0.019 |  | 5.8 | 105.38 | 2.6 |  |  |  |  | 13.489 | 11.495 | [6 empty] | 32.87 | 7.8 | 11.8
2009-11-14 | 6.39 | 5.25 | [5 empty] | 1.57 |  |  |  |  | 43 |  |  |  | 0 | 0.687 |  |  | 0.098 | 0.29 | [5 empty] | 29.3 |  |  |  |  | 58.6 |  | 26.5 |  | 6 | 0.031 |  | 5.7 | 102.86 | 2.53 |  |  |  |  | 13.277 | 11.367 | [6 empty] | 33.06 | 7.8 | 11.8
2009-11-15 | 6.2 | 5.26 | [5 empty] | 1.58 |  |  |  |  | 45 |  |  |  | 0 | 0.845 |  |  | 0.071 | 0.412 | [5 empty] | 29.3 |  |  |  |  | 58.6 |  | 25.8 |  | 6.2 | 0.042 |  | 5.6 | 99.75 | 2.59 |  |  |  |  | 12.031 | 10.872 | [6 empty] | 31.23 | 7.8 | 11.8
2009-11-16 | 6.51 | 4.96 | [5 empty] | 1.62 |  |  |  |  | 44 |  |  |  | 0 | 0.918 |  |  | 0.087 | 0.394 | [5 empty] | 26.7 |  |  |  |  | 53.4 |  | 25.8 |  | 6.4 | 0.039 |  | 5.4 | 101.69 | 2.52 |  |  |  |  | 12.26 | 11.14 | [6 empty] | 32.37 | 8 | 11
2009-11-17 | 6.355 | 5.11 | [5 empty] | 1.6 |  |  |  |  | 44.5 |  |  |  | 0 | 0.8815 |  |  | 0.079 | 0.403 | [5 empty] | 28 |  |  |  |  | 56 |  | 25.3 |  | 5.65 | 0.04 |  | 4.9 | 108.05 | 2.62 |  |  |  |  | 12.849 | 11.825 | [6 empty] | 32.88 | 7.7 | 12.8
2009-11-18 | 6.01 | 5.08 | [5 empty] | 1.48 |  |  |  |  | 42 |  |  |  | 0 | 1.642 |  |  | 0.072 | 0.433 | [5 empty] | 25.3 |  |  |  |  | 50.7 |  | 24.8 |  | 4.9 | 0.041 |  | 4.4 | 105.7 | 2.83 |  |  |  |  | 12.543 | 11.146 | [6 empty] | 33.39 | 7.9 | 12.8
2009-11-19 | 6.14 | 5.03 | [5 empty] | 1.43 |  |  |  |  | 50 |  |  |  | 0 | 1.494 |  |  | 0.081 | 0.54 | [5 empty] | 26.4 |  |  |  |  | 52.8 |  | 23.9 |  | 5.1 | 0.054 |  | 5.3 | 109.17 | 2.69 |  |  |  |  | 13.173 | 12.019 | [6 empty] | 32.76 | 7.9 | 13
2009-11-20 | 6.21 | 5.03 | [5 empty] | 1.41 |  |  |  |  | 44 |  |  |  | 0 | 1.888 |  |  | 0.087 | 0.457 | [5 empty] | 28.5 |  |  |  |  | 57 |  | 24.6 |  | 6.1 | 0.051 |  | 4.2 | 108.55 | 2.81 |  |  |  |  | 12.807 | 11.669 | [6 empty] | 30.85 | 7.9 | 13.6
2009-11-21 | 6.02 | 5.14 | [5 empty] | 1.53 |  |  |  |  | 60 |  |  |  | 1 | 3.165 |  |  | 0.104 | 0.308 | [5 empty] | 30.7 |  |  |  |  | 61.4 |  | 25.4 |  | 6.9 | 0.048 |  | 3.6 | 99.23 | 2.35 |  |  |  |  | 12.76 | 11.62 | [6 empty] | 31.86 | 7.9 | 13.6
2009-11-22 | 6.44 | 5.1 | [5 empty] | 1.77 |  |  |  |  | 55 |  |  |  | 0 | 2.113 |  |  | 0.0955 | 0.617 | [5 empty] | 29.5 |  |  |  |  | 59 |  | 23.7 |  | 5.6 | 0.002 |  | 3.4 | 110.28 | 2.4 |  |  |  |  | 13.12 | 12 | [6 empty] | 32.86 | 7.9 | 13.4
2009-11-23 | 6.51 | 5.19 | [5 empty] | 2 |  |  |  |  | 49 |  |  |  | 0 | 1.791 |  |  | 0.704 | 0.114 | [5 empty] | 25.2 |  |  |  |  | 50.5 |  | 23.3 |  | 5.8 | 0.015 |  | 3.4 | 105.77 | 2.18 |  |  |  |  | 12.521 | 11.498 | [6 empty] | 32.39 | 7.9 | 13.4
2009-11-24 | 6.475 | 5.145 | [5 empty] | 1.885 |  |  |  |  | 52 |  |  |  | 0 | 1.952 |  |  | 0.39975 | 0.3655 | [5 empty] | 27.35 |  |  |  |  | 54.75 |  | 23.6 |  | 5.25 | 0.008 |  | 3.65 | 110.865 | 2.22 |  |  |  |  | 12.94 | 11.81 | [6 empty] | 31.78 | 7.9 | 13.4
2009-11-25 | 6.26 | 4.95 | [5 empty] | 2.01 |  |  |  |  | 51 |  |  |  | 0 | 1.597 |  |  | 0.375 | 0.1 | [5 empty] | 25.2 |  |  |  |  | 50.4 |  | 23.9 |  | 4.7 | 0.001 |  | 3.9 | 115.96 | 2.26 |  |  |  |  | 13.504 | 12.339 | [6 empty] | 31.17 | 7.9 | 13.4
2009-11-26 | 6.33 | 5.16 | [5 empty] | 1.93 |  |  |  |  | 59 |  |  |  | 0 | 1.508 |  |  | 0.087 | 0.379 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 25.1 |  | 5.6 | 0.071 |  | 3.8 | 104.94 | 2.07 |  |  |  |  | 13 | 11.91 | [6 empty] | 32.28 | 7.9 | 13
2009-11-27 | 6.08 | 5.05 | [5 empty] | 1.78 |  |  |  |  | 48 |  |  |  | 0 | 1.369 |  |  | 0.609 | 0.449 | [5 empty] | 29.1 |  |  |  |  | 58.3 |  | 22.2 |  | 6.1 | 0.052 |  | 3.6 | 109.85 | 2.38 |  |  |  |  | 13.083 | 11.985 | [6 empty] | 31.22 | 7.9 | 12.9
2009-11-28 | 5.98 | 5.05 | [5 empty] | 1.77 |  |  |  |  | 47 |  |  |  | 0 | 1.301 |  |  | 0.583 | 0.464 | [5 empty] | 29.6 |  |  |  |  | 59.2 |  | 23.6 |  | 5.9 | 0.01 |  | 3.5 | 102.2 | 2.32 |  |  |  |  | 12.552 | 11.323 | [6 empty] | 31.69 | 7.9 | 13
2009-11-29 | 5.94 | 5.1 | [5 empty] | 1.8 |  |  |  |  | 52 |  |  |  | 0 | 1.392 |  |  | 0.082 | 0.561 | [5 empty] | 30.2 |  |  |  |  | 60.4 |  | 24 |  | 6.2 | 0.009 |  | 3.5 | 108.31 | 2.34 |  |  |  |  | 12.975 | 11.874 | [6 empty] | 30.09 | 7.9 | 13
2009-11-30 | 6.04 | 5.1 | [5 empty] | 1.8 |  |  |  |  | 50 |  |  |  | 0 | 1.299 |  |  | 0.101 | 0.314 | [5 empty] | 29.7 |  |  |  |  | 59.4 |  | 22.9 |  | 6.4 | 0.077 |  | 3.4 | 103.64 | 2.4 |  |  |  |  | 12.33 | 11.19 | [6 empty] | 32.08 | 7.9 | 13
2009-12-01 | 5.99 | 5.1 | [5 empty] | 1.8 |  |  |  |  | 51 |  |  |  | 0 | 1.3455 |  |  | 0.0915 | 0.4375 | [5 empty] | 29.95 |  |  |  |  | 59.9 |  | 22.1 |  | 6.4 | 0.069 |  | 3.4 | 105.825 | 2.39 |  |  |  |  | 12.7635 | 11.5985 | [6 empty] | 31.765 | 7.9 | 13
2009-12-02 | 6.41 | 5.12 | [5 empty] | 1.86 |  |  |  |  | 57 |  |  |  | 0 | 1.177 |  |  | 0.185 | 0.761 | [5 empty] | 29.3 |  |  |  |  | 58.6 |  | 21.3 |  | 6.4 | 0.061 |  | 3.4 | 108.01 | 2.38 |  |  |  |  | 13.55 | 11.56 | [6 empty] | 31.45 | 7.9 | 13
2009-12-03 | 6.12 | 5.12 | [5 empty] | 1.88 |  |  |  |  | 44 |  |  |  | 0 | 1.034 |  |  | 0.096 | 0.39 | [5 empty] | 29.7 |  |  |  |  | 59.5 |  | 21.1 |  | 8.4 | 0.05 |  | 3.4 | 106.9175 | 2.385 |  |  |  |  | 13.366 | 11.254 | [6 empty] | 31.22 | 7.9 | 13
2009-12-04 | 6.14 | 5.29 | [5 empty] | 1.94 |  |  |  |  | 41 |  |  |  | 0 | 0.976 |  |  | 0.084 | 0.297 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 22.5 |  | 7.9 | 0.049 |  | 3.3 | 107.4638 | 2.3825 |  |  |  |  | 12.843 | 11.713 | [6 empty] | 31.93 | 7.9 | 13
2009-12-05 | 6.1 | 5.25 | [5 empty] | 1.88 |  |  |  |  | 52 |  |  |  | 0 | 0.877 |  |  | 0.094 | 0.387 | [5 empty] | 27.9 |  |  |  |  | 55.8 |  | 21.7 |  | 6.9 | 0.099 |  | 3.5 | 107.1906 | 2.3838 |  |  |  |  | 14.104 | 12.882 | [6 empty] | 30.42 | 7.9 | 13
2009-12-06 | 6.21 | 5.26 | [5 empty] | 1.88 |  |  |  |  | 50 |  |  |  | 0 | 0.929 |  |  | 0.087 | 0.294 | [5 empty] | 27.1 |  |  |  |  | 54.2 |  | 22 |  | 7 | 0.074 |  | 3.6 | 107.3272 | 2.3831 |  |  |  |  | 12.79 | 11.687 | [6 empty] | 31.01 | 7.9 | 13
2009-12-07 | 6.19 | 5.17 | [5 empty] | 1.92 |  |  |  |  | 52 |  |  |  | 0 | 0.757 |  |  | 0.058 | 0.197 | [5 empty] | 30.2 |  |  |  |  | 60.4 |  | 23.9 |  | 6.8 | 0.063 |  | 3.7 | 107.2589 | 2.3834 |  |  |  |  | 12.9 | 11.76 | [6 empty] | 31.71 | 7.9 | 13
2009-12-08 | 6.2 | 5.215 | [5 empty] | 1.9 |  |  |  |  | 51 |  |  |  | 0 | 0.843 |  |  | 0.0725 | 0.2455 | [5 empty] | 28.65 |  |  |  |  | 57.3 |  | 23.4 |  | 6.9 | 0.07 |  | 3.65 | 71.3 | 0.8 |  |  |  |  | 13.097 | 11.899 | [6 empty] | 31.73 | 7.9 | 12.8
2009-12-09 | 6.11 | 5.07 | [5 empty] | 2.01 |  |  |  |  | 53 |  |  |  | 0 | 0.937 |  |  | 0.063 | 0.174 | [5 empty] | 29.9 |  |  |  |  | 59.9 |  | 22.9 |  | 7 | 0.077 |  | 3.6 | 81.65 | 1.06 |  |  |  |  | 14.067 | 12.072 | [6 empty] | 31.75 | 7.9 | 12.8
2009-12-10 | 5.99 | 5.07 | [5 empty] | 2.06 |  |  |  |  | 50 |  |  |  | 0 | 0.879 |  |  | 0.194 | 0.173 | [5 empty] | 30.5 |  |  |  |  | 61 |  | 23.5 |  | 5.4 | 0.104 |  | 3.7 | 72.77 | 0.5 |  |  |  |  | 13.06 | 12.88 | [6 empty] | 31.1 | 7.9 | 12.8
2009-12-11 | 6.05 | 5.07 | [5 empty] | 2.035 |  |  |  |  | 51.5 |  |  |  | 0 | 0.908 |  |  | 0.1285 | 0.1735 | [5 empty] | 30.2 |  |  |  |  | 60.45 |  | 23.2 |  | 6.1 | 0.0835 |  | 3.8 | 73.87 | 0.565 |  |  |  |  | 13.582 | 11.9855 | [6 empty] | 31.015 | 7.9 | 12.8
2009-12-12 | 6.34 | 5.07 | [5 empty] | 2.02 |  |  |  |  | 51 |  |  |  | 0 | 0.851 |  |  | 0.097 | 0.203 | [5 empty] | 31.1 |  |  |  |  | 62.2 |  | 23.9 |  | 6.8 | 0.063 |  | 3.9 | 74.97 | 0.63 |  |  |  |  | 14.03 | 12.82 | [6 empty] | 30.93 | 7.9 | 12.8
2009-12-13 | 5.95 | 5.15 | [5 empty] | 1.98 |  |  |  |  | 46 |  |  |  | 0 | 0.846 |  |  | 0.096 | 0.394 | [5 empty] | 39.7 |  |  |  |  | 79.6 |  | 21.5 |  | 6.3 | 0.057 |  | 3.8 | 77 | 0.86 |  |  |  |  | 13.436 | 12.322 | [6 empty] | 30.98 | 7.9 | 12.4
2009-12-14 | 5.93 | 5.1 | [5 empty] | 1.71 |  |  |  |  | 44 |  |  |  | 0 | 0.787 |  |  | 0.234 | 0.368 | [5 empty] | 46.7 |  |  |  |  | 93.5 |  | 24.5 |  | 6.5 | 0.071 |  | 3.8 | 51.33 | 0.17 |  |  |  |  | 13.5 | 12.39 | [6 empty] | 29.1 | 7.9 | 12.4
2009-12-15 | 5.94 | 5.125 | [5 empty] | 1.845 |  |  |  |  | 45 |  |  |  | 0 | 0.8165 |  |  | 0.165 | 0.381 | [5 empty] | 43.2 |  |  |  |  | 86.55 |  | 24.3 |  | 5.95 | 0.0695 |  | 3.85 | 57.725 | 0.485 |  |  |  |  | 13.733 | 12.571 | [6 empty] | 29.145 | 7.9 | 12.4
2009-12-16 | 6.2 | 5.06 | [5 empty] | 1.61 |  |  |  |  | 46 |  |  |  | 0 | 0.723 |  |  | 0.114 | 0.65 | [5 empty] | 34.3 |  |  |  |  | 68.6 |  | 24.1 |  | 5.4 | 0.068 |  | 3.9 | 64.12 | 0.8 |  |  |  |  | 14.154 | 12.075 | [6 empty] | 29.19 | 7.9 | 12.4
2009-12-17 | 5.97 | 5.21 | [5 empty] | 1.68 |  |  |  |  | 54 |  |  |  | 1 | 0.726 |  |  | 0.273 | 0.878 | [5 empty] | 35.4 |  |  |  |  | 70.8 |  | 24.4 |  | 6 | 0.089 |  | 3.8 | 57.33 | 0.39 |  |  |  |  | 12.76 | 12.56 | [6 empty] | 30.32 | 7.9 | 12.8
2009-12-18 | 6.08 | 5.03 | [5 empty] | 1.58 |  |  |  |  | 45 |  |  |  | 0 | 0.758 |  |  | 0.105 | 1.123 | [5 empty] | 39.2 |  |  |  |  | 78.5 |  | 22.7 |  | 6.2 | 0.072 |  | 3.9 | 55.87 | 0.63 |  |  |  |  | 12.56 | 11.49 | [6 empty] | 31.45 | 8.1 | 13.4
2009-12-19 | 6.14 | 5.32 | [5 empty] | 1.79 |  |  |  |  | 45 |  |  |  | 0 | 0.689 |  |  | 0.111 | 0.545 | [5 empty] | 39.6 |  |  |  |  | 79.2 |  | 24.4 |  | 6.9 | 0.201 |  | 3.8 | 53.25 | 0.36 |  |  |  |  | 12.427 | 11.243 | [6 empty] | 31.92 | 8.1 | 11.5
2009-12-20 | 6.19 | 5.12 | [5 empty] | 1.86 |  |  |  |  | 44 |  |  |  | 0 | 0.744 |  |  | 0.166 | 0.939 | [5 empty] | 37.1 |  |  |  |  | 74.2 |  | 23.2 |  | 3.7 | 0.072 |  | 3.7 | 53.89 | 0.27 |  |  |  |  | 12.662 | 11.444 | [6 empty] | 31.92 | 6.8 | 8.8
2009-12-21 | 6.14 | 5.12 | [5 empty] | 1.88 |  |  |  |  | 46 |  |  |  | 0 | 0.757 |  |  | 0.079 | 0.155 | [5 empty] | 35.6 |  |  |  |  | 71.2 |  | 24.4 |  | 6.4 | 0.084 |  | 3.7 | 55.13 | 0.29 |  |  |  |  | 12.61 | 11.52 | [6 empty] | 30.77 | 6.8 | 7.8
2009-12-22 | 6.165 | 5.12 | [5 empty] | 1.87 |  |  |  |  | 45 |  |  |  | 0 | 0.7505 |  |  | 0.1225 | 0.547 | [5 empty] | 36.35 |  |  |  |  | 72.7 |  | 23.75 |  | 5.4 | 0.0455 |  | 3.65 | 56.98 | 0.385 |  |  |  |  | 12.5445 | 11.3435 | [6 empty] | 31.345 | 6.8 | 7.8
2009-12-23 | 6.46 | 4.94 | [5 empty] | 1.79 |  |  |  |  | 43 |  |  |  | 0 | 0.775 |  |  | 0.454 | 0.837 | [5 empty] | 40.6 |  |  |  |  | 81.2 |  | 23.1 |  | 4.4 | 0.007 |  | 3.6 | 58.83 | 0.48 |  |  |  |  | 14.856 | 11.257 | [6 empty] | 31.92 | 6.8 | 7.8
2009-12-24 | 6.11 | 5.2 | [5 empty] | 1.95 |  |  |  |  | 44 |  |  |  | 0 | 0.761 |  |  | 0.113 | 0.519 | [5 empty] | 34.1 |  |  |  |  | 68.3 |  | 24.3 |  | 5.2 | 0.092 |  | 3.8 | 57.83 | 0.3 |  |  |  |  | 14.745 | 11.645 | [6 empty] | 31.45 | 6.4 | 7.6
2009-12-25 | 6.09 | 5.41 | [5 empty] | 1.85 |  |  |  |  | 43 |  |  |  | 0 | 0.691 |  |  | 0.098 | 0.167 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 21.8 |  | 6 | 0.063 |  | 3.7 | 54.93 | 0.31 |  |  |  |  | 15.94 | 11.52 | [6 empty] | 30.67 | 6.2 | 7.4
2009-12-26 | 6.1 | 5.305 | [5 empty] | 1.9 |  |  |  |  | 43.5 |  |  |  | 0 | 0.726 |  |  | 0.1055 | 0.343 | [5 empty] | 32.25 |  |  |  |  | 64.55 |  | 22.6 |  | 6.35 | 0.0575 |  | 3.65 | 52.45 | 0.305 |  |  |  |  | 14.8005 | 11.451 | [6 empty] | 30.94 | 6.1 | 7.4
2009-12-27 | 6.22 | 5.42 | [5 empty] | 1.84 |  |  |  |  | 52 |  |  |  | 0 | 0.656 |  |  | 0.081 | 1.124 | [5 empty] | 32.1 |  |  |  |  | 74.2 |  | 23.4 |  | 6.7 | 0.052 |  | 3.6 | 49.97 | 0.3 |  |  |  |  | 14.947 | 10.589 | [6 empty] | 31.21 | 6 | 7.4
2009-12-28 | 6.03 | 5.61 | [5 empty] | 1.85 |  |  |  |  | 50 |  |  |  | 0 | 0.627 |  |  | 0.091 | 1.134 | [5 empty] | 35.1 |  |  |  |  | 70.2 |  | 24.4 |  | 6.2 | 0.068 |  | 3.6 | 55.41 | 0.32 |  |  |  |  | 15.932 | 11.595 | [6 empty] | 30.94 | 6 | 7.2
2009-12-29 | 6.125 | 5.515 | [5 empty] | 1.845 |  |  |  |  | 51 |  |  |  | 0 | 0.6415 |  |  | 0.086 | 1.129 | [5 empty] | 33.6 |  |  |  |  | 72.2 |  | 23.4 |  | 6.1 | 0.0825 |  | 3.65 | 50.12 | 0.27 |  |  |  |  | 15.135 | 10.672 | [6 empty] | 30.655 | 6 | 7
2009-12-30 | 6.01 | 5.35 | [5 empty] | 1.82 |  |  |  |  | 45 |  |  |  | 0 | 0.594 |  |  | 0.134 | 1.04 | [5 empty] | 28.3 |  |  |  |  | 56.6 |  | 22.4 |  | 6 | 0.097 |  | 3.7 | 59.16 | 0.34 |  |  |  |  | 16.849 | 12.459 | [6 empty] | 30.37 | 6 | 7
2009-12-31 | 6.11 | 5.09 | [5 empty] | 1.73 |  |  |  |  | 41 |  |  |  | 0 | 0.624 |  |  | 0.412 | 0.867 | [5 empty] | 29.9 |  |  |  |  | 59.8 |  | 24.9 |  | 4.7 | 0.091 |  | 3.6 | 51.82 | 0.44 |  |  |  |  | 15.189 | 10.822 | [6 empty] | 30.26 | 6 | 7
| 5.82 | 5.19 | [5 empty] | 1.79 |  |  |  |  | 40 |  |  |  | 0 | 0.613 |  |  | 0.124 | 0.829 | [5 empty] | 32.9 |  |  |  |  | 65.8 |  | 23.8 |  | 5.9 | 0.074 |  | 3.6 | 55.74 | 0.35 |  |  |  |  | 16.166 | 11.801 | [6 empty] | 30.52 | 6 | 7

## 2015
All of the data presented below was copied verbatim from spreadsheets transcribed by Debbie Rideout, Town PLO
| pH | [6 empty] | Chlorine |  |  |  | Colour | [5 empty] | Turbidity | [5 empty] | Total Dissolved Solids |  |  |  |  | Conductivity |  |  |  |  | Hardness |  | Alkalinity |  | Aluminum | Temperature |  | Cl Used | Cl Demand | UVT |  | UVA |  | Flows within plant |  |  |  | Flows from plant |  |  | Chemical Dosages |  |  |  | Dennis Penney
Date | Raw | PTC | PTC (OL) | SWC | Filter | Finish (OL) | Finish | Free | Total | Sample | Analyzer | Raw A | Raw T | SWC A | Filter A | Finish A | Finish T | Raw | Raw (OL) | SWC | Filter | Finish | Finish (OL) | Raw | PTC | SWC | Filter | Finish | Raw | PTC | SWC | Filter | Finish | Raw | Finish | Raw | Finish | Finish (Free) | Raw | Finish |  |  | Raw | Filter | Raw | Filter | Raw | Finish | Filter | Backwash | Bishop's | Botwood | GFW | Chlorine | Alum | Lime (Pre) | Lime (Post) | Jerry Loveless
2009-01-01 | 5.78 | 5.55 |  |  |  |  | 7.3 | 1.83 |  |  |  |  | 43 |  |  |  | 0 | 0.643 |  |  | 0.133 | 0.176 | [5 empty] | 30 |  |  |  |  | 60 |  | 24.1 |  | 6.2 | 0.063 |  | 3.5 | 52.92 | 0.31 |  |  |  |  | 15.48 | 11.21 | [6 empty] | 26.92 | 6 | 7.2 | Noland Simms
2009-01-02 | 6.5 | 5.28 |  |  |  |  | 7.28 | 1.78 |  |  |  |  | 39 |  |  |  | 0 | 0.6 |  |  | 0.397 | 0.311 | [5 empty] | 31.5 |  |  |  |  | 63 |  | 27.9 |  | 4.8 | 0.052 |  | 3.7 | 52.92 | 0.19 |  |  |  |  | 15.7 | 12.21 | [6 empty] | 28.17 | 6 | 7.2
2009-01-03 | 6.14 | 5.415 |  |  |  |  | 7.29 | 1.805 |  |  |  |  | 41 |  |  |  | 0 | 0.6215 |  |  | 0.265 | 0.2435 | [5 empty] | 30.75 |  |  |  |  | 61.5 |  | 26 |  | 5.5 | 0.0575 |  | 3.6 | 52.92 | 0.25 |  |  |  |  | 15.58 | 11.24 | [6 empty] | 27.545 | 6 | 7.2
2009-01-04 | 6.32 | 5.3475 |  |  |  |  | 7.285 | 1.7925 |  |  |  |  | 40 |  |  |  | 0 | 0.61075 |  |  | 0.331 | 0.27725 | [5 empty] | 31.125 |  |  |  |  | 62.25 |  | 26.95 |  | 5.15 | 0.05475 |  | 3.65 | 52.92 | 0.22 |  |  |  |  | 15.64 | 11.725 | [6 empty] | 27.8575 | 6 | 7.2 | Continuous
2009-01-05 | 6.02 | 4.76 |  |  |  |  | 6.76 | 1.63 |  |  |  |  | 40 |  |  |  | 0 | 0.609 |  |  | 0.264 | 0.561 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 25.7 |  | 6.7 | 0.071 |  | 3.7 | 67.56 | 0.82 |  |  |  |  | 16.838 | 12.516 | [6 empty] | 27.7013 | 5.7 | 7.2 | Grab
2009-01-06 | 6.08 | 5.55 |  |  |  |  | 7.64 | 1.72 |  |  |  |  | 40 |  |  |  | 0 | 0.598 |  |  | 0.103 | 0.118 | [5 empty] | 29.6 |  |  |  |  | 59.2 |  | 24.5 |  | 6.8 | 0.063 |  | 4 | 70.56 | 0.88 |  |  |  |  | 16.6 | 12.31 | [6 empty] | 27.08 | 5.7 | 7.2 | ^ Stuff for form dropdown menus
2009-01-07 | 6 | 5.09 |  |  |  |  | 7.07 | 1.71 |  |  |  |  | 39 |  |  |  | 0 | 0.583 |  |  | 0.162 | 0.723 | [5 empty] | 33 |  |  |  |  | 66 |  | 23.7 |  | 6.7 | 0.056 |  | 3.8 | 71.39 | 0.9 |  |  |  |  | 16.697 | 12.42 | [6 empty] | 26.76 | 5.7 | 7.4
2009-01-08 | 6.05 | 5.26 |  |  |  |  | 7.41 | 1.7 |  |  |  |  | 38 |  |  |  | 0 | 0.554 |  |  | 0.25 | 0.255 | [5 empty] | 30.5 |  |  |  |  | 61.1 |  | 26.1 |  | 9.1 | 0.087 |  | 3.7 | 77.35 | 0.98 |  |  |  |  | 17.343 | 13.104 | [6 empty] | 26.29 | 5.5 | 7.4
2009-01-09 | 6.11 | 5.23 |  |  |  |  | 7.07 | 1.71 |  |  |  |  | 35 |  |  |  | 0 | 0.504 |  |  | 0.097 | 0.331 | [5 empty] | 31.1 |  |  |  |  | 62.2 |  | 26 |  | 8.4 | 0.08 |  | 3.6 | 73.34 | 0.92 |  |  |  |  | 16.98 | 12.659 | [6 empty] | 28.06 | 5.5 | 7.4
2009-01-10 | 6.04 | 5.21 |  |  |  |  | 6.95 | 1.73 |  |  |  |  | 40 |  |  |  | 0 | 0.483 |  |  | 0.081 | 0.293 | [5 empty] | 33.7 |  |  |  |  | 67.4 |  | 24.6 |  | 7.4 | 0.071 |  | 3.8 | 72.77 | 0.88 |  |  |  |  | 16.99 | 12.67 | [6 empty] | 27.77 | 5.5 | 7.4
2009-01-11 | 6.195 | 5.195 |  |  |  |  | 6.955 | 1.725 |  |  |  |  | 39 |  |  |  | 0 | 0.472 |  |  | 0.1105 | 0.312 | [5 empty] | 32.6 |  |  |  |  | 65.3 |  | 24.5 |  | 6.95 | 0.0625 |  | 3.65 | 72.45 | 0.94 |  |  |  |  | 16.985 | 12.6645 | [6 empty] | 28.67 | 5.5 | 7.4
2009-01-12 | 6.35 | 5.18 |  |  |  |  | 6.96 | 1.72 |  |  |  |  | 38 |  |  |  | 0 | 0.461 |  |  | 0.14 | 0.805 | [5 empty] | 31.5 |  |  |  |  | 63.2 |  | 24.4 |  | 6.5 | 0.054 |  | 3.5 | 72.13 | 1 |  |  |  |  | 16.594 | 12.037 | [6 empty] | 29.57 | 5.5 | 7.4
2009-01-13 | 5.85 | 5.46 |  |  |  |  | 7.11 | 1.73 |  |  |  |  | 37 |  |  |  | 0 | 0.4777 |  |  | 0.199 | 0.753 | [5 empty] | 33.3 |  |  |  |  | 66.7 |  | 26.6 |  | 10 | 0.035 |  | 3.5 | 71.11 | 0.9 |  |  |  |  | 16.677 | 12.27 | [6 empty] | 28.87 | 5.1 | 7.4
2009-01-14 | 5.96 | 5.3 |  |  |  |  | 7.18 | 1.73 |  |  |  |  | 40 |  |  |  | 0 | 0.461 |  |  | 0.094 | 0.479 | [5 empty] | 32.8 |  |  |  |  | 65.6 |  | 25.7 |  | 9.1 | 0.047 |  | 3.4 | 73.12 | 0.95 |  |  |  |  | 16.752 | 12.391 | [6 empty] | 28.51 | 4.5 | 7.4
2009-01-15 | 5.94 | 5.22 |  |  |  |  | 6.9 | 1.73 |  |  |  |  | 36 |  |  |  | 0 | 0.437 |  |  | 0.071 | 0.238 | [5 empty] | 33.6 |  |  |  |  | 67.2 |  | 26.1 |  | 9.2 | 0.067 |  | 3.4 | 72.46 | 0.92 |  |  |  |  | 16.728 | 12.406 | [6 empty] | 28.05 | 4.3 | 7.4
2009-01-16 | 6.11 | 5.2 |  |  |  |  | 6.82 | 1.73 |  |  |  |  | 38 |  |  |  | 0 | 0.432 |  |  | 0.079 | 0.299 | [5 empty] | 29.35 |  |  |  |  | 58.7 |  | 25.85 |  | 7.65 | 0.07 |  | 3.75 | 70.75 | 0.87 |  |  |  |  | 16.695 | 12.356 | [6 empty] | 28.12 | 4.3 | 7.4
2009-01-17 | 6.09 | 5.31 |  |  |  |  | 5.27 | 1.72 |  |  |  |  | 38 |  |  |  | 0 | 0.427 |  |  | 0.087 | 0.247 | [5 empty] | 25.1 |  |  |  |  | 50.2 |  | 25.6 |  | 6.1 | 0.073 |  | 4.1 | 69.04 | 0.82 |  |  |  |  | 16.68 | 12.34 | [6 empty] | 28.19 | 4.3 | 7.4
2009-01-18 | 6.05 | 5.145 |  |  |  |  | 6.295 | 1.72 |  |  |  |  | 37.5 |  |  |  | 0 | 0.42 |  |  | 0.075 | 0.333 | [5 empty] | 26.65 |  |  |  |  | 53.3 |  | 25.45 |  | 6.25 | 0.0765 |  | 4.1 | 71.66 | 1.02 |  |  |  |  | 16.373 | 11.888 | [6 empty] | 14.085 | 4.2 | 7.4
2009-01-19 | 6.01 | 4.98 |  |  |  |  | 7.32 | 1.71 |  |  |  |  | 37 |  |  |  | 0 | 0.413 |  |  | 0.063 | 0.419 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 25.3 |  | 6.4 | 0.08 |  | 4.1 | 77.88 | 1.16 |  |  |  |  | 17.539 | 14.293 | [6 empty] | 29.44 | 4.2 | 7.4
2009-01-20 | 6.11 | 5.45 |  |  |  |  | 7.62 | 1.61 |  |  |  |  | 41 |  |  |  | 0 | 0.427 |  |  | 0.063 | 0.344 | [5 empty] | 29 |  |  |  |  | 58 |  | 25.2 |  | 6.9 | 0.089 |  | 4.1 | 67.47 | 0.85 |  |  |  |  | 16.584 | 12.186 | [6 empty] | 28.02 | 4.2 | 7.4
2009-01-21 | 6.17 | 5.34 |  |  |  |  | 6.67 | 1.58 |  |  |  |  | 42 |  |  |  | 0 | 0.43 |  |  | 0.086 | 0.396 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 24.9 |  | 6.6 | 0.073 |  | 3.7 | 72.03 | 1.01 |  |  |  |  | 16.994 | 12.615 | [6 empty] | 28.73 | 4.1 | 7.9
2009-01-22 | 6.14 | 5.3 |  |  |  |  | 7.73 | 1.54 |  |  |  |  | 37 |  |  |  | 0 | 0.412 |  |  | 0.074 | 0.476 | [5 empty] | 29.14 |  |  |  |  | 58 |  | 25.1 |  | 6.5 | 0.0805 |  | 3.6 | 69.09 | 1.01 |  |  |  |  | 16.46 | 12.09 | [6 empty] | 28.375 | 4.1 | 7.9
2009-01-23 | 6.13 | 5.25 |  |  |  |  | 7.49 | 1.48 |  |  |  |  | 36 |  |  |  | 0 | 0.401 |  |  | 0.107 | 0.506 | [5 empty] | 30.4 |  |  |  |  | 60.9 |  | 25.3 |  | 6.4 | 0.088 |  | 3.5 | 66.15 | 1.01 |  |  |  |  | 16.455 | 12.061 | [6 empty] | 29.25 | 4.1 | 7.9
2009-01-24 | 6.1 | 5.34 |  |  |  |  | 7.17 | 1.8 |  |  |  |  | 34 |  |  |  | 0 | 0.399 |  |  | 0.128 | 0.442 | [5 empty] | 31.4 |  |  |  |  | 62.8 |  | 24.7 |  | 8.2 | 0.001 |  | 3.4 | 67.23 | 0.69 |  |  |  |  | 16.62 | 12.27 | [6 empty] | 30.04 | 4.1 | 8.2
2009-01-25 | 6.04 | 5.245 |  |  |  |  | 7.07 | 1.81 |  |  |  |  | 33 |  |  |  | 0.5 | 0.3875 |  |  | 0.11 | 0.5275 | [5 empty] | 31.3 |  |  |  |  | 62.6 |  | 24.8 |  | 7.55 | 0.021 |  | 3.45 | 68.86 | 0.745 |  |  |  |  | 17.291 | 12.194 | [6 empty] | 30.785 | 4.1 | 8.2
2009-01-26 | 5.98 | 5.15 |  |  |  |  | 6.97 | 1.82 |  |  |  |  | 32 |  |  |  | 1 | 0.376 |  |  | 0.092 | 0.613 | [5 empty] | 31.2 |  |  |  |  | 62.4 |  | 24.9 |  | 6.9 | 0.041 |  | 3.5 | 70.49 | 0.8 |  |  |  |  | 16.9555 | 12.232 | [6 empty] | 31.53 | 4.1 | 8.2
2009-01-27 | 6.18 | 5.29 |  |  |  |  | 6.82 | 1.84 |  |  |  |  | 33 |  |  |  | 0 | 0.389 |  |  | 0.092 | 6.82 | [5 empty] | 33.2 |  |  |  |  | 66.4 |  | 24.9 |  | 7 | 0.042 |  | 3.7 | 68.44 | 0.65 |  |  |  |  | 16.83 | 12.49 | [6 empty] | 30.12 | 4 | 8.6
2009-01-28 | 5.965 | 5.205 |  |  |  |  | 6.85 | 1.735 |  |  |  |  | 37 |  |  |  | 0 | 0.409 |  |  | 0.2815 | 3.817 | [5 empty] | 32.55 |  |  |  |  | 65.15 |  | 24.1 |  | 7.6 | 0.0255 |  | 3.7 | 66.07 | 0.755 |  |  |  |  | 16.246 | 11.947 | [6 empty] | 29.845 | 4 | 8.65
2009-01-29 | 5.75 | 5.12 |  |  |  |  | 6.88 | 1.63 |  |  |  |  | 41 |  |  |  | 0 | 0.429 |  |  | 0.471 | 0.814 | [5 empty] | 31.9 |  |  |  |  | 63.9 |  | 23.3 |  | 8.2 | 0.009 |  | 3.7 | 63.7 | 0.86 |  |  |  |  | 15.94 | 11.625 | [6 empty] | 29.57 | 4 | 8.7
2009-01-30 | 5.86 | 5.1 |  |  |  |  | 6.97 | 1.76 |  |  |  |  | 31 |  |  |  | 0 | 0.454 |  |  | 0.113 | 0.661 | [5 empty] | 30.9 |  |  |  |  | 61.8 |  | 24.1 |  | 7.7 | 0.087 |  | 3.6 | 66.5 | 0.75 |  |  |  |  | 16.287 | 12.031 | [6 empty] | 28.52 | 4 | 8.7
2009-01-31 | 5.66 | 5.15 |  |  |  |  | 7.07 | 1.69 |  |  |  |  | 34 |  |  |  | 0 | 0.437 |  |  | 0.124 | 0.649 | [5 empty] | 31 |  |  |  |  | 62 |  | 26.9 |  | 5.9 | 0.093 |  | 3.6 | 70.56 | 0.95 |  |  |  |  | 16.71 | 12.12 | [6 empty] | 28.65 | 4 | 8.7
2009-02-01 | 5.77 | 5.145 |  |  |  |  | 6.995 | 1.595 |  |  |  |  | 35.5 |  |  |  | 0 | 0.4365 |  |  | 0.496 | 0.8485 | [5 empty] | 30.65 |  |  |  |  | 61.3 |  | 25.1 |  | 7.35 | 0.087 |  | 3.55 | 60.79 | 0.575 |  |  |  |  | 16.4985 | 12.0755 | [6 empty] | 30.05 | 4 | 8.7
2009-02-02 | 5.88 | 5.14 |  |  |  |  | 6.92 | 1.5 |  |  |  |  | 37 |  |  |  | 0 | 0.436 |  |  | 0.868 | 1.048 | [5 empty] | 30.3 |  |  |  |  | 60.6 |  | 23.3 |  | 8.8 | 0.081 |  | 3.5 | 51.02 | 0.2 |  |  |  |  | 17.809 | 13.611 | [6 empty] | 31.45 | 4 | 8.7
2009-02-03 | 6.06 | 5.27 |  |  |  |  | 6.82 | 1.54 |  |  |  |  | 38 |  |  |  | 0 | 0.429 |  |  | 0.176 | 0.909 | [5 empty] | 31 |  |  |  |  | 62 |  | 25.3 |  | 8.2 | 0.008 |  | 3.6 | 69.7 | 0.85 |  |  |  |  | 19.093 | 12.09 | [6 empty] | 28.17 | 4 | 8.7
2009-02-04 | 6.14 | 5.23 |  |  |  |  | 6.97 | 1.72 |  |  |  |  | 35 |  |  |  | 0 | 0.437 |  |  | 0.092 | 0.561 | [5 empty] | 32.1 |  |  |  |  | 64.2 |  | 25.1 |  | 7.7 | 0.01 |  | 3.5 | 62.09 | 0.55 |  |  |  |  | 14.738 | 12.434 | [6 empty] | 30.01 | 4 | 8.7
2009-02-05 | 6.07 | 6.07 |  |  |  |  | 6.91 | 1.67 |  |  |  |  | 38 |  |  |  | 0 | 0.417 |  |  | 0.074 | 0.496 | [5 empty] | 33.3 |  |  |  |  | 66.7 |  | 24.9 |  | 6.2 | 0.054 |  | 3.6 | 59.16 | 0.63 |  |  |  |  | 12.772 | 11.601 | [6 empty] | 29.53 | 4 | 8.7
2009-02-06 | 6.16 | 6.16 |  |  |  |  | 6.64 | 1.68 |  |  |  |  | 40 |  |  |  | 0 | 0.412 |  |  | 0.081 | 0.492 | [5 empty] | 30.5 |  |  |  |  | 61 |  | 24.5 |  | 6.4 | 0.049 |  | 3.7 | 66.92 | 0.71 |  |  |  |  | 13.915 | 12.719 | [6 empty] | 29.24 | 4 | 8.7
2009-02-07 | 6.01 | 6.01 |  |  |  |  | 6.24 | 1.65 |  |  |  |  | 41 |  |  |  | 0 | 0.479 |  |  | 0.074 | 0.604 | [5 empty] | 30.9 |  |  |  |  | 61.8 |  | 25.1 |  | 6 | 0.063 |  | 3.8 | 66.11 | 0.81 |  |  |  |  | 13.41 | 12.2 | [6 empty] | 31.52 | 4 | 9.6
2009-02-08 | 6.04 | 5.55 |  |  |  |  | 7.005 | 1.65 |  |  |  |  | 42.5 |  |  |  | 0 | 0.48 |  |  | 0.0775 | 0.6325 | [5 empty] | 31.15 |  |  |  |  | 62.3 |  | 25.3 |  | 5.95 | 0.0675 |  | 3.75 | 66.955 | 0.85 |  |  |  |  | 13.6625 | 12.4595 | [6 empty] | 30.565 | 4 | 10.1
2009-02-09 | 6.07 | 5.09 |  |  |  |  | 7.77 | 1.65 |  |  |  |  | 44 |  |  |  | 0 | 0.481 |  |  | 0.081 | 0.661 | [5 empty] | 31.4 |  |  |  |  | 62.8 |  | 25.5 |  | 5.9 | 0.072 |  | 3.7 | 67.8 | 0.89 |  |  |  |  | 13.323 | 12.138 | [6 empty] | 29.61 | 4 | 10.6
2009-02-10 | 6.055 | 5.32 |  |  |  |  | 7.3875 | 1.65 |  |  |  |  | 43.25 |  |  |  | 0 | 0.4805 |  |  | 0.07925 | 0.64675 | [5 empty] | 31.275 |  |  |  |  | 62.55 |  | 25.4 |  | 5.925 | 0.06975 |  | 3.725 | 67.3775 | 0.87 |  |  |  |  | 14.116 | 12.909 | [6 empty] | 30.0875 | 4 | 10.35
2009-02-11 | 6.0625 | 5.205 |  |  |  |  | 7.5787 | 1.65 |  |  |  |  | 43.625 |  |  |  | 0 | 0.48075 |  |  | 0.080125 | 0.65387 | [5 empty] | 31.3375 |  |  |  |  | 62.675 |  | 25.45 |  | 5.9125 | 0.070875 |  | 3.7125 | 67.5888 | 0.88 |  |  |  |  | 13.7195 | 12.5235 | [6 empty] | 29.8487 | 4 | 10.475
2009-02-12 | 5.98 | 5.04 |  |  |  |  | 7.69 | 1.62 |  |  |  |  | 41 |  |  |  | 0 | 0.468 |  |  | 0.642 | 7.69 | [5 empty] | 30 |  |  |  |  | 60 |  | 23.1 |  | 6.2 | 0.057 |  | 3.5 | 48.51 | 0.24 |  |  |  |  | 12.92 | 11.82 | [6 empty] | 28.64 | 4 | 10.6
2009-02-13 | 5.67 | 4.98 |  |  |  |  | 7.67 | 1.63 |  |  |  |  | 32 |  |  |  | 0 | 0.477 |  |  | 0.349 | 0.622 | [5 empty] | 30 |  |  |  |  | 60 |  | 21.9 |  | 6 | 0.072 |  | 3.4 | 61.74 | 0.64 |  |  |  |  | 12.53 | 12.33 | [6 empty] | 29.11 | 4 | 10.6
2009-02-14 | 5.74 | 5.2 |  |  |  |  | 7.77 | 1.65 |  |  |  |  | 32 |  |  |  | 0 | 0.438 |  |  | 0.328 | 0.463 | [5 empty] | 31.1 |  |  |  |  | 62 |  | 23.7 |  | 6.4 | 0.055 |  | 3.4 | 59.79 | 0.76 |  |  |  |  | 12.33 | 12.25 | [6 empty] | 28.87 | 4 | 10.6
2009-02-15 | 5.9 | 5.09 |  |  |  |  | 6.9 | 1.56 |  |  |  |  | 38 |  |  |  | 0 | 0.422 |  |  | 0.124 | 0.639 | [5 empty] | 32.3 |  |  |  |  | 64.6 |  | 22.7 |  | 6 | 0.066 |  | 3.3 | 52.3 | 0.52 |  |  |  |  | 12.492 | 11.411 | [6 empty] | 29.57 | 4 | 10.8
2009-02-16 | 5.85 | 5.06 |  |  |  |  | 6.96 | 1.71 |  |  |  |  | 34 |  |  |  | 0 | 0.439 |  |  | 0.113 | 0.838 | [5 empty] | 31.6 |  |  |  |  | 63.2 |  | 24.5 |  | 6.7 | 0.063 |  | 3.6 | 70.41 | 0.83 |  |  |  |  | 14.588 | 12.587 | [6 empty] | 28.64 | 4 | 10.6
2009-02-17 | 5.84 | 5.16 |  |  |  |  | 6.68 | 1.65 |  |  |  |  | 34 |  |  |  | 0 | 0.431 |  |  | 0.092 | 0.756 | [5 empty] | 31.7 |  |  |  |  | 63.4 |  | 24.1 |  | 5.9 | 0.061 |  | 3.4 | 63.95 | 0.54 |  |  |  |  | 13.41 | 13.25 | [6 empty] | 30.53 | 4 | 10.8
2009-02-18 | 5.82 | 5.09 |  |  |  |  | 6.71 | 1.63 |  |  |  |  | 37 |  |  |  | 0 | 0.4275 |  |  | 0.103 | 0.819 | [5 empty] | 31.7 |  |  |  |  | 63.5 |  | 22.95 |  | 6.9 | 0.0355 |  | 3.3 | 65.92 | 0.68 |  |  |  |  | 13.999 | 12.9185 | [6 empty] | 29.935 | 4 | 10.8
2009-02-19 | 5.8 | 5.02 |  |  |  |  | 6.74 | 1.61 |  |  |  |  | 40 |  |  |  | 0 | 0.424 |  |  | 0.114 | 0.882 | [5 empty] | 31.7 |  |  |  |  | 63.6 |  | 21.8 |  | 7.9 | 0.01 |  | 3.2 | 67.89 | 0.82 |  |  |  |  | 13.815 | 12.7 | [6 empty] | 29.34 | 4 | 10.8
2009-02-20 | 5.96 | 5.17 |  |  |  |  | 6.78 | 1.59 |  |  |  |  | 37 |  |  |  | 0 | 0.417 |  |  | 0.097 | 0.674 | [5 empty] | 30.4 |  |  |  |  | 60.8 |  | 21.1 |  | 6.9 | 0.014 |  | 3.3 | 66.5 | 0.88 |  |  |  |  | 13.37 | 12.246 | [6 empty] | 30.23 | 4 | 10.8
2009-02-21 | 6.02 | 5.24 |  |  |  |  | 6.94 | 1.62 |  |  |  |  | 40 |  |  |  | 0 | 0.436 |  |  | 0.086 | 0.647 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 23.2 |  | 7.1 | 0.098 |  | 3.2 | 66.15 | 0.92 |  |  |  |  | 12.92 | 11.82 | [6 empty] | 29.51 | 4 | 10.8
2009-02-22 | 6.025 | 5.17 |  |  |  |  | 6.855 | 1.59 |  |  |  |  | 40 |  |  |  | 0 | 0.4285 |  |  | 0.235 | 0.7355 | [5 empty] | 30.45 |  |  |  |  | 60.9 |  | 23.3 |  | 7.35 | 0.0505 |  | 3.15 | 67.055 | 1.01 |  |  |  |  | 13.145 | 12.033 | [6 empty] | 30.48 | 4 | 10.8
2009-02-23 | 6.03 | 5.1 |  |  |  |  | 6.77 | 1.56 |  |  |  |  | 40 |  |  |  | 0 | 0.421 |  |  | 0.384 | 0.824 | [5 empty] | 31.7 |  |  |  |  | 63.4 |  | 23.4 |  | 7.6 | 0.003 |  | 3.1 | 67.96 | 1.1 |  |  |  |  | 13.643 | 11.616 | [6 empty] | 31.45 | 4 | 10.8
2009-02-24 | 5.77 | 5.19 |  |  |  |  | 6.83 | 1.58 |  |  |  |  | 42 |  |  |  | 0 | 0.41 |  |  | 0.105 | 0.745 | [5 empty] | 32.2 |  |  |  |  | 64.4 |  | 24.5 |  | 7.4 | 0.009 |  | 3.2 | 65.45 | 1.11 |  |  |  |  | 13.2 | 11.037 | [6 empty] | 30.98 | 4 | 10.8
2009-02-25 | 5.82 | 5.82 |  |  |  |  | 6.9 | 1.56 |  |  |  |  | 38 |  |  |  | 0 | 0.4155 |  |  | 0.242 | 0.772 | [5 empty] | 32.3 |  |  |  |  | 64.6 |  | 24.5 |  | 6.2 | 0.009 |  | 3.2 | 61.56 | 0.89 |  |  |  |  | 12.595 | 11.416 | [6 empty] | 29.58 | 3.8 | 10.8
2009-02-26 | 5.9 | 5.9 |  |  |  |  | 6.85 | 1.56 |  |  |  |  | 41 |  |  |  | 0 | 0.001 |  |  | 0.16 | 0.754 | [5 empty] | 30 |  |  |  |  | 60.1 |  | 21.1 |  | 5.8 | 0.015 |  | 3.2 | 65.18 | 0.84 |  |  |  |  | 13.471 | 12.321 | [6 empty] | 29.84 | 3.8 | 10.8
2009-02-27 | 5.78 | 5 |  |  |  |  | 6.7 | 1.62 |  |  |  |  | 41 |  |  |  | 0 | 0.001 |  |  | 0.121 | 0.683 | [5 empty] | 30.9 |  |  |  |  | 61.8 |  | 21.8 |  | 6 | 0.031 |  | 3.1 | 66.08 | 0.82 |  |  |  |  | 13.42 | 12.319 | [6 empty] | 29.61 | 3.8 | 10.8
2009-02-28 | 5.78 | 5.78 |  |  |  |  | 6.7 | 1.62 |  |  |  |  | 41 |  |  |  | 0 | 0.001 |  |  | 0.121 | 0.683 | [5 empty] | 30.9 |  |  |  |  | 61.8 |  | 21.8 |  | 6.4 | 0.031 |  | 3.1 | 66.08 | 0.82 |  |  |  |  | 13.11 | 11.94 | [6 empty] | 29.61 | 3.8 | 10.8
2009-03-01 | 5.78 | 5.39 |  |  |  |  | 6.7 | 1.62 |  |  |  |  | 41 |  |  |  | 0 | 0.001 |  |  | 0.121 | 0.683 | [5 empty] | 30.9 |  |  |  |  | 61.8 |  | 21.8 |  | 6.2 | 0.031 |  | 3.1 | 66.08 | 0.82 |  |  |  |  | 13.265 | 12.1295 | [6 empty] | 29.61 | 3.8 | 10.8
2009-03-02 | 5.78 | 5.585 |  |  |  |  | 6.7 | 1.62 |  |  |  |  | 41 |  |  |  | 0 | 0.001 |  |  | 0.121 | 0.683 | [5 empty] | 30.9 |  |  |  |  | 61.8 |  | 21.8 |  | 6.3 | 0.031 |  | 3.1 | 57.68 | 0.82 |  |  |  |  | 11.982 | 10.714 | [6 empty] | 29.61 | 4 | 11
2009-03-03 | 6.04 | 5.13 |  |  |  |  | 7.51 | 1.6 |  |  |  |  | 38 |  |  |  | 0 | 0.001 |  |  | 0.072 | 0.65 | [5 empty] | 32.3 |  |  |  |  | 64.7 |  | 22.8 |  | 6.5 | 0.062 |  | 3 | 67.08 | 0.99 |  |  |  |  | 13.903 | 11.765 | [6 empty] | 29.1 | 4 | 11
2009-03-04 | 5.98 | 5.98 |  |  |  |  | 7.54 | 1.6 |  |  |  |  | 42 |  |  |  | 0 | 0.417 |  |  | 0.061 | 0.582 | [5 empty] | 31.7 |  |  |  |  | 63.4 |  | 23.9 |  | 6.2 | 0.057 |  | 3 | 64.54 | 1.09 |  |  |  |  | 13.101 | 10.871 | [6 empty] | 29.88 | 4 | 11
2009-03-05 | 6.15 | 5.19 |  |  |  |  | 7.6 | 1.6 |  |  |  |  | 36 |  |  |  | 0 | 0.209 |  |  | 0.135 | 0.646 | [5 empty] | 33 |  |  |  |  | 66 |  | 23.4 |  | 6 | 0.052 |  | 3 | 63.72 | 0.84 |  |  |  |  | 13.039 | 11.851 | [6 empty] | 29.22 | 4 | 11
2009-03-06 | 5.81 | 5.81 |  |  |  |  | 6.5 | 1.57 |  |  |  |  | 36 |  |  |  | 0 | 0.313 |  |  | 0.114 | 0.632 | [5 empty] | 32.2 |  |  |  |  | 64.4 |  | 25.3 |  | 5.9 | 0.007 |  | 3 | 63.22 | 0.76 |  |  |  |  | 12.99 | 12.31 | [6 empty] | 29.45 | 4 | 11
2009-03-07 | 5.8 | 5.8 |  |  |  |  | 6.74 | 1.63 |  |  |  |  | 36 |  |  |  | 0 | 0.424 |  |  | 0.083 | 0.652 | [5 empty] | 34.7 |  |  |  |  | 69.5 |  | 23.5 |  | 8.6 | 0.058 |  | 3 | 64.54 | 0.86 |  |  |  |  | 12.283 | 11.753 | [6 empty] | 29.57 | 4.2 | 11.4
2009-03-08 | 5.93 | 5.93 |  |  |  |  | 6.8 | 1.64 |  |  |  |  | 37 |  |  |  | 0 | 0.38 |  |  | 0.113 | 0.942 | [5 empty] | 35.1 |  |  |  |  | 70.2 |  | 21.8 |  | 7.9 | 0.057 |  | 3 | 62.73 | 0.68 |  |  |  |  | 13.7 | 12.31 | [6 empty] | 29.34 | 4.2 | 11.4
2009-03-09 | 5.91 | 5.91 |  |  |  |  | 6.755 | 1.63 |  |  |  |  | 36.5 |  |  |  | 0 | 0.3785 |  |  | 0.1085 | 0.788 | [5 empty] | 34.1 |  |  |  |  | 68.2 |  | 22.1 |  | 7.5 | 0.06 |  | 3 | 65.665 | 0.87 |  |  |  |  | 12.9915 | 12.0315 | [6 empty] | 29.395 | 4.2 | 11.55
2009-03-10 | 5.89 | 5.89 |  |  |  |  | 6.71 | 1.62 |  |  |  |  | 36 |  |  |  | 0 | 0.377 |  |  | 0.104 | 0.634 | [5 empty] | 33.1 |  |  |  |  | 66.2 |  | 22.4 |  | 7.1 | 0.063 |  | 3 | 68.6 | 1.06 |  |  |  |  | 13.72 | 11.641 | [6 empty] | 29.45 | 4.2 | 11.7
2009-03-11 | 5.94 | 5.94 |  |  |  |  | 7.13 | 1.66 |  |  |  |  | 38 |  |  |  | 0 | 0.382 |  |  | 0.099 | 0.747 | [5 empty] | 32.9 |  |  |  |  | 65.8 |  | 21.8 |  | 7 | 0.071 |  | 3 | 57.33 | 0.4 |  |  |  |  | 12.85 | 12.6 | [6 empty] | 30.27 | 4.2 | 11.4
2009-03-12 | 5.8 | 5.8 |  |  |  |  | 6.65 | 1.64 |  |  |  |  | 36 |  |  |  | 0.2 | 0.38 |  |  | 0.288 | 0.881 | [5 empty] | 34.2 |  |  |  |  | 68.4 |  | 22.4 |  | 6.8 | 0.066 |  | 3 | 65.14 | 0.9 |  |  |  |  | 13.318 | 11.64 | [6 empty] | 28.17 | 4.2 | 11.4
2009-03-13 | 5.94 | 5.94 |  |  |  |  | 6.81 | 1.6 |  |  |  |  | 35 |  |  |  | 0 | 0.389 |  |  | 0.152 | 0.89 | [5 empty] | 34.4 |  |  |  |  | 68.8 |  | 21.7 |  | 8.6 | 0.002 |  | 3 | 66.99 | 0.73 |  |  |  |  | 13.801 | 13.068 | [6 empty] | 28.87 | 4.2 | 11.4
2009-03-14 | 5.91 | 5.91 |  |  |  |  | 6.78 | 1.43 |  |  |  |  | 35 |  |  |  | 0 | 0.384 |  |  | 0.107 | 0.725 | [5 empty] | 34.2 |  |  |  |  | 68.4 |  | 21.3 |  | 7.7 | 0.009 |  | 3 | 63.72 | 1.08 |  |  |  |  | 12.722 | 11.519 | [6 empty] | 29.6 | 4.2 | 11.4
2009-03-15 | 6.01 | 5.24 |  |  |  |  | 6.98 | 1.6 |  |  |  |  | 30 |  |  |  | 0 | 0.397 |  |  | 0.146 | 0.659 | [5 empty] | 33.9 |  |  |  |  | 67.9 |  | 21.5 |  | 6.8 | 0.012 |  | 2.9 | 66.18 | 0.94 |  |  |  |  | 12.94 | 11.81 | [6 empty] | 29.6 | 4.2 | 11.4
2009-03-16 | 6.095 | 5.22 |  |  |  |  | 6.855 | 4.095 |  |  |  |  | 33.5 |  |  |  | 0 | 0.383 |  |  | 0.1595 | 0.788 | [5 empty] | 33.75 |  |  |  |  | 67.55 |  | 21.55 |  | 6.7 | 0.027 |  | 2.95 | 67.07 | 0.96 |  |  |  |  | 12.831 | 11.6645 | [6 empty] | 29.47 | 4.2 | 11.4
2009-03-17 | 6.18 | 5.2 |  |  |  |  | 6.73 | 6.59 |  |  |  |  | 37 |  |  |  | 0 | 0.369 |  |  | 0.173 | 0.917 | [5 empty] | 33.6 |  |  |  |  | 67.2 |  | 21.6 |  | 6.6 | 0.042 |  | 3 | 67.96 | 0.98 |  |  |  |  | 13.68 | 12.003 | [6 empty] | 29.34 | 4.2 | 11.4
2009-03-18 | 6.17 | 5.31 |  |  |  |  | 6.97 | 1.56 |  |  |  |  | 36 |  |  |  | 0 | 0.368 |  |  | 0.112 | 0.686 | [5 empty] | 34.2 |  |  |  |  | 68.4 |  | 21.6 |  | 6.8 | 0.072 |  | 3.2 | 61.28 | 0.73 |  |  |  |  | 12.89 | 12.133 | [6 empty] | 29.34 | 4.2 | 11.4
2009-03-19 | 6.14 | 5.3 |  |  |  |  | 6.94 | 1.43 |  |  |  |  | 35 |  |  |  | 0 | 0.374 |  |  | 0.127 | 0.731 | [5 empty] | 33.9 |  |  |  |  | 67.8 |  | 22.6 |  | 6.9 | 0.081 |  | 3.2 | 71.86 | 1.19 |  |  |  |  | 14.562 | 12.438 | [6 empty] | 28.74 | 4 | 11.4
2009-03-20 | 6.04 | 5.32 |  |  |  |  | 7.11 | 1.46 |  |  |  |  | 40 |  |  |  | 0 | 0.359 |  |  | 0.091 | 0.62 | [5 empty] | 32.6 |  |  |  |  | 65.2 |  | 23.2 |  | 6.4 | 0.095 |  | 3.2 | 63.06 | 0.84 |  |  |  |  | 14.562 | 12.438 | [6 empty] | 30.54 | 4 | 11.4
2009-03-21 | 5.73 | 5.33 |  |  |  |  | 6.81 | 1.44 |  |  |  |  | 42 |  |  |  | 0 | 0.357 |  |  | 0.104 | 0.756 | [5 empty] | 32.4 |  |  |  |  | 64.8 |  | 23.7 |  | 6.6 | 0.083 |  | 3.4 | 66.99 | 1.15 |  |  |  |  | 13.443 | 11.743 | [6 empty] | 29.25 | 4 | 11.4
2009-03-22 | 6.1 | 5.22 |  |  |  |  | 7.01 | 1.53 |  |  |  |  | 42 |  |  |  | 0 | 0.366 |  |  | 0.113 | 1.241 | [5 empty] | 33.1 |  |  |  |  | 66.2 |  | 23.6 |  | 6.2 | 0.091 |  | 3.1 | 67.05 | 0.87 |  |  |  |  | 13.35 | 12.66 | [6 empty] | 29.44 | 4.2 | 11.4
2009-03-23 | 6.07 | 5.24 |  |  |  |  | 6.975 | 1.56 |  |  |  |  | 40.5 |  |  |  | 0 | 0.3615 |  |  | 0.16 | 0.9785 | [5 empty] | 32.85 |  |  |  |  | 65.7 |  | 23.9 |  | 6.3 | 0.09 |  | 3.15 | 63.33 | 0.75 |  |  |  |  | 12.956 | 11.834 | [6 empty] | 29.105 | 4.1 | 11.4
2009-03-24 | 6.04 | 5.26 |  |  |  |  | 6.94 | 1.59 |  |  |  |  | 39 |  |  |  | 0 | 0.357 |  |  | 0.207 | 0.716 | [5 empty] | 32.6 |  |  |  |  | 65.2 |  | 24.2 |  | 6.4 | 0.089 |  | 3.2 | 71.82 | 1.02 |  |  |  |  | 14.965 | 12.484 | [6 empty] | 28.77 | 4.1 | 11.4
2009-03-25 | 6.12 | 5.37 |  |  |  |  | 7.25 | 1.49 |  |  |  |  | 40 |  |  |  | 0 | 0.354 |  |  | 0.085 | 0.561 | [5 empty] | 31.3 |  |  |  |  | 62.6 |  | 21.7 |  | 6.7 | 0.098 |  | 3.1 | 67.14 | 1 |  |  |  |  | 14.471 | 12.229 | [6 empty] | 29 | 4.1 | 11.4
2009-03-26 | 5.92 | 5.36 |  |  |  |  | 7.01 | 1.51 |  |  |  |  | 41 |  |  |  | 0 | 0.354 |  |  | 0.079 | 0.603 | [5 empty] | 31.6 |  |  |  |  | 63.2 |  | 21.7 |  | 6.9 | 0.081 |  | 3.5 | 69.41 | 0.99 |  |  |  |  | 13.833 | 12.603 | [6 empty] | 29.29 | 4.1 | 11.4
2009-03-27 | 6.01 | 5.29 |  |  |  |  | 6.95 | 1.67 |  |  |  |  | 39 |  |  |  | 0 | 0.357 |  |  | 0.061 | 0.493 | [5 empty] | 30.7 |  |  |  |  | 61.4 |  | 22.4 |  | 7.2 | 0.069 |  | 3.5 | 66.18 | 0.67 |  |  |  |  | 13.11 | 12.86 | [6 empty] | 29.32 | 4.1 | 11.4
2009-03-28 | 5.8 | 5.26 |  |  |  |  | 6.83 | 1.55 |  |  |  |  | 37 |  |  |  | 0 | 0.351 |  |  | 0.09 | 0.517 | [5 empty] | 33.3 |  |  |  |  | 66.7 |  | 23 |  | 6.7 | 0.058 |  | 3 | 63.57 | 0.9 |  |  |  |  | 13.074 | 11.797 | [6 empty] | 28.17 | 4.1 | 11.4
2009-03-29 | 5.86 | 5.13 |  |  |  |  | 6.63 | 1.54 |  |  |  |  | 36 |  |  |  | 0 | 0.359 |  |  | 0.082 | 0.719 | [5 empty] | 33.1 |  |  |  |  | 66.2 |  | 22.6 |  | 6.9 | 0.072 |  | 3.1 | 69.04 | 0.97 |  |  |  |  | 14.01 | 12.5 | [6 empty] | 27.7 | 4.1 | 11.4
2009-03-30 | 5.885 | 5.135 |  |  |  |  | 6.705 | 1.545 |  |  |  |  | 34 |  |  |  | 0 | 0.352 |  |  | 0.0805 | 0.586 | [5 empty] | 33.45 |  |  |  |  | 66.9 |  | 22.2 |  | 6.8 | 0.0665 |  | 3.05 | 69.58 | 1.06 |  |  |  |  | 13.542 | 12.1485 | [6 empty] | 27.73 | 4.1 | 11.4
2009-03-31 | 5.91 | 5.14 |  |  |  |  | 6.78 | 1.55 |  |  |  |  | 32 |  |  |  | 0 | 0.345 |  |  | 0.079 | 0.453 | [5 empty] | 33.8 |  |  |  |  | 67.6 |  | 21.8 |  | 6.7 | 0.061 |  | 3 | 70.12 | 1.15 |  |  |  |  | 13.944 | 11.773 | [6 empty] | 27.76 | 4.1 | 11.4
2009-04-01 | 5.69 | 5.32 |  |  |  |  | 6.71 | 1.54 |  |  |  |  | 35 |  |  |  | 0 | 0.352 |  |  | 0.093 | 0.508 | [5 empty] | 33.8 |  |  |  |  | 67.6 |  | 25.1 |  | 6.7 | 0.059 |  | 3 | 66.15 | 0.78 |  |  |  |  | 13.23 | 12.96 | [6 empty] | 27.09 | 4.1 | 11.4
2009-04-02 | 5.72 | 5.2 |  |  |  |  | 6.82 | 1.59 |  |  |  |  | 36 |  |  |  | 0 | 0.349 |  |  | 0.064 | 0.518 | [5 empty] | 34.1 |  |  |  |  | 68.2 |  | 22.3 |  | 8.4 | 0.007 |  | 3.1 | 69.89 | 0.84 |  |  |  |  | 14.184 | 13.036 | [6 empty] | 32.39 | 4.1 | 11.4
2009-04-03 | 5.77 | 5.07 |  |  |  |  | 6.52 | 1.43 |  |  |  |  | 35 |  |  |  | 0 | 0.357 |  |  | 0.073 | 0.892 | [5 empty] | 34.3 |  |  |  |  | 68.7 |  | 23.7 |  | 7.8 | 0.009 |  | 3 | 65.59 | 1.08 |  |  |  |  | 13.317 | 12.053 | [6 empty] | 32.39 | 4.1 | 11.4
2009-04-04 | 5.93 | 5.05 |  |  |  |  | 6.67 | 1.39 |  |  |  |  | 36 |  |  |  | 0 | 0.347 |  |  | 0.068 | 0.507 | [5 empty] | 33.9 |  |  |  |  | 67.8 |  | 22.7 |  | 6.9 | 0.012 |  | 3.1 | 66.5 | 1.11 |  |  |  |  | 13.242 | 12.061 | [6 empty] | 32.21 | 4.1 | 11.4
2009-04-05 | 5.89 | 5.03 |  |  |  |  | 6.85 | 1.29 |  |  |  |  | 33 |  |  |  | 0 | 0.347 |  |  | 0.051 | 0.512 | [5 empty] | 31.6 |  |  |  |  | 63.2 |  | 22.7 |  | 6.9 | 0.018 |  | 3.2 | 35.28 | 0.1 |  |  |  |  | 12.769 | 11.556 | [6 empty] | 30.71 | 4.1 | 11.4
2009-04-06 | 5.82 | 5.05 |  |  |  |  | 6.765 | 1.4 |  |  |  |  | 33 |  |  |  | 0 | 0.351 |  |  | 0.0985 | 0.6985 | [5 empty] | 33.5 |  |  |  |  | 67.05 |  | 22.95 |  | 7.9 | 0.0205 |  | 3.1 | 54.47 | 0.65 |  |  |  |  | 13.0055 | 11.8085 | [6 empty] | 31.55 | 4.1 | 11.4
2009-04-07 | 5.75 | 5.07 |  |  |  |  | 6.68 | 1.51 |  |  |  |  | 33 |  |  |  | 0 | 0.355 |  |  | 0.146 | 0.885 | [5 empty] | 35.4 |  |  |  |  | 70.9 |  | 23.2 |  | 8.9 | 0.023 |  | 3 | 73.66 | 1.2 |  |  |  |  | 14.395 | 12.36 | [6 empty] | 32.39 | 4.1 | 11.4
2009-04-08 | 5.39 | 5.03 |  |  |  |  | 6.98 | 1.46 |  |  |  |  | 33 |  |  |  | 0 | 0.353 |  |  | 0.199 | 0.65 | [5 empty] | 36.2 |  |  |  |  | 72.4 |  | 23.4 |  | 8.6 | 0.024 |  | 3 | 66.26 | 1.18 |  |  |  |  | 13.59 | 11.408 | [6 empty] | 30.98 | 4.1 | 11.4
2009-04-09 | 5.9 | 5.38 |  |  |  |  | 6.98 | 1.59 |  |  |  |  | 33 |  |  |  | 0 | 0.347 |  |  | 0.067 | 0.597 | [5 empty] | 34.8 |  |  |  |  | 69.6 |  | 22.8 |  | 7.9 | 0.037 |  | 3.1 | 64.43 | 0.56 |  |  |  |  | 14.932 | 13.624 | [6 empty] | 29.91 | 4.1 | 11.4
2009-04-10 | 5.9 | 5.41 |  |  |  |  | 6.98 | 1.57 |  |  |  |  | 31 |  |  |  | 0 | 0.346 |  |  | 0.101 | 0.557 | [5 empty] | 27.8 |  |  |  |  | 55.6 |  | 23.6 |  | 7.2 | 0.0305 |  | 4 | 70.16 | 0.94 |  |  |  |  | 13.912 | 12.715 | [6 empty] | 29.31 | 4.1 | 11.4
2009-04-11 | 5.88 | 5.2 |  |  |  |  | 6.83 | 1.58 |  |  |  |  | 33 |  |  |  | 0 | 0.348 |  |  | 0.096 | 0.536 | [5 empty] | 33.3 |  |  |  |  | 66.6 |  | 23.9 |  | 6.9 | 0.036 |  | 3 | 70.34 | 0.91 |  |  |  |  | 13.996 | 12.811 | [6 empty] | 29.33 | 4.1 | 11.4
2009-04-12 | 6.05 | 5.05 |  |  |  |  | 6.71 | 1.36 |  |  |  |  | 44 |  |  |  | 0 | 0.355 |  |  | 0.101 | 0.584 | [5 empty] | 34.1 |  |  |  |  | 68.2 |  | 21.8 |  | 7.1 | 0.056 |  | 2.9 | 67.58 | 1.04 |  |  |  |  | 14 | 12.78 | [6 empty] | 29.52 | 4.1 | 11.6
2009-04-13 | 6.07 | 5.24 |  |  |  |  | 6.84 | 1.4 |  |  |  |  | 43 |  |  |  | 0 | 0.351 |  |  | 0.085 | 0.5465 | [5 empty] | 33.9 |  |  |  |  | 67.8 |  | 22.05 |  | 6.95 | 0.0585 |  | 2.95 | 66.99 | 1.08 |  |  |  |  | 13.55 | 12.279 | [6 empty] | 28.84 | 4.1 | 11.6
2009-04-14 | 6.09 | 5.43 |  |  |  |  | 6.97 | 1.46 |  |  |  |  | 42 |  |  |  | 0 | 0.347 |  |  | 0.069 | 0.509 | [5 empty] | 33.7 |  |  |  |  | 67.4 |  | 22.3 |  | 6.8 | 0.061 |  | 3 | 74.31 | 1.21 |  |  |  |  | 14.707 | 12.648 | [6 empty] | 28.16 | 4.1 | 11.6
2009-04-15 | 6.04 | 5.41 |  |  |  |  | 6.98 | 1.36 |  |  |  |  | 36 |  |  |  | 0 | 0.347 |  |  | 0.58 | 0.557 | [5 empty] | 34.2 |  |  |  |  | 68.4 |  | 24.5 |  | 7.4 | 0.078 |  | 3.1 | 66.02 | 1.3 |  |  |  |  | 13.517 | 11.258 | [6 empty] | 29.72 | 4.1 | 11.6
2009-04-16 | 5.72 | 5.47 |  |  |  |  | 6.89 | 1.38 |  |  |  |  | 27 |  |  |  | 0 | 0.352 |  |  | 0.069 | 0.511 | [5 empty] | 34.7 |  |  |  |  | 69.4 |  | 24.1 |  | 7.1 | 0.063 |  | 3 | 68.38 | 1.24 |  |  |  |  | 13.224 | 11.86 | [6 empty] | 29.58 | 4.1 | 11.6
2009-04-17 | 5.72 | 5.03 |  |  |  |  | 6.37 | 1.36 |  |  |  |  | 43 |  |  |  | 0 | 0.465 |  |  | 0.091 | 0.731 | [5 empty] | 39.2 |  |  |  |  | 78.4 |  | 24.1 |  | 6.9 | 0.053 |  | 2.5 | 72.77 | 1.24 |  |  |  |  | 13.94 | 12.71 | [6 empty] | 29.23 | 4.1 | 11.6
2009-04-18 | 5.53 | 4.98 |  |  |  |  | 6.9 | 1.4 |  |  |  |  | 44 |  |  |  | 0 | 0.483 |  |  | 0.087 | 0.748 | [5 empty] | 37.8 |  |  |  |  | 77.1 |  | 21.7 |  | 9.5 | 0.01 |  | 2.7 | 67.96 | 1.15 |  |  |  |  | 13.287 | 12.113 | [6 empty] | 29.57 | 4.1 | 12
2009-04-19 | 5.37 | 5.37 |  |  |  |  | 6.82 | 1.44 |  |  |  |  | 44 |  |  |  | 0 | 0.465 |  |  | 0.1 | 0.731 | [5 empty] | 36.2 |  |  |  |  | 72.5 |  | 22.8 |  | 9.2 | 0.012 |  | 2.8 | 70.56 | 1.12 |  |  |  |  | 13.71 | 12.52 | [6 empty] | 29.34 | 4.1 | 12
2009-04-20 | 5.54 | 5.205 |  |  |  |  | 6.965 | 1.515 |  |  |  |  | 43 |  |  |  | 0 | 0.4235 |  |  | 0.097 | 0.7135 | [5 empty] | 35.4 |  |  |  |  | 70.85 |  | 23.05 |  | 8.4 | 0.024 |  | 2.7 | 72.115 | 1.3 |  |  |  |  | 13.4985 | 12.3165 | [6 empty] | 29.725 | 4.1 | 12
2009-04-21 | 5.71 | 5.04 |  |  |  |  | 7.11 | 1.59 |  |  |  |  | 42 |  |  |  | 0 | 0.382 |  |  | 0.094 | 0.696 | [5 empty] | 34.6 |  |  |  |  | 69.2 |  | 23.3 |  | 7.6 | 0.036 |  | 2.6 | 73.67 | 1.48 |  |  |  |  | 14.101 | 12.067 | [6 empty] | 30.11 | 4.1 | 12
2009-04-22 | 5.63 | 5 |  |  |  |  | 6.81 | 1.52 |  |  |  |  | 44 |  |  |  | 0 | 0.382 |  |  | 0.104 | 0.723 | [5 empty] | 36.1 |  |  |  |  | 72.2 |  | 23.9 |  | 6.2 | 0.038 |  | 2.7 | 70.56 | 0.92 |  |  |  |  | 13.36 | 13.15 | [6 empty] | 29.43 | 4.1 | 12
2009-04-23 | 5.81 | 5.13 |  |  |  |  | 7.32 | 1.44 |  |  |  |  | 37 |  |  |  | 0 | 0.38 |  |  | 0.291 | 0.628 | [5 empty] | 37.3 |  |  |  |  | 74.7 |  | 23.4 |  | 8.6 | 0.031 |  | 2.7 | 70.56 | 1.14 |  |  |  |  | 13.555 | 12.409 | [6 empty] | 30.98 | 4.1 | 12.4
2009-04-24 | 5.75 | 5.08 |  |  |  |  | 6.91 | 1.44 |  |  |  |  | 36 |  |  |  | 0 | 0.397 |  |  | 0.287 | 0.642 | [5 empty] | 36.6 |  |  |  |  | 73.3 |  | 22.7 |  | 8.4 | 0.044 |  | 2.7 | 66.5 | 1.1 |  |  |  |  | 13.037 | 11.867 | [6 empty] | 30.51 | 4.1 | 12.4
2009-04-25 | 5.9 | 5.1 |  |  |  |  | 7.07 | 1.43 |  |  |  |  | 31 |  |  |  | 0 | 0.401 |  |  | 0.1 | 0.657 | [5 empty] | 34.9 |  |  |  |  | 69.8 |  | 23.3 |  | 7.7 | 0.057 |  | 28 | 70.89 | 1.13 |  |  |  |  | 13.768 | 12.591 | [6 empty] | 30.98 | 4.1 | 12.4
2009-04-26 | 5.9 | 5.1 |  |  |  |  | 7.08 | 1.42 |  |  |  |  | 38 |  |  |  | 0 | 0.421 |  |  | 0.084 | 0.627 | [5 empty] | 35.1 |  |  |  |  | 70.2 |  | 25.5 |  | 7.4 | 0.049 |  | 2.9 | 66.15 | 1.06 |  |  |  |  | 13.3 | 12.11 | [6 empty] | 30.06 | 4.1 | 12.4
2009-04-27 | 5.99 | 5.09 |  |  |  |  | 7.215 | 1.515 |  |  |  |  | 42.5 |  |  |  | 0 | 0.436 |  |  | 0.0925 | 0.7105 | [5 empty] | 30.45 |  |  |  |  | 70.9 |  | 24.35 |  | 7.5 | 0.05 |  | 2.8 | 68.035 | 1.1 |  |  |  |  | 13.534 | 12.3505 | [6 empty] | 29.935 | 4.1 | 12.4
2009-04-28 | 6.08 | 5.08 |  |  |  |  | 7.35 | 1.61 |  |  |  |  | 47 |  |  |  | 0 | 0.451 |  |  | 0.101 | 0.794 | [5 empty] | 25.8 |  |  |  |  | 71.6 |  | 23.2 |  | 7.6 | 0.051 |  | 2.7 | 69.92 | 1.14 |  |  |  |  | 13.505 | 11.538 | [6 empty] | 29.81 | 4.1 | 12.4
2009-04-29 | 5.71 | 5.14 |  |  |  |  | 7.02 | 1.68 |  |  |  |  | 44 |  |  |  | 0 | 0.383 |  |  | 0.086 | 0.805 | [5 empty] | 35.6 |  |  |  |  | 71.3 |  | 22.3 |  | 10 | 0.01 |  | 2.5 | 61.61 | 1.06 |  |  |  |  | 12.293 | 10.208 | [6 empty] | 29.11 | 4.1 | 12.4
2009-04-30 | 5.82 | 5 |  |  |  |  | 7.11 | 1.65 |  |  |  |  | 45 |  |  |  | 0 | 0.394 |  |  | 0.079 | 0.824 | [5 empty] | 34.7 |  |  |  |  | 69.4 |  | 22.1 |  | 8.2 | 0.082 |  | 2.6 | 64.85 | 0.81 |  |  |  |  | 13.006 | 11.958 | [6 empty] | 30.24 | 4.1 | 12.4
2009-05-01 | 5.92 | 4.99 |  |  |  |  | 7.31 | 1.72 |  |  |  |  | 45 |  |  |  | 0 | 0.407 |  |  | 0.068 | 0.797 | [5 empty] | 33.4 |  |  |  |  | 66.8 |  | 21.6 |  | 7.8 | 0.076 |  | 2.9 | 63.81 | 0.39 |  |  |  |  | 12.472 | 11.54 | [6 empty] | 29.49 | 4.1 | 12.4
2009-05-02 | 5.6 | 4.94 |  |  |  |  | 6.62 | 1.79 |  |  |  |  | 47 |  |  |  | 0 | 0.384 |  |  | 0.073 | 0.833 | [5 empty] | 32.1 |  |  |  |  | 64.2 |  | 21.4 |  | 7.1 | 0.063 |  | 2.3 | 67.72 | 1.79 |  |  |  |  | 12.898 | 11.983 | [6 empty] | 29.57 | 4.1 | 12.4
2009-05-03 | 5.49 | 5.07 |  |  |  |  | 7.39 | 1.84 |  |  |  |  | 46 |  |  |  | 0 | 0.377 |  |  | 0.071 | 0.732 | [5 empty] | 32.1 |  |  |  |  | 64.2 |  | 22.4 |  | 7 | 0.074 |  | 2.3 | 68.6 | 0.77 |  |  |  |  | 12.73 | 11.93 | [6 empty] | 29.23 | 4.1 | 12.4
2009-05-04 | 5.545 | 5.005 |  |  |  |  | 7.005 | 1.815 |  |  |  |  | 46.5 |  |  |  | 0 | 0.3805 |  |  | 0.072 | 0.7825 | [5 empty] | 32.1 |  |  |  |  | 64.2 |  | 21.9 |  | 7.05 | 0.0685 |  | 2.3 | 68.16 | 1.28 |  |  |  |  | 12.814 | 11.9565 | [6 empty] | 29.4 | 4.1 | 12.4
2009-05-05 | 5.5175 | 5.0375 |  |  |  |  | 7.1975 | 1.79 |  |  |  |  | 46.25 |  |  |  | 0 | 0.37875 |  |  | 0.0715 | 0.75725 | [5 empty] | 32.1 |  |  |  |  | 64.2 |  | 22.15 |  | 7.025 | 0.07125 |  | 2.3 | 65.36 | 0.82 |  |  |  |  | 12.258 | 11.375 | [6 empty] | 29.315 | 4.1 | 12.4
2009-05-06 | 5.69 | 5.05 |  |  |  |  | 7.1 | 1.66 |  |  |  |  | 43 |  |  |  | 0 | 0.354 |  |  | 0.354 | 0.794 | [5 empty] | 29.7 |  |  |  |  | 59.5 |  | 22.6 |  | 6.8 | 0.082 |  | 2.4 | 64.63 | 1 |  |  |  |  | 12.823 | 11.043 | [6 empty] | 28.7 | 4.1 | 12.4
2009-05-07 | 5.46 | 4.97 |  |  |  |  | 6.87 | 1.66 |  |  |  |  | 45 |  |  |  | 0 | 0.327 |  |  | 0.094 | 0.813 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 23 |  | 6.7 | 0.089 |  | 3.6 | 64.3 | 0.83 |  |  |  |  | 12.812 | 11.729 | [6 empty] | 28.06 | 4.1 | 12.4
2009-05-08 | 5.46 | 4.98 |  |  |  |  | 6.82 | 1.78 |  |  |  |  | 46 |  |  |  | 0 | 0.321 |  |  | 0.104 | 0.834 | [5 empty] | 26.1 |  |  |  |  | 52.2 |  | 23.4 |  | 6.9 | 0.073 |  | 3.7 | 68.36 | 0.94 |  |  |  |  | 13.41 | 11.4 | [6 empty] | 28.08 | 4.3 | 12.4
2009-05-09 | 5.63 | 4.74 |  |  |  |  | 6.28 | 1.72 |  |  |  |  | 38 |  |  |  | 0 | 0.312 |  |  | 0.094 | 0.985 | [5 empty] | 27.3 |  |  |  |  | 54.7 |  | 22.9 |  | 6.7 | 0.009 |  | 3.9 | 60.73 | 0.73 |  |  |  |  | 12.092 | 11.241 | [6 empty] | 30.04 | 4.5 | 12.6
2009-05-10 | 6.04 | 4.68 |  |  |  |  | 6.26 | 1.71 |  |  |  |  | 37 |  |  |  | 0 | 0.296 |  |  | 0.068 | 0.892 | [5 empty] | 28.5 |  |  |  |  | 57 |  | 23.9 |  | 6.8 | 0.011 |  | 3.9 | 66.26 | 0.85 |  |  |  |  | 12.61 | 11.77 | [6 empty] | 32.86 | 4.7 | 12.6
2009-05-11 | 5.885 | 4.87 |  |  |  |  | 6.56 | 1.735 |  |  |  |  | 35.5 |  |  |  | 0 | 0.3015 |  |  | 0.0695 | 0.84 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 25.15 |  | 6.85 | 0.022 |  | 4.1 | 69.06 | 0.925 |  |  |  |  | 12.351 | 11.5055 | [6 empty] | 31.565 | 4.7 | 12.6
2009-05-12 | 5.73 | 5.06 |  |  |  |  | 6.86 | 1.76 |  |  |  |  | 34 |  |  |  | 0 | 0.307 |  |  | 0.071 | 0.788 | [5 empty] | 28.3 |  |  |  |  | 56.6 |  | 26.4 |  | 6.9 | 0.033 |  | 4.3 | 71.86 | 1 |  |  |  |  | 13.53 | 11.842 | [6 empty] | 30.27 | 4.7 | 12.6
2009-05-13 | 6.1 | 4.94 |  |  |  |  | 6.96 | 1.8 |  |  |  |  | 38 |  |  |  | 0 | 0.32 |  |  | 0.069 | 0.824 | [5 empty] | 27.5 |  |  |  |  | 55 |  | 23.3 |  | 7 | 0.042 |  | 4.2 | 66.15 | 0.57 |  |  |  |  | 12.51 | 12.68 | [6 empty] | 30.67 | 5 | 12.8
2009-05-14 | 5.71 | 5.01 |  |  |  |  | 6.93 | 1.72 |  |  |  |  | 36 |  |  |  | 0 | 0.282 |  |  | 0.065 | 0.786 | [5 empty] | 28.1 |  |  |  |  | 56.1 |  | 21.9 |  | 7.2 | 0.055 |  | 4.3 | 59.65 | 0.76 |  |  |  |  | 11.643 | 10.913 | [6 empty] | 30.04 | 5 | 13
2009-05-15 | 5.56 | 4.93 |  |  |  |  | 6.87 | 1.78 |  |  |  |  | 41 |  |  |  | 0 | 0.286 |  |  | 0.071 | 0.799 | [5 empty] | 27.6 |  |  |  |  | 55.3 |  | 23.3 |  | 6.9 | 0.003 |  | 4.2 | 68.71 | 0.7 |  |  |  |  | 13.348 | 12.556 | [6 empty] | 32.39 | 5 | 13
2009-05-16 | 5.65 | 5.22 |  |  |  |  | 7.07 | 1.63 |  |  |  |  | 36 |  |  |  | 0 | 0.291 |  |  | 0.064 | 0.678 | [5 empty] | 27.6 |  |  |  |  | 55.2 |  | 21.8 |  | 6.8 | 0.015 |  | 4.1 | 61.76 | 0.75 |  |  |  |  | 12.605 | 11.777 | [6 empty] | 32.86 | 5 | 12.5
2009-05-17 | 6.1 | 4.85 |  |  |  |  | 6.68 | 1.51 |  |  |  |  | 38 |  |  |  | 0 | 0.297 |  |  | 0.068 | 0.663 | [5 empty] | 25.7 |  |  |  |  | 51.4 |  | 22.7 |  | 7.1 | 0.023 |  | 5.2 | 57.33 | 0.83 |  |  |  |  | 11.87 | 11.1 | [6 empty] | 31.54 | 5 | 12.5
2009-05-18 | 5.955 | 4.965 |  |  |  |  | 7.155 | 1.535 |  |  |  |  | 37 |  |  |  | 0 | 0.306 |  |  | 0.074 | 0.584 | [5 empty] | 26.95 |  |  |  |  | 53.95 |  | 22.3 |  | 7 | 0.03 |  | 6.15 | 59.535 | 0.82 |  |  |  |  | 12.2375 | 11.4385 | [6 empty] | 31.73 | 5 | 12.6
2009-05-19 | 5.81 | 5.08 |  |  |  |  | 7.63 | 1.56 |  |  |  |  | 36 |  |  |  | 0 | 0.315 |  |  | 0.08 | 0.505 | [5 empty] | 28.2 |  |  |  |  | 56.5 |  | 21.9 |  | 6.9 | 0.037 |  | 7.1 | 61.74 | 0.81 |  |  |  |  | 12.68 | 11.84 | [6 empty] | 31.92 | 5 | 12.7
2009-05-20 | 6.04 | 4.86 |  |  |  |  | 7.55 | 1.67 |  |  |  |  | 35 |  |  |  | 0 | 0.321 |  |  | 0.064 | 0.593 | [5 empty] | 27.9 |  |  |  |  | 55.6 |  | 23.4 |  | 7.3 | 0.106 |  | 7.9 | 64.54 | 0.7 |  |  |  |  | 13.164 | 12.373 | [6 empty] | 31.92 | 5 | 12.7
2009-05-21 | 6 | 4.94 |  |  |  |  | 7.7 | 1.68 |  |  |  |  | 31 |  |  |  | 0 | 0.384 |  |  | 0.059 | 0.342 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 23.9 |  | 7.1 | 0.097 |  | 8 | 66.92 | 0.71 |  |  |  |  | 13.576 | 12.734 | [6 empty] | 31.38 | 5 | 12
2009-05-22 | 5.95 | 4.92 |  |  |  |  | 8.47 | 1.67 |  |  |  |  | 34 |  |  |  | 0 | 0.642 |  |  | 0.059 | 0.571 | [5 empty] | 28.1 |  |  |  |  | 56.3 |  | 21.2 |  | 7.8 | 0.074 |  | 9.8 | 61.21 | 0.68 |  |  |  |  | 12.629 | 11.801 | [6 empty] | 30.82 | 5 | 11
2009-05-23 | 6.18 | 4.94 |  |  |  |  | 7.8 | 1.86 |  |  |  |  | 36 |  |  |  | 0 | 0.726 |  |  | 0.063 | 0.332 | [5 empty] | 25.9 |  |  |  |  | 51.8 |  | 21.6 |  | 7.9 | 0.056 |  | 9.6 | 60.64 | 0.55 |  |  |  |  | 12.263 | 11.431 | [6 empty] | 29.6 | 5 | 10
2009-05-24 | 6.02 | 4.94 |  |  |  |  | 7.12 | 2.07 |  |  |  |  | 38 |  |  |  | 0 | 0.558 |  |  | 0.061 | 0.476 | [5 empty] | 22 |  |  |  |  | 44 |  | 22.6 |  | 7.2 | 0.061 |  | 9.6 | 63.31 | 0.42 |  |  |  |  | 12.373 | 11.521 | [6 empty] | 29.24 | 5 | 10
2009-05-25 | 6.055 | 4.98 |  |  |  |  | 7.65 | 2.025 |  |  |  |  | 36.5 |  |  |  | 0 | 0.5975 |  |  | 0.06 | 0.3715 | [5 empty] | 23.6 |  |  |  |  | 47.2 |  | 22.95 |  | 7.35 | 0.0675 |  | 9.6 | 65.195 | 0.52 |  |  |  |  | 12.318 | 11.476 | [6 empty] | 29.025 | 5 | 10.2
2009-05-26 | 6.09 | 5.02 |  |  |  |  | 8.18 | 1.98 |  |  |  |  | 35 |  |  |  | 0 | 0.637 |  |  | 0.059 | 0.267 | [5 empty] | 25.2 |  |  |  |  | 50.4 |  | 23.3 |  | 7.5 | 0.074 |  | 9.6 | 67.08 | 0.62 |  |  |  |  | 13.387 | 11.709 | [6 empty] | 28.81 | 5 | 10.4
2009-05-27 | 6.07 | 4.95 |  |  |  |  | 7.97 | 2 |  |  |  |  | 37 |  |  |  | 0 | 0.653 |  |  | 0.073 | 0.341 | [5 empty] | 26.7 |  |  |  |  | 53.4 |  | 23 |  | 8 | 0.069 |  | 9.6 | 61.12 | 0.58 |  |  |  |  | 12.566 | 10.746 | [6 empty] | 29.62 | 5 | 9.5
2009-05-28 | 5.83 | 4.9 |  |  |  |  | 7.1 | 1.72 |  |  |  |  | 37 |  |  |  | 0 | 1.036 |  |  | 0.079 | 0.306 | [5 empty] | 26.9 |  |  |  |  | 53.8 |  | 22.2 |  | 6.8 | 0.041 |  | 10.1 | 58.61 | 0.65 |  |  |  |  | 12.102 | 11.245 | [6 empty] | 29.24 | 5 | 9.5
2009-05-29 | 6.21 | 5.09 |  |  |  |  | 7.16 | 2.03 |  |  |  |  | 30 |  |  |  | 0 | 0.598 |  |  | 0.063 | 0.239 | [5 empty] | 25.1 |  |  |  |  | 50.2 |  | 22.7 |  | 7.4 | 0.058 |  | 10.5 | 66.15 | 0.39 |  |  |  |  | 12.3 | 12.41 | [6 empty] | 29.43 | 5.2 | 9.3
2009-05-30 | 5.98 | 4.99 |  |  |  |  | 7.48 | 1.75 |  |  |  |  | 36 |  |  |  | 0 | 0.582 |  |  | 0.064 | 0.259 | [5 empty] | 26.4 |  |  |  |  | 52.8 |  | 21.4 |  | 6.7 | 0.154 |  | 11.4 | 66.65 | 0.81 |  |  |  |  | 12.616 | 11.802 | [6 empty] | 27.7 | 5.2 | 9
2009-05-31 | 6.37 | 4.59 |  |  |  |  | 7.09 | 1.59 |  |  |  |  | 35 |  |  |  | 0 | 0.611 |  |  | 0.063 | 0.293 | [5 empty] | 26.5 |  |  |  |  | 53 |  | 21.4 |  | 6.5 | 0.108 |  | 11.6 | 64.06 | 0.89 |  |  |  |  | 12.519 | 11.73 | [6 empty] | 29.57 | 5.4 | 9
2009-06-01 | 6.17 | 4.605 |  |  |  |  | 7.055 | 1.57 |  |  |  |  | 36 |  |  |  | 0 | 0.644 |  |  | 0.0655 | 0.3225 | [5 empty] | 25.4 |  |  |  |  | 50.8 |  | 21.6 |  | 6.6 | 0.088 |  | 11.8 | 67.64 | 0.985 |  |  |  |  | 12.5675 | 11.766 | [6 empty] | 29.585 | 5.4 | 8.5
2009-06-02 | 5.97 | 4.62 |  |  |  |  | 7.02 | 1.55 |  |  |  |  | 37 |  |  |  | 0 | 0.677 |  |  | 0.068 | 0.352 | [5 empty] | 24.3 |  |  |  |  | 48.6 |  | 21.8 |  | 6.7 | 0.068 |  | 12 | 71.22 | 1.08 |  |  |  |  | 13.984 | 12.279 | [6 empty] | 29.6 | 5.4 | 8
2009-06-03 | 6.14 | 4.9 |  |  |  |  | 7.54 | 1.57 |  |  |  |  | 38 |  |  |  | 0 | 0.551 |  |  | 0.061 | 0.243 | [5 empty] | 25.6 |  |  |  |  | 51.2 |  | 22.3 |  | 7 | 0.073 |  | 12.2 | 68.44 | 1.13 |  |  |  |  | 13.31 | 11.494 | [6 empty] | 30.01 | 5.6 | 8.5
2009-06-04 | 6.04 | 4.98 |  |  |  |  | 7.34 | 1.52 |  |  |  |  | 37 |  |  |  | 0 | 0.525 |  |  | 0.069 | 0.209 | [5 empty] | 25.8 |  |  |  |  | 51.6 |  | 23 |  | 6.9 | 0.084 |  | 12.4 | 65.57 | 0.92 |  |  |  |  | 12.979 | 12.179 | [6 empty] | 29.04 | 5.6 | 8.5
2009-06-05 | 6.51 | 5.02 |  |  |  |  | 7.79 | 1.4 |  |  |  |  | 38 |  |  |  | 0 | 0.564 |  |  | 0.063 | 0.197 | [5 empty] | 25.9 |  |  |  |  | 51.8 |  | 23.1 |  | 7.1 | 0.073 |  | 12.6 | 49.29 | 0.29 |  |  |  |  | 13.974 | 13.189 | [7 empty] | 5.6 | 8.5
2009-06-06 | 6.49 | 5.08 |  |  |  |  | 7.94 | 1.49 |  |  |  |  | 34 |  |  |  | 0 | 0.509 |  |  | 0.071 | 0.397 | [5 empty] | 26.1 |  |  |  |  | 52.2 |  | 23.8 |  | 6.9 | 0.069 |  | 12.5 | 63.17 | 0.7 |  |  |  |  | 13.943 | 13.112 | [6 empty] | 29.67 | 5.6 | 8.5
2009-06-07 | 6.4 | 5.04 |  |  |  |  | 7.65 | 1.57 |  |  |  |  | 32 |  |  |  | 0 | 0.482 |  |  | 0.062 | 0.267 | [5 empty] | 27 |  |  |  |  | 54.1 |  | 22.5 |  | 6.9 | 0.059 |  | 12.7 | 62.09 | 0.84 |  |  |  |  | 12.537 | 11.677 | [6 empty] | 29.07 | 5.6 | 8.5
2009-06-08 | 6.445 | 5.06 |  |  |  |  | 7.795 | 1.53 |  |  |  |  | 33 |  |  |  | 0 | 0.4955 |  |  | 0.0665 | 0.332 | [5 empty] | 26.55 |  |  |  |  | 53.15 |  | 23.15 |  | 6.9 | 0.064 |  | 12.6 | 62.63 | 0.77 |  |  |  |  | 13.24 | 12.3945 | [6 empty] | 29.37 | 5.6 | 8.5
2009-06-09 | 6.4225 | 5.05 |  |  |  |  | 7.7225 | 1.55 |  |  |  |  | 32.5 |  |  |  | 0 | 0.48875 |  |  | 0.06425 | 0.2995 | [5 empty] | 26.775 |  |  |  |  | 53.625 |  | 22.825 |  | 6.9 | 0.0615 |  | 12.65 | 62.36 | 0.805 |  |  |  |  | 12.8885 | 12.0358 | [6 empty] | 29.22 | 5.6 | 8.5
2009-06-10 | 6.01 | 5.13 |  |  |  |  | 7.63 | 1.61 |  |  |  |  | 34 |  |  |  | 0 | 0.497 |  |  | 0.069 | 0.198 | [5 empty] | 25.1 |  |  |  |  | 50.2 |  | 23.3 |  | 7 | 0.061 |  | 12.6 | 66.02 | 0.75 |  |  |  |  | 13.03 | 12.675 | [6 empty] | 29.295 | 5.6 | 8.5
2009-06-11 | 6.09 | 5.2 |  |  |  |  | 7.59 | 1.54 |  |  |  |  | 33 |  |  |  | 0 | 0.654 |  |  | 0.073 | 1.89 | [5 empty] | 26.3 |  |  |  |  | 52.6 |  | 22.9 |  | 6.8 | 0.067 |  | 12.7 | 82.89 | 1.34 |  |  |  |  | 13.334 | 12.985 | [6 empty] | 29.79 | 5.6 | 8.5
2009-06-12 | 6.07 | 5.16 |  |  |  |  | 7.9 | 1.6 |  |  |  |  | 33 |  |  |  | 0 | 0.554 |  |  | 0.082 | 0.291 | [5 empty] | 25.7 |  |  |  |  | 51.4 |  | 21.7 |  | 6.8 | 0.072 |  | 12.8 | 48.258 | 0.19 |  |  |  |  | 13.758 | 12.172 | [6 empty] | 30.41 | 5.6 | 8.5
2009-06-13 | 6.25 | 5.12 |  |  |  |  | 7.58 | 1.62 |  |  |  |  | 37 |  |  |  | 0 | 0.509 |  |  | 0.074 | 0.391 | [5 empty] | 26.2 |  |  |  |  | 52.4 |  | 22 |  | 7.3 | 0.068 |  | 13.3 | 62.58 | 0.74 |  |  |  |  | 12.917 | 12.058 | [6 empty] | 30.01 | 5.6 | 8.3
2009-06-14 | 5.89 | 4.96 |  |  |  |  | 6.83 | 1.62 |  |  |  |  | 39 |  |  |  | 0 | 0.547 |  |  | 0.079 | 0.227 | [5 empty] | 25.8 |  |  |  |  | 51.6 |  | 22.3 |  | 6.8 | 0.078 |  | 13.8 | 62.18 | 0.91 |  |  |  |  | 11.97 | 11.18 | [6 empty] | 30.27 | 5.6 | 8.5
2009-06-15 | 5.925 | 5.07 |  |  |  |  | 7.12 | 1.59 |  |  |  |  | 39 |  |  |  | 0 | 0.592 |  |  | 0.075 | 0.2125 | [5 empty] | 26 |  |  |  |  | 52 |  | 22.5 |  | 6.75 | 0.081 |  | 13.85 | 59.16 | 0.96 |  |  |  |  | 11.564 | 10.62 | [6 empty] | 30.14 | 5.8 | 8.7
2009-06-16 | 5.96 | 5.18 |  |  |  |  | 7.41 | 1.56 |  |  |  |  | 39 |  |  |  | 0 | 0.637 |  |  | 0.071 | 0.198 | [5 empty] | 26.2 |  |  |  |  | 52.4 |  | 22.7 |  | 6.7 | 0.084 |  | 13.9 | 71.4 | 1.05 |  |  |  |  | 15.008 | 12.42 | [6 empty] | 30.57 | 5.8 | 8.7
2009-06-17 | 6.07 | 5.13 |  |  |  |  | 7.71 | 1.52 |  |  |  |  | 32 |  |  |  | 0 | 0.497 |  |  | 0.084 | 0.211 | [5 empty] | 25.7 |  |  |  |  | 51.4 |  | 22.4 |  | 6.9 | 0.074 |  | 13.9 | 65.99 | 1.16 |  |  |  |  | 14.051 | 11.167 | [6 empty] | 30.47 | 5.8 | 8.7
2009-06-18 | 6.12 | 5.11 |  |  |  |  | 7.55 | 1.6 |  |  |  |  | 30 |  |  |  | 0 | 0.4169 |  |  | 0.332 | 0.183 | [5 empty] | 26.25 |  |  |  |  | 52.5 |  | 22.15 |  | 6.9 | 0.0715 |  | 13.15 | 66.555 | 1.045 |  |  |  |  | 12.957 | 11.17 | [6 empty] | 31.505 | 5.8 | 8.7
2009-06-19 | 6.17 | 5 |  |  |  |  | 7.02 | 1.39 |  |  |  |  | 28 |  |  |  | 0 | 0.747 |  |  | 0.58 | 0.212 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 21.9 |  | 6.9 | 0.069 |  | 12.4 | 67.12 | 0.93 |  |  |  |  | 13.12 | 13.12 | [6 empty] | 32.54 | 5.8 | 8.7
2009-06-20 | 6.45 | 5.04 |  |  |  |  | 7.2 | 1.37 |  |  |  |  | 27 |  |  |  | 0 | 0.588 |  |  | 0.124 | 0.233 | [5 empty] | 27 |  |  |  |  | 54 |  | 21.6 |  | 7 | 0.072 |  | 13.3 | 66.52 | 1.19 |  |  |  |  | 12.657 | 11.814 | [6 empty] | 29.57 | 5.8 | 8.7
2009-06-21 | 6.13 | 5.03 |  |  |  |  | 7.6 | 1.4 |  |  |  |  | 27 |  |  |  | 0 | 0.631 |  |  | 0.068 | 0.212 | [5 empty] | 26.3 |  |  |  |  | 52.6 |  | 23.3 |  | 6.4 | 0.057 |  | 13.2 | 66.98 | 1.07 |  |  |  |  | 13.1 | 12.31 | [6 empty] | 29.57 | 5.8 | 8.7
2009-06-22 | 6.075 | 5.03 |  |  |  |  | 7.515 | 1.475 |  |  |  |  | 28 |  |  |  | 0 | 0.574 |  |  | 0.0705 | 0.2345 | [5 empty] | 25.9 |  |  |  |  | 51.8 |  | 23.55 |  | 6.55 | 0.0605 |  | 13.95 | 72.605 | 1.075 |  |  |  |  | 12.8785 | 12.062 | [6 empty] | 30.15 | 5.8 | 8.7
2009-06-23 | 6.02 | 5.03 |  |  |  |  | 7.43 | 1.55 |  |  |  |  | 29 |  |  |  | 0 | 0.517 |  |  | 0.073 | 0.257 | [5 empty] | 25.5 |  |  |  |  | 51 |  | 23.8 |  | 6.7 | 0.064 |  | 14.7 | 78.23 | 1.08 |  |  |  |  | 16.152 | 13.513 | [6 empty] | 30.73 | 5.8 | 8.7
2009-06-24 | 6.04 | 5.03 |  |  |  |  | 7.39 | 1.63 |  |  |  |  | 31 |  |  |  | 0 | 0.533 |  |  | 0.074 | 0.444 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 21.9 |  | 7.1 | 0.068 |  | 14.5 | 74.97 | 0.78 |  |  |  |  | 14 | 14.12 | [6 empty] | 29.34 | 5.8 | 8.7
2009-06-25 | 5.86 | 5.06 |  |  |  |  | 7.5 | 1.62 |  |  |  |  | 36 |  |  |  | 0 | 0.525 |  |  | 0.068 | 0.359 | [5 empty] | 27 |  |  |  |  | 54 |  | 21.7 |  | 7.2 | 0.044 |  | 14.6 | 69.26 | 0.91 |  |  |  |  | 13.311 | 12.441 | [6 empty] | 25.82 | 5.8 | 8.5
2009-06-26 | 5.8 | 4.78 |  |  |  |  | 7.34 | 1.78 |  |  |  |  | 27 |  |  |  | 0 | 0.545 |  |  | 0.067 | 0.193 | [5 empty] | 26.4 |  |  |  |  | 52.8 |  | 22.9 |  | 7.3 | 0.117 |  | 14.4 | 66.59 | 0.71 |  |  |  |  | 13.02 | 12.147 | [6 empty] | 29.57 | 6 | 8.2
2009-06-27 | 5.96 | 4.79 |  |  |  |  | 7.45 | 1.81 |  |  |  |  | 26 |  |  |  | 0 | 0.496 |  |  | 0.051 | 0.257 | [5 empty] | 26.7 |  |  |  |  | 53.4 |  | 23.3 |  | 6.9 | 0.098 |  | 14.5 | 63.22 | 0.68 |  |  |  |  | 12.414 | 11.524 | [6 empty] | 29.75 | 6 | 8.2
2009-06-28 | 5.95 | 4.84 |  |  |  |  | 7.39 | 1.81 |  |  |  |  | 30 |  |  |  | 0 | 0.581 |  |  | 0.059 | 0.247 | [5 empty] | 25.9 |  |  |  |  | 51.8 |  | 23.2 |  | 6.9 | 0.101 |  | 14.4 | 68.36 | 0.69 |  |  |  |  | 13.28 | 12.41 | [6 empty] | 29.54 | 6 | 8.2
2009-06-29 | 6.3 | 4.74 |  |  |  |  | 7.71 | 1.7 |  |  |  |  | 26 |  |  |  | 0 | 0.506 |  |  | 0.058 | 0.255 | [5 empty] | 25 |  |  |  |  | 50 |  | 23.9 |  | 7.5 | 0.098 |  | 14.4 | 73.98 | 0.96 |  |  |  |  | 12.847 | 11.967 | [6 empty] | 26.76 | 6 | 8.2
2009-06-30 | 6.065 | 4.765 |  |  |  |  | 7.46 | 1.59 |  |  |  |  | 26 |  |  |  | 0 | 0.5125 |  |  | 0.057 | 0.2765 | [5 empty] | 25.75 |  |  |  |  | 51.5 |  | 22.8 |  | 7.6 | 0.1075 |  | 14.45 | 73.71 | 0.955 |  |  |  |  | 14.359 | 12.625 | [6 empty] | 27.465 | 6 | 8.2
2009-07-01 | 5.83 | 4.79 |  |  |  |  | 7.21 | 1.48 |  |  |  |  | 26 |  |  |  | 0 | 0.519 |  |  | 0.056 | 0.298 | [5 empty] | 26.5 |  |  |  |  | 53 |  | 21.7 |  | 7.7 | 0.117 |  | 14.5 | 73.44 | 0.95 |  |  |  |  | 14.562 | 13.727 | [6 empty] | 28.17 | 6 | 8.2
2009-07-02 | 5.9475 | 4.7775 |  |  |  |  | 7.335 | 1.535 |  |  |  |  | 26 |  |  |  | 0 | 0.51575 |  |  | 0.0565 | 0.28725 | [5 empty] | 26.125 |  |  |  |  | 52.25 |  | 22.25 |  | 7.65 | 0.11225 |  | 14.475 | 73.575 | 0.9525 |  |  |  |  | 14.4605 | 13.176 | [6 empty] | 27.8175 | 6 | 8.2
2009-07-03 | 5.8887 | 4.7837 |  |  |  |  | 7.2725 | 1.5075 |  |  |  |  | 26 |  |  |  | 0 | 0.51737 |  |  | 0.05625 | 0.29263 | [5 empty] | 26.3125 |  |  |  |  | 52.625 |  | 21.975 |  | 7.675 | 0.11463 |  | 14.4875 | 73.5075 | 0.95125 |  |  |  |  | 14.5113 | 13.4515 | [6 empty] | 27.9938 | 6 | 8.2
2009-07-04 | 5.87 | 4.67 |  |  |  |  | 7.29 | 1.47 |  |  |  |  | 28 |  |  |  | 0 | 0.522 |  |  | 0.065 | 0.178 | [5 empty] | 23.6 |  |  |  |  | 47.2 |  | 21.9 |  | 6.7 | 0.087 |  | 15.6 | 73.49 | 0.98 |  |  |  |  | 14.435 | 13.593 | [6 empty] | 27.1 | 6 | 7.9
2009-07-05 | 5.99 | 5.01 |  |  |  |  | 7.67 | 1.24 |  |  |  |  | 26 |  |  |  | 0 | 0.528 |  |  | 0.06 | 0.115 | [5 empty] | 25.3 |  |  |  |  | 50.6 |  | 21.7 |  | 6.8 | 0.073 |  | 15.9 | 73.4988 | 0.96562 |  |  |  |  | 13.57 | 12.61 | [6 empty] | 29.74 | 6 | 8.1
2009-07-06 | 5.93 | 4.84 |  |  |  |  | 7.48 | 1.355 |  |  |  |  | 27 |  |  |  | 0 | 0.525 |  |  | 0.0625 | 0.1465 | [5 empty] | 24.45 |  |  |  |  | 48.9 |  | 21.8 |  | 6.75 | 0.08 |  | 15.75 | 73.4944 | 0.97281 |  |  |  |  | 14.0025 | 13.1015 | [6 empty] | 28.42 | 6 | 8
2009-07-07 | 5.96 | 4.925 |  |  |  |  | 7.575 | 1.2975 |  |  |  |  | 26.5 |  |  |  | 0 | 0.5265 |  |  | 0.06125 | 0.13075 | [5 empty] | 24.875 |  |  |  |  | 49.75 |  | 21.75 |  | 6.775 | 0.0765 |  | 15.825 | 73.4966 | 0.96922 |  |  |  |  | 13.7863 | 12.8558 | [6 empty] | 29.08 | 6 | 8.05
2009-07-08 | 5.945 | 4.8825 |  |  |  |  | 7.5275 | 1.3262 |  |  |  |  | 26.75 |  |  |  | 0 | 0.52575 |  |  | 0.061875 | 0.13862 | [5 empty] | 24.6625 |  |  |  |  | 49.325 |  | 21.775 |  | 6.7625 | 0.07825 |  | 15.7875 | 73.4955 | 0.97102 |  |  |  |  | 13.8944 | 12.9786 | [6 empty] | 28.75 | 6 | 8.025
2009-07-09 | 5.88 | 4.99 |  |  |  |  | 6.7 | 1.4 |  |  |  |  | 27 |  |  |  | 1 | 0.54 |  |  | 0.079 | 0.153 | [5 empty] | 21.7 |  |  |  |  | 43.4 |  | 21.9 |  | 6.5 | 0.078 |  | 15.4 | 60.16 | 0.58 |  |  |  |  | 14.592 | 13.825 | [6 empty] | 26.44 | 6 | 8.0375
2009-07-10 | 5.8 | 4.98 |  |  |  |  | 8.11 | 1.42 |  |  |  |  | 26 |  |  |  | 0 | 0.578 |  |  | 0.059 | 0.151 | [5 empty] | 23.2 |  |  |  |  | 46.4 |  | 22.3 |  | 6.8 | 0.069 |  | 15.6 | 61.74 | 0.56 |  |  |  |  | 15.05 | 14.15 | [6 empty] | 28.05 | 6 | 7.2
2009-07-11 | 6.45 | 4.97 |  |  |  |  | 7.38 | 1.34 |  |  |  |  | 25 |  |  |  | 0 | 0.591 |  |  | 0.056 | 0.17 | [5 empty] | 25.3 |  |  |  |  | 50.6 |  | 21.9 |  | 6.6 | 0.059 |  | 16.1 | 55.83 | 0.53 |  |  |  |  | 14.294 | 13.434 | [6 empty] | 28.17 | 6 | 7.2
2009-07-12 | 6.02 | 4.96 |  |  |  |  | 7.47 | 1.6 |  |  |  |  | 26 |  |  |  | 0 | 0.598 |  |  | 0.067 | 0.156 | [5 empty] | 24.8 |  |  |  |  | 49.6 |  | 24.6 |  | 6.8 | 0.079 |  | 16.2 | 60.24 | 0.79 |  |  |  |  | 12.426 | 11.462 | [6 empty] | 27.7 | 6 | 7.2
2009-07-13 | 6.19 | 4.61 |  |  |  |  | 7.13 | 1.32 |  |  |  |  | 28 |  |  |  | 0 | 0.436 |  |  | 0.072 | 0.164 | [5 empty] | 28.6 |  |  |  |  | 57.2 |  | 24.1 |  | 6.7 | 0.081 |  | 16.3 | 58.19 | 0.71 |  |  |  |  | 13.36 | 12.448 | [6 empty] | 25.33 | 6 | 7.2
2009-07-14 | 6.145 | 4.855 |  |  |  |  | 7.46 | 1.3 |  |  |  |  | 27 |  |  |  | 0 | 0.2235 |  |  | 0.0685 | 0.1935 | [5 empty] | 29.2 |  |  |  |  | 58.4 |  | 24.25 |  | 7.05 | 0.0775 |  | 21.05 | 58.865 | 0.62 |  |  |  |  | 14.655 | 13.025 | [6 empty] | 25.205 | 6 | 7.1
2009-07-15 | 6.1 | 5.1 |  |  |  |  | 7.79 | 1.28 |  |  |  |  | 26 |  |  |  | 0 | 0.011 |  |  | 0.065 | 0.223 | [5 empty] | 29.8 |  |  |  |  | 59.6 |  | 24.4 |  | 7.4 | 0.074 |  | 25.8 | 59.54 | 0.53 |  |  |  |  | 15.78 | 14.97 | [6 empty] | 25.08 | 6 | 7
2009-07-16 | 6.38 | 5.38 |  |  |  |  | 7.95 | 1.29 |  |  |  |  | 24 |  |  |  | 0 | 0.584 |  |  | 0.064 | 0.21 | [5 empty] | 24 |  |  |  |  | 48 |  | 23.9 |  | 6.8 | 0.03 |  | 16.8 | 61.61 | 0.56 |  |  |  |  | 15.969 | 15.13 | [6 empty] | 24.88 | 5.8 | 6.3
2009-07-17 | 5.6 | 5.25 |  |  |  |  | 7.22 | 1.35 |  |  |  |  | 25 |  |  |  | 0 | 0.512 |  |  | 0.06 | 0.186 | [5 empty] | 24.3 |  |  |  |  | 48.6 |  | 22.7 |  | 7.1 | 0.044 |  | 17.5 | 55.63 | 0.19 |  |  |  |  | 17.49 | 16.36 | [6 empty] | 25.82 | 5.8 | 6.6
2009-07-18 | 6.56 | 5.39 |  |  |  |  | 7.17 | 2.06 |  |  |  |  | 26 |  |  |  | 0 | 0.547 |  |  | 0.064 | 0.217 | [5 empty] | 36.7 |  |  |  |  | 73.4 |  | 21.7 |  | 7.4 | 0.051 |  | 18 | 75.79 | 0.21 |  |  |  |  | 17.684 | 15.186 | [6 empty] | 27.92 | 5.8 | 6.6
2009-07-19 | 5.98 | 4.96 |  |  |  |  | 6.69 | 2.04 |  |  |  |  | 27 |  |  |  | 0 | 0.746 |  |  | 0.069 | 0.158 | [5 empty] | 23.9 |  |  |  |  | 47.8 |  | 22.7 |  | 6.7 | 0.042 |  | 17.1 | 86 | 0.85 |  |  |  |  | 14.28 | 13.51 | [6 empty] | 27.92 | 5.5 | 6.7
2009-07-20 | 6.05 | 4.935 |  |  |  |  | 6.81 | 2.155 |  |  |  |  | 25 |  |  |  | 0 | 0.644 |  |  | 0.0665 | 0.167 | [5 empty] | 24.65 |  |  |  |  | 49.3 |  | 22.35 |  | 6.45 | 0.0325 |  | 16.3 | 87.42 | 0.805 |  |  |  |  | 15.982 | 14.348 | [6 empty] | 28.745 | 5.65 | 7.05
2009-07-21 | 6.12 | 4.91 |  |  |  |  | 6.93 | 2.27 |  |  |  |  | 23 |  |  |  | 0 | 0.542 |  |  | 0.064 | 0.176 | [5 empty] | 25.4 |  |  |  |  | 50.8 |  | 22 |  | 6.2 | 0.023 |  | 15.5 | 88.84 | 0.76 |  |  |  |  | 14.644 | 13.294 | [6 empty] | 29.57 | 5.8 | 7.4
2009-07-22 | 6.11 | 4.78 |  |  |  |  | 7.46 | 2.18 |  |  |  |  | 27 |  |  |  | 0 | 0.532 |  |  | 0.061 | 0.542 | [5 empty] | 26.4 |  |  |  |  | 52.8 |  | 22.7 |  | 6.8 | 0.048 |  | 15.1 | 78.19 | 0.63 |  |  |  |  | 13.076 | 12.621 | [6 empty] | 29.34 | 5.8 | 7.7
2009-07-23 | 6.09 | 4.97 |  |  |  |  | 7.25 | 2.01 |  |  |  |  | 26 |  |  |  | 0 | 0.529 |  |  | 0.067 | 0.146 | [5 empty] | 27 |  |  |  |  | 54.1 |  | 23.1 |  | 6.5 | 0.064 |  | 15.1 | 88.95 | 1.03 |  |  |  |  | 14.561 | 13.266 | [6 empty] | 30.23 | 5.8 | 7.7
2009-07-24 | 6.01 | 4.88 |  |  |  |  | 6.44 | 1.96 |  |  |  |  | 30 |  |  |  | 0 | 0.491 |  |  | 0.074 | 0.098 | [5 empty] | 26.6 |  |  |  |  | 53.2 |  | 23.8 |  | 6 | 0.051 |  | 15.2 | 77.42 | 0.76 |  |  |  |  | 13.357 | 12.933 | [6 empty] | 29.74 | 5.8 | 7.7
2009-07-25 | 6.14 | 4.86 |  |  |  |  | 7.1 | 1.83 |  |  |  |  | 27 |  |  |  | 0 | 0.716 |  |  | 0.074 | 0.341 | [5 empty] | 26.9 |  |  |  |  | 53.8 |  | 23.6 |  | 6.4 | 0.057 |  | 13.7 | 78.21 | 1.25 |  |  |  |  | 13.312 | 11.539 | [6 empty] | 33.84 | 5.8 | 7.7
2009-07-26 | 6.21 | 4.78 |  |  |  |  | 6.8 | 1.8 |  |  |  |  | 41 |  |  |  | 0 | 0.62 |  |  | 0.059 | 0.438 | [5 empty] | 21 |  |  |  |  | 42 |  | 21.8 |  | 6.5 | 0.048 |  | 13 | 74.31 | 1.07 |  |  |  |  | 12.63 | 11.74 | [6 empty] | 30.35 | 5.8 | 7.7
2009-07-27 | 6.19 | 4.845 |  |  |  |  | 6.975 | 1.78 |  |  |  |  | 39 |  |  |  | 0 | 0.5955 |  |  | 0.069 | 0.3575 | [5 empty] | 22.55 |  |  |  |  | 45.1 |  | 21.9 |  | 6.6 | 0.051 |  | 13.1 | 79.8 | 1.05 |  |  |  |  | 13.671 | 12.798 | [6 empty] | 30.285 | 5.8 | 8.1
2009-07-28 | 6.17 | 4.91 |  |  |  |  | 7.15 | 1.8 |  |  |  |  | 37 |  |  |  | 0 | 0.571 |  |  | 0.079 | 0.277 | [5 empty] | 24.1 |  |  |  |  | 48.2 |  | 22 |  | 6.7 | 0.054 |  | 13.2 | 83.19 | 1.02 |  |  |  |  | 14.225 | 13.384 | [6 empty] | 30.22 | 5.8 | 8.1
2009-07-29 | 6.04 | 4.9 |  |  |  |  | 7.07 | 1.77 |  |  |  |  | 38 |  |  |  | 0 | 0.617 |  |  | 0.081 | 0.201 | [5 empty] | 26.3 |  |  |  |  | 52.6 |  | 22.6 |  | 7.4 | 0.079 |  | 13.3 | 81.72 | 1.05 |  |  |  |  | 14.002 | 13.137 | [6 empty] | 29.75 | 5.8 | 8.1
2009-07-30 | 6.23 | 4.89 |  |  |  |  | 6.92 | 1.75 |  |  |  |  | 39 |  |  |  | 0 | 0.581 |  |  | 0.071 | 0.191 | [5 empty] | 26.2 |  |  |  |  | 52.4 |  | 22.9 |  | 7.1 | 0.063 |  | 14.8 | 81.25 | 1.22 |  |  |  |  | 15.24 | 12.436 | [6 empty] | 33.53 | 5.8 | 8.1
2009-07-31 | 6.12 | 4.75 |  |  |  |  | 5.82 | 1.45 |  |  |  |  | 38 |  |  |  | 0 | 0.631 |  |  | 0.097 | 0.622 | [5 empty] | 21.4 |  |  |  |  | 42.8 |  | 22.4 |  | 5.8 | 0.093 |  | 16.2 | 81.59 | 1.48 |  |  |  |  | 16.06 | 12.64 | [6 empty] | 33.95 | 6 | 8.4
2009-08-01 | 6.6 | 5 |  |  |  |  | 7.28 | 1.84 |  |  |  |  | 33 |  |  |  | 0 | 0.608 |  |  | 0.06 | 0.198 | [5 empty] | 28 |  |  |  |  | 56 |  | 22.6 |  | 7.5 | 0.144 |  | 15.4 | 77.18 | 0.77 |  |  |  |  | 13.36 | 13.4 | [6 empty] | 30.98 | 6 | 9
2009-08-02 | 6.21 | 5.01 |  |  |  |  | 7.48 | 1.97 |  |  |  |  | 34 |  |  |  | 0 | 0.588 |  |  | 0.065 | 0.179 | [5 empty] | 27 |  |  |  |  | 54.1 |  | 23.6 |  | 7.3 | 0.123 |  | 15.4 | 72.99 | 0.79 |  |  |  |  | 12.91 | 11.99 | [6 empty] | 30.04 | 6 | 9
2009-08-03 | 6.195 | 4.88 |  |  |  |  | 7.46 | 1.93 |  |  |  |  | 32.5 |  |  |  | 0 | 0.6125 |  |  | 0.0745 | 0.181 | [5 empty] | 27.8 |  |  |  |  | 55.65 |  | 23.55 |  | 7 | 0.1195 |  | 15.45 | 74.07 | 0.9 |  |  |  |  | 12.838 | 11.87 | [6 empty] | 30.075 | 6 | 9
2009-08-04 | 6.18 | 4.75 |  |  |  |  | 7.44 | 1.71 |  |  |  |  | 31 |  |  |  | 0 | 0.637 |  |  | 0.084 | 0.183 | [5 empty] | 28.6 |  |  |  |  | 57.2 |  | 23.5 |  | 6.7 | 0.116 |  | 15.5 | 85.07 | 1.15 |  |  |  |  | 14.288 | 13.495 | [6 empty] | 30.11 | 6 | 9
2009-08-05 | 6.12 | 4.7 |  |  |  |  | 7.76 | 1.74 |  |  |  |  | 33 |  |  |  | 0 | 0.597 |  |  | 0.076 | 0.154 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 23.9 |  | 6.4 | 0.092 |  | 15.5 | 86 | 1.05 |  |  |  |  | 14.77 | 13.98 | [6 empty] | 29.7 | 6 | 8.8
2009-08-06 | 6.13 | 4.74 |  |  |  |  | 7.7 | 1.83 |  |  |  |  | 29 |  |  |  | 0 | 0.576 |  |  | 0.06 | 0.147 | [5 empty] | 26.8 |  |  |  |  | 53.8 |  | 24.8 |  | 7.6 | 0.071 |  | 17.6 | 81.59 | 0.96 |  |  |  |  | 14.17 | 13.28 | [6 empty] | 29.11 | 6.2 | 8.8
2009-08-07 | 6.03 | 4.99 |  |  |  |  | 7.86 | 1.9 |  |  |  |  | 30 |  |  |  | 0 | 0.596 |  |  | 0.075 | 0.152 | [5 empty] | 27.5 |  |  |  |  | 55.1 |  | 21.8 |  | 7.4 | 0.068 |  | 18 | 81.78 | 0.96 |  |  |  |  | 13.832 | 12.961 | [6 empty] | 27.7 | 6.2 | 8.8
2009-08-08 | 6.06 | 4.82 |  |  |  |  | 6.45 | 1.89 |  |  |  |  | 31 |  |  |  | 0 | 0.577 |  |  | 0.083 | 0.179 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 22.2 |  | 6.4 | 0.095 |  | 18.1 | 87.03 | 1.01 |  |  |  |  | 14.429 | 13.64 | [6 empty] | 27.99 | 6.5 | 8.8
2009-08-09 | 6.12 | 4.89 |  |  |  |  | 7.67 | 1.98 |  |  |  |  | 25 |  |  |  | 0 | 0.551 |  |  | 0.101 | 0.337 | [5 empty] | 27.7 |  |  |  |  | 55.4 |  | 22.3 |  | 6.7 | 0.0815 |  | 18.1 | 79.38 | 0.94 |  |  |  |  | 13.27 | 12.36 | [6 empty] | 27.03 | 6.5 | 8.8
2009-08-10 | 5.875 | 4.865 |  |  |  |  | 7.565 | 1.995 |  |  |  |  | 26.5 |  |  |  | 0 | 0.557 |  |  | 0.084 | 0.2475 | [5 empty] | 27.65 |  |  |  |  | 55.35 |  | 22.45 |  | 6.95 | 0.08825 |  | 18.05 | 78.28 | 0.915 |  |  |  |  | 13.8495 | 13 | [6 empty] | 28.07 | 6.5 | 8.8
2009-08-11 | 5.63 | 4.84 |  |  |  |  | 7.46 | 2.01 |  |  |  |  | 28 |  |  |  | 0 | 0.563 |  |  | 0.067 | 0.158 | [5 empty] | 27.6 |  |  |  |  | 55.3 |  | 22.6 |  | 7.2 | 0.07 |  | 18 | 77.18 | 0.89 |  |  |  |  | 12.96 | 12.09 | [6 empty] | 29.11 | 6.5 | 8.8
2009-08-12 | 6.05 | 4.66 |  |  |  |  | 7.19 | 1.85 |  |  |  |  | 26 |  |  |  | 0 | 0.538 |  |  | 0.067 | 0.444 | [5 empty] | 27.8 |  |  |  |  | 55.7 |  | 24.4 |  | 7.1 | 0.075 |  | 16.9 | 87.19 | 1.12 |  |  |  |  | 14.682 | 13.322 | [6 empty] | 29.34 | 6.5 | 8.8
2009-08-13 | 6 | 4.74 |  |  |  |  | 8.01 | 1.86 |  |  |  |  | 22 |  |  |  | 0 | 0.554 |  |  | 0.079 | 0.176 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 23.6 |  | 6.9 | 0.068 |  | 16.9 | 82.62 | 1.04 |  |  |  |  | 13.807 | 12.925 | [6 empty] | 29.67 | 6.5 | 8.6
2009-08-14 | 6.07 | 4.77 |  |  |  |  | 7.6 | 1.77 |  |  |  |  | 31 |  |  |  | 0 | 0.542 |  |  | 0.092 | 0.157 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 24.5 |  | 7.4 | 0.084 |  | 17 | 76.43 | 0.92 |  |  |  |  | 13.321 | 12.894 | [6 empty] | 29.86 | 6.5 | 8.6
2009-08-15 | 6.03 | 4.77 |  |  |  |  | 7.8 | 1.74 |  |  |  |  | 31 |  |  |  | 0 | 0.576 |  |  | 0.102 | 0.308 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 23.4 |  | 6.9 | 0.124 |  | 16.9 | 85.73 | 1.26 |  |  |  |  | 14.668 | 12.958 | [6 empty] | 29.63 | 6.5 | 8.6
2009-08-16 | 5.98 | 4.74 |  |  |  |  | 7.79 | 1.84 |  |  |  |  | 28 |  |  |  | 0 | 0.559 |  |  | 0.107 | 0.292 | [5 empty] | 26.2 |  |  |  |  | 52.4 |  | 25.1 |  | 6.7 | 0.117 |  | 17 | 81.92 | 1.03 |  |  |  |  | 13.54 | 12.96 | [6 empty] | 28.79 | 6.5 | 8.6
2009-08-17 | 5.91 | 4.74 |  |  |  |  | 7.885 | 1.84 |  |  |  |  | 30.5 |  |  |  | 0 | 0.5675 |  |  | 0.0875 | 0.245 | [5 empty] | 27.45 |  |  |  |  | 54.9 |  | 23.85 |  | 7.05 | 0.0925 |  | 17.8 | 84.63 | 0.99 |  |  |  |  | 14.081 | 13.475 | [6 empty] | 30.08 | 6.5 | 8.6
2009-08-18 | 5.84 | 4.74 |  |  |  |  | 7.98 | 1.79 |  |  |  |  | 33 |  |  |  | 0 | 0.567 |  |  | 0.068 | 0.198 | [5 empty] | 28.7 |  |  |  |  | 57.4 |  | 22.6 |  | 7.4 | 0.068 |  | 18.6 | 96.03 | 1.27 |  |  |  |  | 15.967 | 14.242 | [6 empty] | 31.37 | 6.5 | 8.6
2009-08-19 | 5.93 | 5.01 |  |  |  |  | 7.64 | 1.86 |  |  |  |  | 32 |  |  |  | 0 | 0.574 |  |  | 0.184 | 0.197 | [5 empty] | 29.1 |  |  |  |  | 58.2 |  | 22.4 |  | 6.9 | 0.094 |  | 18.8 | 99.25 | 1.02 |  |  |  |  | 16.16 | 15.664 | [6 empty] | 30.7 | 6.5 | 8.6
2009-08-20 | 6.24 | 4.95 |  |  |  |  | 7.26 | 2 |  |  |  |  | 34 |  |  |  | 0 | 0.547 |  |  | 0.193 | 0.337 | [5 empty] | 29.3 |  |  |  |  | 58.6 |  | 23.2 |  | 7.3 | 0.098 |  | 19.7 | 107.65 | 1.4 |  |  |  |  | 16.417 | 14.366 | [6 empty] | 31.09 | 6.3 | 8.6
2009-08-21 | 6.01 | 5.02 |  |  |  |  | 7.43 | 1.96 |  |  |  |  | 32 |  |  |  | 0 | 0.542 |  |  | 0.072 | 0.203 | [5 empty] | 26.7 |  |  |  |  | 53.4 |  | 22.8 |  | 7.6 | 0.078 |  | 19.2 | 99.23 | 1.08 |  |  |  |  | 15.73 | 14.84 | [6 empty] | 29.69 | 6.1 | 7.8
2009-08-22 | 6.23 | 5.19 |  |  |  |  | 7.74 | 2.12 |  |  |  |  | 29 |  |  |  | 0 | 0.578 |  |  | 0.102 | 0.204 | [5 empty] | 27.6 |  |  |  |  | 55.3 |  | 23.1 |  | 7 | 0.082 |  | 19.1 | 101.45 | 1.07 |  |  |  |  | 15.314 | 14.441 | [6 empty] | 29.11 | 6.2 | 7.5
2009-08-23 | 6.22 | 5.04 |  |  |  |  | 6.97 | 1.71 |  |  |  |  | 28 |  |  |  | 0 | 0.585 |  |  | 0.074 | 0.154 | [5 empty] | 25.5 |  |  |  |  | 51.1 |  | 23.4 |  | 6.8 | 0.043 |  | 19.6 | 88.64 | 1.28 |  |  |  |  | 14.364 | 13.436 | [6 empty] | 29.34 | 5.8 | 7.5
2009-08-24 | 6.1 | 4.955 |  |  |  |  | 6.98 | 1.83 |  |  |  |  | 28.5 |  |  |  | 0 | 0.5765 |  |  | 0.0765 | 0.1555 | [5 empty] | 25.65 |  |  |  |  | 51.35 |  | 23.35 |  | 6.75 | 0.0495 |  | 20 | 72.755 | 1.175 |  |  |  |  | 14.839 | 13.9385 | [6 empty] | 29.445 | 5.8 | 7.5
2009-08-25 | 5.98 | 4.87 |  |  |  |  | 6.99 | 1.95 |  |  |  |  | 29 |  |  |  | 0 | 0.568 |  |  | 0.079 | 0.157 | [5 empty] | 25.8 |  |  |  |  | 51.6 |  | 23.3 |  | 6.7 | 0.056 |  | 20.4 | 56.87 | 1.2275 |  |  |  |  | 16.019 | 14.015 | [6 empty] | 29.55 | 5.8 | 7.5
2009-08-26 | 5.74 | 4.97 |  |  |  |  | 8.26 | 1.94 |  |  |  |  | 28 |  |  |  | 0 | 0.522 |  |  | 0.081 | 0.196 | [5 empty] | 25.6 |  |  |  |  | 51.2 |  | 22.5 |  | 7.6 | 0.047 |  | 20.8 | 92.61 | 1.01 |  |  |  |  | 15.25 | 14.26 | [6 empty] | 27.16 | 5.8 | 7.6
2009-08-27 | 6.23 | 4.74 |  |  |  |  | 6.91 | 1.92 |  |  |  |  | 27 |  |  |  | 0 | 0.548 |  |  | 0.11 | 0.245 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 23.5 |  | 7.4 | 0.056 |  | 20.4 | 89.63 | 1 |  |  |  |  | 14.806 | 13.994 | [6 empty] | 27.23 | 6 | 7.6
2009-08-28 | 6.18 | 4.71 |  |  |  |  | 7.12 | 1.88 |  |  |  |  | 26 |  |  |  | 0 | 0.523 |  |  | 0.101 | 0.199 | [5 empty] | 27.2 |  |  |  |  | 54.4 |  | 23.9 |  | 8.1 | 0.058 |  | 20.4 | 92.74 | 1.13 |  |  |  |  | 14.881 | 13.982 | [6 empty] | 26.76 | 6 | 7.6
2009-08-29 | 6.12 | 4.73 |  |  |  |  | 7.15 | 1.96 |  |  |  |  | 29 |  |  |  | 0 | 0.587 |  |  | 0.099 | 0.167 | [5 empty] | 28 |  |  |  |  | 56 |  | 22.9 |  | 7.4 | 0.067 |  | 20.5 | 86.22 | 1.01 |  |  |  |  | 14.197 | 13.19 | [6 empty] | 30.72 | 6.4 | 7.6
2009-08-30 | 6.04 | 4.73 |  |  |  |  | 6.65 | 1.96 |  |  |  |  | 30 |  |  |  | 0 | 0.537 |  |  | 0.092 | 0.146 | [5 empty] | 26.7 |  |  |  |  | 53.4 |  | 24.9 |  | 7.7 | 0.051 |  | 20.3 | 88.66 | 1.14 |  |  |  |  | 13.933 | 12.976 | [6 empty] | 30.12 | 6.4 | 7.6
2009-08-31 | 6.175 | 4.765 |  |  |  |  | 6.815 | 1.97 |  |  |  |  | 30.5 |  |  |  | 0 | 0.532 |  |  | 0.078 | 0.1655 | [5 empty] | 27.55 |  |  |  |  | 55.1 |  | 23.85 |  | 7.45 | 0.056 |  | 19.55 | 86.015 | 5.62 |  |  |  |  | 14.065 | 13.083 | [6 empty] | 31.49 | 6.4 | 7.8
2009-09-01 | 6.31 | 4.8 |  |  |  |  | 6.98 | 1.98 |  |  |  |  | 31 |  |  |  | 0 | 0.527 |  |  | 0.064 | 0.185 | [5 empty] | 28.4 |  |  |  |  | 56.8 |  | 22.8 |  | 7.2 | 0.061 |  | 18.8 | 83.37 | 10.1 |  |  |  |  | 13.548 | 12.638 | [6 empty] | 32.86 | 6.4 | 8
2009-09-02 | 5.91 | 4.86 |  |  |  |  | 7.27 | 2.19 |  |  |  |  | 27 |  |  |  | 0 | 0.529 |  |  | 0.076 | 0.14 | [5 empty] | 27.8 |  |  |  |  | 55.5 |  | 23.8 |  | 8 | 0.046 |  | 18.6 | 84.96 | 0.91 |  |  |  |  | 13.373 | 12.425 | [6 empty] | 30.75 | 6.4 | 7
2009-09-03 | 5.96 | 4.99 |  |  |  |  | 7.24 | 2.17 |  |  |  |  | 22 |  |  |  | 0 | 0.654 |  |  | 0.117 | 0.154 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 22.7 |  | 6.9 | 0.054 |  | 18.4 | 91 | 1.03 |  |  |  |  | 14.607 | 12.923 | [6 empty] | 30.19 | 6.8 | 7
2009-09-04 | 6.09 | 5.01 |  |  |  |  | 7.01 | 2.13 |  |  |  |  | 21 |  |  |  | 0 | 0.624 |  |  | 0.113 | 0.147 | [5 empty] | 26.9 |  |  |  |  | 53..8 |  | 24.6 |  | 7.5 | 0.069 |  | 18.4 | 83.7 | 0.71 |  |  |  |  | 14.104 | 13.393 | [6 empty] | 30.54 | 6.8 | 7
2009-09-05 | 5.99 | 5.02 |  |  |  |  | 6.85 | 2.1 |  |  |  |  | 24 |  |  |  | 0 | 0.516 |  |  | 0.059 | 0.147 | [5 empty] | 27.2 |  |  |  |  | 55.4 |  | 24.3 |  | 7.3 | 0.061 |  | 17.1 | 83.26 | 0.91 |  |  |  |  | 12.489 | 12.588 | [6 empty] | 30.27 | 6.8 | 7
2009-09-06 | 6.1 | 4.96 |  |  |  |  | 7 | 2.07 |  |  |  |  | 27 |  |  |  | 0 | 0.558 |  |  | 0.057 | 0.135 | [5 empty] | 26.6 |  |  |  |  | 53.2 |  | 23.4 |  | 7 | 0.068 |  | 16.2 | 82.62 | 0.89 |  |  |  |  | 13.64 | 12.69 | [6 empty] | 32.65 | 6.8 | 7
2009-09-07 | 6.085 | 4.995 |  |  |  |  | 7.1 | 2.03 |  |  |  |  | 27.5 |  |  |  | 0 | 0.566 |  |  | 0.054 | 0.1525 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 23.05 |  | 6.9 | 0.071 |  | 16.15 | 85.38 | 0.97 |  |  |  |  | 13.84 | 12.929 | [6 empty] | 31.955 | 6.9 | 7.3
2009-09-08 | 6.07 | 5.03 |  |  |  |  | 7.2 | 1.74 |  |  |  |  | 28 |  |  |  | 0 | 0.574 |  |  | 0.051 | 0.17 | [5 empty] | 27 |  |  |  |  | 54 |  | 22.7 |  | 6.8 | 0.074 |  | 16.1 | 87.19 | 1.19 |  |  |  |  | 14.485 | 13.512 | [6 empty] | 31.26 | 9.9 | 7.3
2009-09-09 | 6.1 | 5.01 |  |  |  |  | 7.03 | 1.69 |  |  |  |  | 33 |  |  |  | 0 | 0.615 |  |  | 0.051 | 0.197 | [5 empty] | 28.7 |  |  |  |  | 57.4 |  | 22.4 |  | 6.4 | 0.075 |  | 15.7 | 96.56 | 1.55 |  |  |  |  | 16.491 | 13.515 | [6 empty] | 30.88 | 6.9 | 7.3
2009-09-10 | 5.98 | 5.07 |  |  |  |  | 7.91 | 1.71 |  |  |  |  | 31 |  |  |  | 0 | 0.567 |  |  | 0.58 | 0.213 | [5 empty] | 27.3 |  |  |  |  | 54.6 |  | 23.4 |  | 6.9 | 0.079 |  | 15.3 | 92.41 | 1.33 |  |  |  |  | 16.157 | 13.81 | [6 empty] | 30.02 | 6.9 | 7.3
2009-09-11 | 6.16 | 5.06 |  |  |  |  | 6.96 | 1.73 |  |  |  |  | 26 |  |  |  | 0 | 0.563 |  |  | 0.059 | 0.139 | [5 empty] | 24.7 |  |  |  |  | 49.4 |  | 22.2 |  | 6.8 | 0.038 |  | 15.1 | 97.02 | 1.43 |  |  |  |  | 15.76 | 13.94 | [6 empty] | 30.71 | 6.9 | 7.1
2009-09-12 | 5.34 | 4.94 |  |  |  |  | 6.99 | 1.92 |  |  |  |  | 18 |  |  |  | 0 | 0.583 |  |  | 0.061 | 0.145 | [5 empty] | 26.9 |  |  |  |  | 53.8 |  | 22 |  | 6.8 | 0.011 |  | 15.7 | 90.41 | 0.95 |  |  |  |  | 14.32 | 14.32 | [6 empty] | 30.04 | 6.7 | 7.1
2009-09-13 | 5.66 | 4.7 |  |  |  |  | 6.48 | 1.86 |  |  |  |  | 26 |  |  |  | 0 | 0.556 |  |  | 0.056 | 0.23 | [5 empty] | 26.8 |  |  |  |  | 53.7 |  | 22.8 |  | 6.7 | 0.019 |  | 15.4 | 86.22 | 0.98 |  |  |  |  | 14.741 | 13.781 | [6 empty] | 30.04 | 6.7 | 7.4
2009-09-14 | 5.795 | 4.875 |  |  |  |  | 6.85 | 1.895 |  |  |  |  | 26.5 |  |  |  | 0 | 0.532 |  |  | 0.0545 | 0.1885 | [5 empty] | 26.8 |  |  |  |  | 53.65 |  | 22.35 |  | 6.75 | 0.0235 |  | 15.75 | 92.735 | 1.105 |  |  |  |  | 14.5305 | 14.0505 | [6 empty] | 30.7 | 6.7 | 7.4
2009-09-15 | 5.93 | 5.05 |  |  |  |  | 7.22 | 1.93 |  |  |  |  | 27 |  |  |  | 0 | 0.508 |  |  | 0.053 | 0.147 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 21.9 |  | 6.8 | 0.028 |  | 16.1 | 99.25 | 1.23 |  |  |  |  | 16.077 | 14.271 | [6 empty] | 31.36 | 6.7 | 7.4
2009-09-16 | 6.01 | 5.01 |  |  |  |  | 7.14 | 1.87 |  |  |  |  | 26 |  |  |  | 0 | 0.502 |  |  | 0.059 | 0.19 | [5 empty] | 27.7 |  |  |  |  | 55.4 |  | 24.9 |  | 6.5 | 0.027 |  | 15.7 | 85.6 | 0.96 |  |  |  |  | 14.56 | 13.72 | [6 empty] | 29.72 | 6.7 | 7.4
2009-09-17 | 6.47 | 4.89 |  |  |  |  | 7.12 | 1.73 |  |  |  |  | 21 |  |  |  | 0 | 0.535 |  |  | 0.06 | 0.144 | [5 empty] | 26.6 |  |  |  |  | 53.2 |  | 23.8 |  | 6.8 | 0.03 |  | 15.7 | 83.79 | 1.07 |  |  |  |  | 14.533 | 13.584 | [6 empty] | 30.04 | 6.8 | 7.6
2009-09-18 | 6.24 | 4.98 |  |  |  |  | 6.96 | 1.79 |  |  |  |  | 24 |  |  |  | 0 | 0.704 |  |  | 0.066 | 0.148 | [5 empty] | 26.4 |  |  |  |  | 52.9 |  | 22.9 |  | 6.7 | 0.034 |  | 15.6 | 88 | 1.09 |  |  |  |  | 14.794 | 13.825 | [6 empty] | 30.004 | 6.8 | 7.6
2009-09-19 | 6.355 | 4.95 |  |  |  |  | 6.92 | 1.82 |  |  |  |  | 24 |  |  |  | 0 | 0.58 |  |  | 0.059 | 0.5 | [5 empty] | 27.5 |  |  |  |  | 55 |  | 22.5 |  | 6.7 | 0.041 |  | 14.6 | 98.76 | 1.12 |  |  |  |  | 16.313 | 15.235 | [6 empty] | 30.27 | 6.8 | 7.6
2009-09-20 | 6.2975 | 5.03 |  |  |  |  | 7.4 | 1.86 |  |  |  |  | 20 |  |  |  | 0 | 0.567 |  |  | 0.081 | 0.137 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 22.7 |  | 6.5 | 0.037 |  | 14.5 | 93.05 | 1.01 |  |  |  |  | 15.38 | 14.71 | [6 empty] | 30.9 | 6.8 | 7.6
2009-09-21 | 6.3262 | 5.02 |  |  |  |  | 7.175 | 1.91 |  |  |  |  | 25.5 |  |  |  | 0 | 0.705 |  |  | 0.071 | 0.154 | [5 empty] | 27.7 |  |  |  |  | 55.5 |  | 23.05 |  | 6.8 | 0.034 |  | 15.05 | 97.82 | 1.07 |  |  |  |  | 15.8465 | 14.9725 | [6 empty] | 29.77 | 6.8 | 7.6
2009-09-22 | 6.3119 | 5.01 |  |  |  |  | 6.95 | 1.96 |  |  |  |  | 31 |  |  |  | 0 | 0.843 |  |  | 0.061 | 0.171 | [5 empty] | 27.3 |  |  |  |  | 54.8 |  | 23.4 |  | 7.1 | 0.031 |  | 15.6 | 102.59 | 1.13 |  |  |  |  | 16.406 | 15.092 | [6 empty] | 28.64 | 6.8 | 7.6
2009-09-23 | 6.3191 | 4.98 |  |  |  |  | 7.26 | 1.98 |  |  |  |  | 27 |  |  |  | 0 | 0.698 |  |  | 0.068 | 0.204 | [5 empty] | 27.1 |  |  |  |  | 54.2 |  | 27.9 |  | 6.6 | 0.009 |  | 15.8 | 101.21 | 1.11 |  |  |  |  | 15.912 | 14.857 | [6 empty] | 29.11 | 6.8 | 7.6
2009-09-24 | 6.3155 | 5 |  |  |  |  | 7.21 | 2 |  |  |  |  | 20 |  |  |  | 0 | 0.604 |  |  | 0.059 | 0.137 | [5 empty] | 28.3 |  |  |  |  | 56.6 |  | 26.1 |  | 6.4 | 0.01 |  | 15.2 | 105.84 | 1.11 |  |  |  |  | 16.75 | 15.44 | [6 empty] | 30.51 | 6.8 | 7.6
2009-09-25 | 6.3173 | 4.995 |  |  |  |  | 7.395 | 1.99 | [9 empty] | 0.6015 |  |  | 0.06 | 0.145 | [5 empty] | 27.55 |  |  |  |  | 55.1 |  | 25.85 |  | 6.45 | 0.0145 |  | 15.2 | 107.68 | 1.15 |  |  |  |  | 16.331 | 15.1485 | [6 empty] | 28.995 | 6.8 | 7.65
2009-09-26 | 6.3164 | 4.99 |  |  |  |  | 7.58 | 1.98 |  |  |  |  | 23 |  |  |  | 0 | 0.599 |  |  | 0.061 | 0.153 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 25.6 |  | 6.5 | 0.019 |  | 15.2 | 109.52 | 1.19 |  |  |  |  | 17.029 | 15.699 | [6 empty] | 27.48 | 6.8 | 7.7
2009-09-27 | 6.3168 | 5.08 |  |  |  |  | 7.62 | 1.89 |  |  |  |  | 23 |  |  |  | 0 | 0.649 |  |  | 0.096 | 0.267 | [5 empty] | 27.1 |  |  |  |  | 54.2 |  | 25.9 |  | 6.7 | 0.061 |  | 14.3 | 105.38 | 1.35 |  |  |  |  | 16.28 | 14.77 | [6 empty] | 29.36 | 6.8 | 7.5
2009-09-28 | 6.3166 | 5.09 |  |  |  |  | 6.59 | 1.84 |  |  |  |  | 21.5 |  |  |  | 0 | 0.6125 |  |  | 0.0855 | [6 empty] | 27.3 |  |  |  |  | 54.6 |  | 25.5 |  | 6.9 | 0.0595 |  | 14.2 | 101.3 | 1.38 |  |  |  |  | 16.14 | 14.268 | [6 empty] | 30.75 | 7.2 | 7.1
2009-09-29 | 6.3167 | 5.1 |  |  |  |  | 5.56 | 1.8 |  |  |  |  | 20 |  |  |  | 0 | 0.576 |  |  | 0.075 | 0.104 | [5 empty] | 27.5 |  |  |  |  | 55 |  | 25.1 |  | 7.1 | 0.058 |  | 14.1 | 108.16 | 1.21 |  |  |  |  | 17.826 | 16.3 | [6 empty] | 32.14 | 7.2 | 7.1
2009-09-30 | 6.3166 | 5.07 |  |  |  |  | 7.68 | 1.83 |  |  |  |  | 24 |  |  |  | 0.074 | 0.737 |  |  | 0.144 | 0.144 | [5 empty] | 28.4 |  |  |  |  | 56.4 |  | 25.3 |  | 6.4 | 0.06 |  | 13.9 | 112.46 | 1.37 |  |  |  |  | 17.94 | 15.95 | [6 empty] | 31.02 | 6.6 | 7.1
2009-10-01 | 6.3167 | 5 |  |  |  |  | 7.27 | 1.96 |  |  |  |  | 22 |  |  |  | 0 | 0.587 |  |  | 0.089 | 0.224 | [5 empty] | 27.2 |  |  |  |  | 54.4 |  | 24.8 |  | 6.9 | 0.074 |  | 14.7 | 109.16 | 1.05 |  |  |  |  | 17.388 | 16.475 | [6 empty] | 32.58 | 6.6 | 7.1
2009-10-02 | 6.3167 | 4.99 |  |  |  |  | 6.85 | 2.06 |  |  |  |  | 24 |  |  |  | 0 | 0.57 |  |  | 0.066 | 0.143 | [5 empty] | 25.6 |  |  |  |  | 51.2 |  | 24.3 |  | 6.7 | 0.018 |  | 14.7 | 114.66 | 1.13 |  |  |  |  | 18.14 | 16.3 | [6 empty] | 33.71 | 6.6 | 7.1
2009-10-03 | 6.3167 | 5.05 |  |  |  |  | 7 | 2.13 |  |  |  |  | 27 |  |  |  | 0 | 0.687 |  |  | 0.068 | 0.16 | [5 empty] | 27 |  |  |  |  | 54.1 |  | 23 |  | 5 | 0.042 |  | 14.6 | 117.84 | 1.24 |  |  |  |  | 17.832 | 15.854 | [6 empty] | 30.51 | 7.6 | 7.1
2009-10-04 | 6.3167 | 5 |  |  |  |  | 7.26 | 2.12 |  |  |  |  | 26 |  |  |  | 0 | 0.632 |  |  | 0.062 | 0.177 | [5 empty] | 27.1 |  |  |  |  | 54.2 |  | 22.9 |  | 5.7 | 0.048 |  | 14.6 | 101.85 | 0.9 |  |  |  |  | 16.153 | 15.297 | [6 empty] | 31.22 | 7.6 | 7.1
2009-10-05 | 6.3167 | 4.995 |  |  |  |  | 7.085 | 2.115 |  |  |  |  | 25 |  |  |  | 0 | 0.623 |  |  | 0.065 | 0.182 | [5 empty] | 25.85 |  |  |  |  | 51.7 |  | 23.35 |  | 5.9 | 0.0505 |  | 13.5 | 91.025 | 0.545 |  |  |  |  | 16.9925 | 15.5755 | [6 empty] | 32.42 | 7.6 | 7.1
2009-10-06 | 6.3167 | 4.99 |  |  |  |  | 6.91 | 2.11 |  |  |  |  | 24 |  |  |  | 0 | 0.614 |  |  | 0.068 | 0.187 | [5 empty] | 24.6 |  |  |  |  | 49.2 |  | 23.8 |  | 6.1 | 0.053 |  | 12.4 | 80.2 | 0.19 |  |  |  |  | 17.675 | 15.841 | [6 empty] | 33.62 | 7.6 | 7.1
2009-10-07 | 6.46 | 5.4 |  |  |  |  | 7.3 | 2.11 |  |  |  |  | 27 |  |  |  | 0 | 0.593 |  |  | 0.061 | 0.116 | [5 empty] | 26.6 |  |  |  |  | 53.2 |  | 23.6 |  |  | 0.039 |  | 12.9 | 99.23 | 0.71 |  |  |  |  | 17.86 | 15.99 | [6 empty] | 30.23 | 6.6 | 7.1
2009-10-08 | 6.86 | 5.49 |  |  |  |  | 6.81 | 2.01 |  |  |  |  | 18 |  |  |  | 0 | 0.497 |  |  | 0.066 | 0.206 | [5 empty] | 25.3 |  |  |  |  | 50.7 |  | 23.5 |  | 5.4 | 0.041 |  | 12.9 | 98.28 | 0.91 |  |  |  |  | 16.503 | 15.289 | [6 empty] | 30.51 | 5.7 | 7.1
2009-10-09 | 6.96 | 5.21 |  |  |  |  | 6.57 | 1.91 |  |  |  |  | 21 |  |  |  | 0 | 0.521 |  |  | 0.078 | 0.263 | [5 empty] | 25.6 |  |  |  |  | 51.2 |  | 26.8 |  | 4.8 | 0.0005 |  | 12.6 | 105.59 | 1.16 |  |  |  |  | 17.631 | 15.625 | [6 empty] | 30.28 | 5.4 | 7.4
2009-10-10 | 6.6 | 5.19 |  |  |  |  | 6.8 | 1.78 |  |  |  |  | 17 |  |  |  | 0 | 0.503 |  |  | 0.071 | 0.371 | [5 empty] | 24.7 |  |  |  |  | 49.5 |  | 23.6 |  | 6.5 | 0.067 |  | 12.1 | 102.82 | 1.15 |  |  |  |  | 16.807 | 15.929 | [6 empty] | 30.15 | 4 | 8.1
2009-10-11 | 6.64 | 5.18 |  |  |  |  | 6.67 | 1.76 |  |  |  |  | 21 |  |  |  | 0 | 0.534 |  |  | 0.101 | 0.497 | [5 empty] | 26.3 |  |  |  |  | 52.6 |  | 21.7 |  | 7.2 | 0.031 |  | 12 | 98.06 | 1.35 |  |  |  |  | 16.497 | 14.305 | [6 empty] | 30.699 | 3.8 | 8.2
2009-10-12 | 6.86 | 5.1 |  |  |  |  | 6.725 | 1.825 |  |  |  |  | 22 |  |  |  | 0 | 0.647 |  |  | 0.1035 | 0.545 | [5 empty] | 25.95 |  |  |  |  | 51.95 |  | 23.5 |  | 5.65 | 0.031 |  | 11.05 | 99.315 | 1.225 |  |  |  |  | 16.652 | 14.7625 | [6 empty] | 31.3095 | 3.8 | 8.6
2009-10-13 | 7.08 | 5.02 |  |  |  |  | 6.78 | 1.89 |  |  |  |  | 23 |  |  |  | 0 | 0.76 |  |  | 0.106 | 0.593 | [5 empty] | 25.6 |  |  |  |  | 51.3 |  | 25.3 |  | 4.1 | 0.031 |  | 10.1 | 100.57 | 1.1 |  |  |  |  | 16.144 | 15.22 | [6 empty] | 31.92 | 3.8 | 9
2009-10-14 | 6.76 | 5.1 |  |  |  |  | 6.55 | 1.97 |  |  |  |  | 25 |  |  |  | 0 | 0.683 |  |  | 0.139 | 0.625 | [5 empty] | 26.3 |  |  |  |  | 52.7 |  | 26.2 |  | 4.4 | 0.039 |  | 10.2 | 97.92 | 1.12 |  |  |  |  | 16.232 | 14.398 | [6 empty] | 30.98 | 3.8 | 9.2
2009-10-15 | 6.77 | 4.97 |  |  |  |  | 6.82 | 1.99 |  |  |  |  | 27 |  |  |  | 0 | 0.691 |  |  | 0.116 | 0.476 | [5 empty] | 27.4 |  |  |  |  | 54.8 |  | 24.8 |  | 6 | 0.042 |  | 10.1 | 98.92 | 0.92 |  |  |  |  | 16.782 | 15.438 | [6 empty] | 30.95 | 3.8 | 9.4
2009-10-16 | 6.64 | 4.96 |  |  |  |  | 6.78 | 2.01 |  |  |  |  | 30 |  |  |  | 0 | 0.681 |  |  | 0.121 | 0.617 | [5 empty] | 28 |  |  |  |  | 56 |  | 25.9 |  | 5.6 | 0.041 |  | 10.1 | 100.32 | 1.02 |  |  |  |  | 16.348 | 15.423 | [6 empty] | 29.47 | 3.8 | 9.4
2009-10-17 | 6.33 | 5 |  |  |  |  | 7.12 | 1.9 |  |  |  |  | 33 |  |  |  | 0 | 0.647 |  |  | 0.127 | 0.624 | [5 empty] | 27.3 |  |  |  |  | 54.6 |  | 25.3 |  | 5.9 | 0.047 |  | 11.3 | 106.74 | 1.29 |  |  |  |  | 17.14 | 15.183 | [6 empty] | 32.52 | 3.8 | 9.4
2009-10-18 | 6.69 | 4.96 |  |  |  |  | 7 | 1.74 |  |  |  |  | 36 |  |  |  | 0 | 0.628 |  |  | 0.093 | 0.351 | [5 empty] | 25.4 |  |  |  |  | 50.8 |  | 24.3 |  | 6 | 0.042 |  | 11 | 96.8 | 1.26 |  |  |  |  | 16.03 | 14.67 | [6 empty] | 26.46 | 3.8 | 9.4
2009-10-19 | 6.64 | 4.985 |  |  |  |  | 7.16 | 1.74 |  |  |  |  | 34.5 |  |  |  | 0 | 0.6185 |  |  | 0.1035 | 0.339 | [5 empty] | 25.1 |  |  |  |  | 50.2 |  | 24.1 |  | 5.85 | 0.053 |  | 10.95 | 96.82 | 1.27 |  |  |  |  | 15.69 | 14.594 | [6 empty] | 27.615 | 3.8 | 9.4
2009-10-20 | 6.59 | 5.01 |  |  |  |  | 7.32 | 1.66 |  |  |  |  | 33 |  |  |  | 0 | 0.609 |  |  | 0.114 | 0.327 | [5 empty] | 24.8 |  |  |  |  | 49.6 |  | 23.9 |  | 5.7 | 0.064 |  | 10.9 | 109.17 | 1.48 |  |  |  |  | 17.709 | 15.777 | [6 empty] | 28.77 | 3.8 | 9.4
2009-10-21 | 6.615 | 4.92 |  |  |  |  | 6.53 | 1.61 |  |  |  |  | 30 |  |  |  | 0 | 0.567 |  |  | 0.311 | 0.637 | [5 empty] | 26.1 |  |  |  |  | 52.2 |  | 25.3 |  | 5.7 | 0.084 |  | 10.8 | 99.27 | 1.42 |  |  |  |  | 18.754 | 14.83 | [6 empty] | 29.75 | 3.8 | 9.4
2009-10-22 | 6.57 | 4.89 |  |  |  |  | 6.12 | 1.7 |  |  |  |  | 32 |  |  |  | 0 | 0.628 |  |  | 0.143 | 0.486 | [5 empty] | 22.5 |  |  |  |  | 45 |  | 24.8 |  | 5.4 | 0.076 |  | 9.2 | 101.55 | 1.47 |  |  |  |  | 17.843 | 14.554 | [6 empty] | 30.98 | 3.8 | 9.9
2009-10-23 | 6.55 | 5.09 |  |  |  |  | 6.12 | 1.72 |  |  |  |  | 32 |  |  |  | 0 | 0.622 |  |  | 0.103 | 0.492 | [5 empty] | 23.1 |  |  |  |  | 46.2 |  | 24.9 |  | 5.8 | 0.047 |  | 8.5 | 108.05 | 1.59 |  |  |  |  | 16.68 | 14.84 | [6 empty] | 30.22 | 3.8 | 10.2
2009-10-24 | 6.8 | 5.12 |  |  |  |  | 6.45 | 1.79 |  |  |  |  | 20 |  |  |  | 0 | 0.604 |  |  | 0.081 | 0.559 | [5 empty] | 25 |  |  |  |  | 50.1 |  | 26.3 |  | 4.4 | 0.004 |  | 8.5 | 97.84 | 1.21 |  |  |  |  | 15.847 | 14.792 | [6 empty] | 30.98 | 3.8 | 13
2009-10-25 | 6.76 | 4.99 |  |  |  |  | 6.61 | 1.73 |  |  |  |  | 23 |  |  |  | 0 | 0.693 |  |  | 0.076 | 0.407 | [5 empty] | 25.1 |  |  |  |  | 50.2 |  | 22.2 |  | 4.8 | 0.015 |  | 8.4 | 70.63 | 0.54 |  |  |  |  | 15.2 | 14.129 | [6 empty] | 30.75 | 3.8 | 13
2009-10-26 | 6.49 | 5.025 |  |  |  |  | 6.68 | 1.785 |  |  |  |  | 23.5 |  |  |  | 0 | 0.6395 |  |  | 0.156 | 0.468 | [5 empty] | 25.2 |  |  |  |  | 50.4 |  | 22.5 |  | 5.2 | 0.0215 |  | 8.2 | 81.265 | 0.765 |  |  |  |  | 15.5235 | 14.4605 | [6 empty] | 27.15 | 3.8 | 13
2009-10-27 | 6.22 | 5.06 |  |  |  |  | 6.75 | 1.84 |  |  |  |  | 24 |  |  |  | 0 | 0.586 |  |  | 0.236 | 0.529 | [5 empty] | 25.3 |  |  |  |  | 50.6 |  | 22.8 |  | 5.6 | 0.028 |  | 8 | 91.9 | 0.99 |  |  |  |  | 16.67 | 14.768 | [6 empty] | 23.55 | 3.8 | 13
2009-10-28 | 6.4 | 5.01 |  |  |  |  | 7.12 | 1.88 |  |  |  |  | 19 |  |  |  | 0 | 0.656 |  |  | 0.144 | 0.607 | [5 empty] | 25.4 |  |  |  |  | 50.8 |  | 23.9 |  | 6.3 | 0.039 |  | 8 | 107.07 | 1.39 |  |  |  |  | 16.814 | 14.988 | [6 empty] | 26.21 | 3.8 | 12.8
2009-10-29 | 6.43 | 5.055 |  |  |  |  | 6.925 | 1.78 |  |  |  |  | 20 |  |  |  | 0 | 0.6535 |  |  | 0.188 | 0.668 | [5 empty] | 25.3 |  |  |  |  | 50.6 |  | 23.85 |  | 6.5 | 0.02 |  | 7.3 | 102.645 | 1.35 |  |  |  |  | 16.742 | 14.878 | [6 empty] | 27.19 | 3.4 | 12.6
2009-10-30 | 6.46 | 5.1 |  |  |  |  | 6.73 | 1.68 |  |  |  |  | 21 |  |  |  | 0 | 0.651 |  |  | 0.232 | 0.729 | [5 empty] | 25.2 |  |  |  |  | 50.4 |  | 23.8 |  | 6.7 | 0.001 |  | 6.6 | 98.22 | 1.31 |  |  |  |  | 15.971 | 14.993 | [6 empty] | 28.17 | 3 | 12.4
2009-10-31 | 6.37 | 5.03 |  |  |  |  | 7.1 | 1.68 |  |  |  |  | 25 |  |  |  | 0 | 0.637 |  |  | 0.197 | 0.667 | [5 empty] | 26.1 |  |  |  |  | 52.2 |  | 24.1 |  | 6.5 | 0.009 |  | 6.5 | 99.56 | 1.3 |  |  |  |  | 16.166 | 15.181 | [6 empty] | 29.51 | 2.8 | 12.6
2009-11-01 | 6.2 | 5.06 |  |  |  |  | 7.03 | 1.81 |  |  |  |  | 18 |  |  |  | 0 | 1.378 |  |  | 0.254 | 0.629 | [5 empty] | 25.5 |  |  |  |  | 51 |  | 22.5 |  | 6.4 | 0.03 |  | 7.3 | 101.21 | 1.39 |  |  |  |  | 15.946 | 14.374 | [6 empty] | 28.39 | 2.8 | 12.6
2009-11-02 | 6.505 | 4.99 |  |  |  |  | 6.58 | 1.875 |  |  |  |  | 21.5 |  |  |  | 0 | 1.139 |  |  | 0.2425 | 0.6925 | [5 empty] | 25.85 |  |  |  |  | 51.75 |  | 23 |  | 5.15 | 0.016 |  | 6.95 | 100.68 | 1.285 |  |  |  |  | 16.056 | 14.7775 | [6 empty] | 29.45 | 2.8 | 12.75
2009-11-03 | 6.81 | 4.92 |  |  |  |  | 6.13 | 1.94 |  |  |  |  | 25 |  |  |  | 0 | 0.9 |  |  | 0.231 | 0.756 | [5 empty] | 26.2 |  |  |  |  | 52.5 |  | 23.5 |  | 3.9 | 0.002 |  | 6.6 | 100.15 | 1.18 |  |  |  |  | 15.849 | 14.556 | [6 empty] | 30.51 | 2.8 | 12.9
2009-11-04 | 6.33 | 4.97 |  |  |  |  | 6.74 | 1.89 |  |  |  |  | 28 |  |  |  | 0 | 0.968 |  |  | 0.261 | 1.049 | [5 empty] | 28.5 |  |  |  |  | 57.1 |  | 25.1 |  | 4.7 | 0.08 |  | 6.7 | 108.07 | 1.39 |  |  |  |  | 16.806 | 14.965 | [6 empty] | 30.98 | 2.5 | 12.9
2009-11-05 | 6.315 | 4.98 |  |  |  |  | 6.805 | 1.79 |  |  |  |  | 24.5 |  |  |  | 0 | 0.9085 |  |  | 0.3605 | 1.0035 | [5 empty] | 28.7 |  |  |  |  | 57.45 |  | 24.45 |  | 5.55 | 0.0735 |  | 6.25 | 107.24 | 1.375 |  |  |  |  | 16.803 | 14.965 | [6 empty] | 30.805 | 2.25 | 13.2
2009-11-06 | 6.3 | 4.99 |  |  |  |  | 6.87 | 1.69 |  |  |  |  | 21 |  |  |  | 0 | 0.849 |  |  | 0.46 | 0.958 | [5 empty] | 28.9 |  |  |  |  | 57.8 |  | 23.8 |  | 6.4 | 0.067 |  | 5.8 | 106.41 | 1.36 |  |  |  |  | 16.777 | 15.824 | [6 empty] | 30.63 | 2 | 13.5
2009-11-07 | 6.335 | 4.99 |  |  |  |  | 6.78 | 1.81 |  |  |  |  | 23 |  |  |  | 0 | 0.496 |  |  | 0.3155 | 0.745 | [5 empty] | 27.2 |  |  |  |  | 54.4 |  | 23.8 |  | 6.25 | 0.057 |  | 5.55 | 102.95 | 1.185 |  |  |  |  | 16.135 | 14.487 | [6 empty] | 30.28 | 3.05 | 11.55
2009-11-08 | 6.37 | 5.01 |  |  |  |  | 6.17 | 1.97 |  |  |  |  | 25 |  |  |  | 0 | 0.874 |  |  | 0.171 | 0.532 | [5 empty] | 25.5 |  |  |  |  | 51 |  | 23.8 |  | 6.1 | 0.047 |  | 5.3 | 99.49 | 1.01 |  |  |  |  | 16 | 15.15 | [6 empty] | 29.93 | 4.1 | 9.6
2009-11-09 | 6.29 | 5.085 |  |  |  |  | 6.385 | 2.02 |  |  |  |  | 23.5 |  |  |  | 0 | 0.961 |  |  | 0.155 | 0.5285 | [5 empty] | 26.15 |  |  |  |  | 52.3 |  | 24.65 |  | 6.25 | 0.067 |  | 5.15 | 104 | 1.14 |  |  |  |  | 16.809 | 14.946 | [6 empty] | 30.77 | 4.5 | 9
2009-11-10 | 6.21 | 5.16 |  |  |  |  | 6.6 | 1.92 |  |  |  |  | 22 |  |  |  | 0 | 1.048 |  |  | 0.139 | 0.525 | [5 empty] | 26.8 |  |  |  |  | 53.6 |  | 25.5 |  | 6.4 | 0.087 |  | 5 | 106.26 | 1.37 |  |  |  |  | 16.595 | 14.662 | [6 empty] | 31.61 | 4.5 | 9
2009-11-11 | 6.22 | 5.06 |  |  |  |  | 6.64 | 1.92 |  |  |  |  | 26 |  |  |  | 0 | 1.008 |  |  | 0.145 | 0.733 | [5 empty] | 27 |  |  |  |  | 54 |  | 24.4 |  | 6.3 | 0.074 |  | 4.7 | 100.81 | 1.15 |  |  |  |  | 16.294 | 14.927 | [6 empty] | 30.05 | 5 | 9.2
2009-11-12 | 5.92 | 5.92 |  |  |  |  | 7.21 | 1.93 |  |  |  |  | 34 |  |  |  | 0 | 1.08 |  |  | 0.147 | 0.511 | [5 empty] | 27.8 |  |  |  |  | 55.6 |  | 24.5 |  | 6.5 | 0.063 |  | 4.5 | 107.17 | 1.44 |  |  |  |  | 17.181 | 14.71 | [6 empty] | 30.57 | 5.8 | 7.2
2009-11-13 | 6.19 | 5.04 |  |  |  |  | 6.41 | 1.89 |  |  |  |  | 25 |  |  |  | 0 | 0.973 |  |  | 0.138 | 0.482 | [5 empty] | 28.5 |  |  |  |  | 57 |  | 24.4 |  | 6.8 | 0.062 |  | 4.5 | 94.82 | 1.04 |  |  |  |  | 15.77 | 14.67 | [6 empty] | 35.59 | 5.9 | 9
2009-11-14 | 6.29 | 5.14 |  |  |  |  | 7.53 | 1.84 |  |  |  |  | 27 |  |  |  | 0 | 0.968 |  |  | 0.149 | 0.699 | [5 empty] | 27.7 |  |  |  |  | 55.4 |  | 23.8 |  | 5.1 | 0.048 |  | 5 | 93.03 | 0.83 |  |  |  |  | 16.941 | 15.821 | [6 empty] | 30.98 | 6.1 | 8.8
2009-11-15 | 6.75 | 5.47 |  |  |  |  | 7.65 | 1.65 |  |  |  |  | 34 |  |  |  | 0 | 0.947 |  |  | 0.127 | 0.386 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 22.8 |  | 4.9 | 0.03 |  | 4.7 | 90.395 | 0.975 |  |  |  |  | 15.6 | 14.46 | [6 empty] | 30.51 | 6.5 | 8.8
2009-11-16 | 6.355 | 5.55 |  |  |  |  | 7.865 | 1.53 |  |  |  |  | 36.5 |  |  |  | 0 | 0.972 |  |  | 0.2635 | 0.465 | [5 empty] | 28.15 |  |  |  |  | 56.3 |  | 22.25 |  | 5 | 0.0395 |  | 4.7 | 87.76 | 1.12 |  |  |  |  | 16.199 | 15.06 | [6 empty] | 30.53 | 6.75 | 8.4
2009-11-17 | 5.96 | 5.63 |  |  |  |  | 8.08 | 1.53 |  |  |  |  | 39 |  |  |  | 0 | 0.997 |  |  | 0.4 | 0.544 | [5 empty] | 28.1 |  |  |  |  | 56.2 |  | 21.7 |  | 5.1 | 0.049 |  | 4.7 | 93.01 | 1.19 |  |  |  |  | 17.01 | 15.538 | [6 empty] | 30.55 | 7 | 8
2009-11-18 | 6.3 | 5.59 |  |  |  |  | 7 | 1.61 |  |  |  |  | 32 |  |  |  | 0 | 0.936 |  |  | 0.182 | 0.298 | [5 empty] | 25.7 |  |  |  |  | 51.5 |  | 23.9 |  | 5 | 0.031 |  | 4.5 | 93.38 | 1.21 |  |  |  |  | 16.54 | 15.02 | [6 empty] | 29.58 | 6.5 | 8
2009-11-19 | 7 | 5.39 |  |  |  |  | 7.04 | 1.69 |  |  |  |  | 38 |  |  |  | 0 | 0.888 |  |  | 0.192 | 0.5 | [5 empty] | 28.2 |  |  |  |  | 56.5 |  | 22.7 |  | 8 | 0.049 |  | 4.5 | 89.72 | 1.07 |  |  |  |  | 15.843 | 14.739 | [6 empty] | 25.82 | 6.3 | 8.2
2009-11-20 | 6.78 | 5.52 |  |  |  |  | 7.15 | 1.82 |  |  |  |  | 31 |  |  |  | 0 | 0.828 |  |  | 0.204 | 0.458 | [5 empty] | 28.4 |  |  |  |  | 56.7 |  | 23.3 |  | 8.3 | 0.002 |  | 4.4 | 92.26 | 0.91 |  |  |  |  | 17.017 | 15.339 | [6 empty] | 27.23 | 5.7 | 8.2
2009-11-21 | 6.73 | 5.37 |  |  |  |  | 6.88 | 1.85 |  |  |  |  | 33 |  |  |  | 0 | 0.831 |  |  | 0.198 | 0.426 | [5 empty] | 24.5 |  |  |  |  | 49 |  | 23.5 |  | 8 | 0.036 |  | 4.2 | 95.49 | 1.07 |  |  |  |  | 16.717 | 14.872 | [6 empty] | 26.525 | 5.1 | 8.6
2009-11-22 | 6.15 | 5.39 |  |  |  |  | 6.7 | 1.74 |  |  |  |  | 32 |  |  |  | 0 | 0.736 |  |  | 0.201 | 0.437 | [5 empty] | 26.1 |  |  |  |  | 52.2 |  | 23.9 |  | 7.7 | 0.043 |  | 4.9 | 88.2 | 0.82 |  |  |  |  | 16.22 | 15.66 | [6 empty] | 26.8775 | 4.5 | 9
2009-11-23 | 6.375 | 5.305 |  |  |  |  | 6.7 | 1.75 |  |  |  |  | 35 |  |  |  | 0 | 0.724 |  |  | 0.226 | 0.6815 | [5 empty] | 26.6 |  |  |  |  | 53.2 |  | 23.35 |  | 7.4 | 0.023 |  | 4.5 | 91.08 | 0.975 |  |  |  |  | 16.4685 | 15.266 | [6 empty] | 26.7012 | 4.4 | 9
2009-11-24 | 6.6 | 5.22 |  |  |  |  | 6.7 | 1.76 |  |  |  |  | 38 |  |  |  | 0 | 0.712 |  |  | 0.251 | 0.926 | [5 empty] | 27.1 |  |  |  |  | 54.2 |  | 22.8 |  | 7.1 | 0.003 |  | 4.1 | 93.96 | 1.13 |  |  |  |  | 17.236 | 14.722 | [6 empty] | 26.29 | 4.3 | 9
2009-11-25 | 6.29 | 5.16 |  |  |  |  | 4.83 | 1.78 |  |  |  |  | 30 |  |  |  | 0 | 0.91 |  |  | 0.197 | 0.41 | [5 empty] | 22.1 |  |  |  |  | 44.2 |  | 24.5 |  | 1.4 | 0.25 |  | 4.7 | 87.27 | 0.82 |  |  |  |  | 16.303 | 15.211 | [6 empty] | 25.35 | 3.8 | 9
2009-11-26 | 6.24 | 5.17 |  |  |  |  | 5.05 | 1.74 |  |  |  |  | 28 |  |  |  | 0 | 0.897 |  |  | 0.201 | 0.467 | [5 empty] | 23.6 |  |  |  |  | 47.3 |  | 24.2 |  | 1.6 | 0.19 |  | 4.6 | 89.63 | 0.84 |  |  |  |  | 16.776 | 15.767 | [6 empty] | 23.25 | 3.3 | 9
2009-11-27 | 5.93 | 5.09 |  |  |  |  | 6.96 | 1.75 |  |  |  |  | 29 |  |  |  | 0 | 0.859 |  |  | 0.291 | 0.603 | [5 empty] | 26 |  |  |  |  | 52 |  | 25.1 |  | 4.9 | 0.221 |  | 4.8 | 89.13 | 1.14 |  |  |  |  | 15.982 | 13.996 | [6 empty] | 26.92 | 4 | 9
2009-11-28 | 6.29 | 4.9 |  |  |  |  | 7.42 | 1.76 |  |  |  |  | 30 |  |  |  | . | 1.13 |  |  | 0.261 | 0.504 | [5 empty] | 25 |  |  |  |  | 50 |  | 24.8 |  | 5.7 | 0.316 |  | 4.3 | 87.07 | 0.88 |  |  |  |  | 16.175 | 15.049 | [6 empty] | 29.63 | 4.5 | 9.4
2009-11-29 | 6.36 | 4.96 |  |  |  |  | 6.34 | 1.59 |  |  |  |  | 28 |  |  |  | 0 | 0.97 |  |  | 0.19 | 0.784 | [5 empty] | 22.7 |  |  |  |  | 45.4 |  | 23.7 |  | 5.9 | 0.036 |  | 4.7 | 92.39 | 1.28 |  |  |  |  | 16.354 | 14.612 | [6 empty] | 30.33 | 3 | 9.4
2009-11-30 | 6.215 | 4.985 |  |  |  |  | 6.565 | 1.49 |  |  |  |  | 29 |  |  |  | 0 | 0.947 |  |  | 0.169 | 0.957 | [5 empty] | 24.45 |  |  |  |  | 48.9 |  | 23.7 |  | 6.05 | 0.0465 |  | 4.25 | 89.72 | 1.31 |  |  |  |  | 16.014 | 14.539 | [6 empty] | 32.385 | 1 | 11.2
2009-12-01 | 6.07 | 5.01 |  |  |  |  | 6.79 | 1.48 |  |  |  |  | 30 |  |  |  | 0 | 0.924 |  |  | 0.148 | 1.13 | [5 empty] | 26.2 |  |  |  |  | 52.4 |  | 23.7 |  | 6.2 | 0.057 |  | 3.8 | 97.06 | 1.54 |  |  |  |  | 16.605 | 14.605 | [6 empty] | 34.44 | 1 | 11.2
2009-12-02 | 6 | 4.8 |  |  |  |  | 6.46 | 1.7 |  |  |  |  | 26 |  |  |  | 0 | 0.868 |  |  | 0.363 | 0.747 | [5 empty] | 26.5 |  |  |  |  | 53 |  | 25.9 |  | 4.8 | 0.041 |  | 3.3 | 104.7 | 1.55 |  |  |  |  | 16.2 | 14.635 | [6 empty] | 31.15 | 1.3 | 11
2009-12-03 | 6.74 | 5.09 |  |  |  |  | 6.31 | 1.96 |  |  |  |  | 27 |  |  |  | 0 | 0.847 |  |  | 0.462 | 1.108 | [5 empty] | 26.1 |  |  |  |  | 52.2 |  | 24.7 |  | 5.1 | 0.053 |  | 3.5 | 112.39 | 1.37 |  |  |  |  | 16.919 | 15.314 | [6 empty] | 31.51 | 1.5 | 11
2009-12-04 | 5.77 | 5.14 |  |  |  |  | 6.35 | 2.15 |  |  |  |  | 33 |  |  |  | 0 | 0.805 |  |  | 0.142 | 0.451 | [5 empty] | 27.9 |  |  |  |  | 55.8 |  | 23.9 |  | 6 | 0.36 |  | 3.5 | 110.28 | 1.2 |  |  |  |  | 16.88 | 14.95 | [6 empty] | 33.41 | 5.6 | 7
2009-12-05 | 5.58 | 5.58 |  |  |  |  | 6.41 | 1.92 |  |  |  |  | 34 |  |  |  | 0 | 0.782 |  |  | 0.13 | 0.232 | [5 empty] | 28.3 |  |  |  |  | 56.7 |  | 26.5 |  | 5 | 0.01 |  | 3.4 | 101.85 | 1.13 |  |  |  |  | 16.234 | 15.144 | [6 empty] | 30.51 | 8.8 | 4.4
2009-12-06 | 6.42 | 5.84 |  |  |  |  | 6.79 | 1.86 |  |  |  |  | 26 |  |  |  | 0 | 0.791 |  |  | 0.202 | 0.523 | [5 empty] | 29.3 |  |  |  |  | 58.7 |  | 26 |  | 6.5 | 0.001 |  | 3.3 | 84.09 | 0.71 |  |  |  |  | 15.984 | 14.835 | [6 empty] | 30.51 | 8.8 | 5
2009-12-07 | 6.18 | 5.76 |  |  |  |  | 6.73 | 1.71 |  |  |  |  | 40 |  |  |  | 0 | 0.735 |  |  | 0.179 | 0.348 | [5 empty] | 28.9 |  |  |  |  | 57.8 |  | 25.1 |  | 3.5 | 0.031 |  | 3.2 | 97.24 | 1.28 |  |  |  |  | 16.109 | 14.9895 | [6 empty] | 31.12 | 8.7 | 5
2009-12-08 | 6.265 | 5.49 |  |  |  |  | 6.525 | 1.695 |  |  |  |  | 46.5 |  |  |  | 0 | 0.73 |  |  | 0.149 | 0.358 | [5 empty] | 27.6 |  |  |  |  | 55.2 |  | 25.45 |  | 4.7 | 0.0345 |  | 3.3 | 101.54 | 1.31 |  |  |  |  | 17.847 | 14.767 | [6 empty] | 31.38 | 7.7 | 5.1
2009-12-09 | 6.35 | 5.22 |  |  |  |  | 6.32 | 1.68 |  |  |  |  | 53 |  |  |  | 0 | 0.725 |  |  | 0.119 | 0.368 | [5 empty] | 26.3 |  |  |  |  | 52.6 |  | 25.8 |  | 5.9 | 0.038 |  | 3.4 | 105.84 | 1.34 |  |  |  |  | 20.99 | 15.89 | [6 empty] | 31.64 | 6.7 | 5.2
2009-12-10 | 6.5 | 5.22 |  |  |  |  | 6.38 | 1.88 |  |  |  |  | 32 |  |  |  | 0 | 0.682 |  |  | 0.071 | 0.241 | [5 empty] | 26.2 |  |  |  |  | 52.4 |  | 22.7 |  | 5.6 | 0.005 |  | 3.4 | 89.48 | 0.93 |  |  |  |  | 15.247 | 14.48 | [6 empty] | 30.51 | 6.4 | 5.3
2009-12-11 | 6.58 | 5.44 |  |  |  |  | 6.57 | 1.81 |  |  |  |  | 28 |  |  |  | 0 | 0.681 |  |  | 0.074 | 0.295 | [5 empty] | 28.1 |  |  |  |  | 56.3 |  | 21 |  | 5.7 | 0.007 |  | 3.5 | 87.87 | 0.9 |  |  |  |  | 15.873 | 14.717 | [6 empty] | 29.81 | 6.8 | 5.9
2009-12-12 | 6.49 | 5.31 |  |  |  |  | 6.67 | 1.76 |  |  |  |  | 27 |  |  |  | 0 | 0.657 |  |  | 0.061 | 0.307 | [5 empty] | 27.6 |  |  |  |  | 55.2 |  | 22.3 |  | 6 | 0.012 |  | 3.5 | 88.675 | 0.915 |  |  |  |  | 15.943 | 14.465 | [6 empty] | 29.25 | 6.4 | 6
2009-12-13 | 6.37 | 5.39 |  |  |  |  | 6.61 | 1.785 |  |  |  |  | 20 |  |  |  | 0 | 0.659 |  |  | 0.047 | 0.271 | [5 empty] | 26.1 |  |  |  |  | 52.2 |  | 23.1 |  | 6 | 0.019 |  | 3.6 | 88.2725 | 0.9075 |  |  |  |  | 15.56 | 14.5985 | [6 empty] | 30.71 | 6.6 | 6
2009-12-14 | 6.455 | 5.39 |  |  |  |  | 6.605 | 1.7725 |  |  |  |  | 24.5 |  |  |  | 0 | 0.6405 |  |  | 0.059 | 0.2665 | [5 empty] | 26.1 |  |  |  |  | 52.25 |  | 24.8 |  | 5.6 | 0.01 |  | 3.6 | 88.4738 | 0.91125 |  |  |  |  | 15.7515 | 14.5318 | [6 empty] | 30.375 | 6.6 | 6
2009-12-15 | 6.54 | 5.39 |  |  |  |  | 6.6 | 1.7788 |  |  |  |  | 29 |  |  |  | 0 | 0.622 |  |  | 0.071 | 0.262 | [5 empty] | 26.1 |  |  |  |  | 52.3 |  | 26.5 |  | 5.2 | 0.001 |  | 3.6 | 88.3731 | 0.90938 |  |  |  |  | 15.989 | 13.958 | [6 empty] | 30.04 | 6.6 | 6
2009-12-16 | 6.37 | 5.43 |  |  |  |  | 6.71 | 1.7756 |  |  |  |  | 33 |  |  |  | 0 | 0.595 |  |  | 0.071 | 0.274 | [5 empty] | 27.5 |  |  |  |  | 55.2 |  | 25.3 |  | 6.5 | 0.001 |  | 3.6 | 79.38 | 0.91031 |  |  |  |  | 15.608 | 13.369 | [6 empty] | 29.57 | 6.6 | 6
2009-12-17 | 6.29 | 5.51 |  |  |  |  | 6.96 | 1.7772 |  |  |  |  | 30 |  |  |  | 0 | 0.567 |  |  | 0.049 | 0.281 | [5 empty] | 28.2 |  |  |  |  | 56.4 |  | 25.6 |  | 6.8 | 0.003 |  | 3.6 | 83.8766 | 0.90984 |  |  |  |  | 15.837 | 14.618 | [6 empty] | 29.53 | 6.6 | 6.3
2009-12-18 | 6.24 | 5.51 |  |  |  |  | 6.99 | 1.7764 |  |  |  |  | 30 |  |  |  | 0 | 0.566 |  |  | 0.052 | 0.39 | [5 empty] | 28.6 |  |  |  |  | 57.2 |  | 23.7 |  | 6.4 | 0.003 |  | 3.5 | 81.6283 | 0.91008 |  |  |  |  | 15.043 | 13.919 | [6 empty] | 30.57 | 6.6 | 6.3
2009-12-19 | 6.12 | 5.49 |  |  |  |  | 6.43 | 1.7768 |  |  |  |  | 33 |  |  |  | 0 | 0.569 |  |  | 0.046 | 0.332 | [5 empty] | 26.5 |  |  |  |  | 53 |  | 24.4 |  | 6.7 | 0.009 |  | 3.5 | 82.7524 | 0.90996 |  |  |  |  | 15.7225 | 13.9935 | [6 empty] | 29.25 | 6.6 | 6.3
2009-12-20 | 5.98 | 5.41 |  |  |  |  | 6.68 | 1.7766 |  |  |  |  | 31 |  |  |  | 0 | 0.557 |  |  | 0.048 | 0.334 | [5 empty] | 25.3 |  |  |  |  | 50.6 |  | 24.8 |  | 6.1 | 0.017 |  | 3.5 | 82.1904 | 0.91002 |  |  |  |  | 15.3827 | 13.9563 | [6 empty] | 31.11 | 6.6 | 6.5
2009-12-21 | 6.035 | 5.5 |  |  |  |  | 6.875 | 1.7767 |  |  |  |  | 28.5 |  |  |  | 0 | 0.547 |  |  | 0.052 | 0.3405 | [5 empty] | 25.85 |  |  |  |  | 51.7 |  | 24.3 |  | 6.25 | 0.0205 |  | 3.45 | 82.4714 | 0.90999 |  |  |  |  | 15.625 | 14.299 | [6 empty] | 30.725 | 6.6 | 6.5
2009-12-22 | 6.09 | 5.59 |  |  |  |  | 7.07 | 1.7767 |  |  |  |  | 26 |  |  |  | 0 | 0.537 |  |  | 0.056 | 0.347 | [5 empty] | 26.4 |  |  |  |  | 52.8 |  | 23.8 |  | 6.4 | 0.024 |  | 3.4 | 82.3309 | 0.91 |  |  |  |  | 16.298 | 14.518 | [6 empty] | 30.34 | 6.6 | 6.5
2009-12-23 | 6.155 | 5.585 |  |  |  |  | 6.93 | 1.7767 |  |  |  |  | 27.5 |  |  |  | 0 | 0.536 |  |  | 0.0855 | 0.4105 | [5 empty] | 27.45 |  |  |  |  | 54.9 |  | 24.2 |  | 6.3 | 0.0235 |  | 3.5 | 82.4011 | 0.91 |  |  |  |  | 15.9615 | 14.4085 | [6 empty] | 29.455 | 6.55 | 6.5
2009-12-24 | 6.22 | 5.58 |  |  |  |  | 6.79 | 1.7767 |  |  |  |  | 29 |  |  |  | 0 | 0.535 |  |  | 0.115 | 0.474 | [5 empty] | 28.5 |  |  |  |  | 57 |  | 24.6 |  | 6.2 | 0.023 |  | 3.6 | 79.38 | 0.91 |  |  |  |  | 15.221 | 13.997 | [6 empty] | 28.57 | 6.5 | 6.5
2009-12-25 | 6.22 | 5.54 |  |  |  |  | 6.72 | 1.7767 |  |  |  |  | 28 |  |  |  | 0 | 0.537 |  |  | 0.056 | 0.347 | [5 empty] | 29.1 |  |  |  |  | 58.2 |  | 24.9 |  | 6.1 | 0.018 |  | 3.7 | 97.02 | 0.91 |  |  |  |  | 15.852 | 14.675 | [6 empty] | 29.24 | 6.2 | 6.5
2009-12-26 | 6.68 | 5.51 |  |  |  |  | 6.74 | 1.7767 |  |  |  |  | 31 |  |  |  | 0 | 0.543 |  |  | 0.209 | 0.506 | [5 empty] | 30.1 |  |  |  |  | 60.2 |  | 22 |  | 5.8 | 0.021 |  | 3.9 | 70.56 | 0.91 |  |  |  |  | 15.307 | 14.042 | [6 empty] | 29.57 | 6.2 | 6.6
2009-12-27 | 6.59 | 5.84 |  |  |  |  | 6.5 | 1.7767 |  |  |  |  | 29 |  |  |  | 0 | 0.534 |  |  | 0.097 | 0.333 | [5 empty] | 29 |  |  |  |  | 58 |  | 21.9 |  | 6.1 | 0.022 |  | 3.8 | 83.79 | 0.91 |  |  |  |  | 14.536 | 13.242 | [6 empty] | 30.28 | 5.9 | 7
2009-12-28 | 6.38 | 5.76 |  |  |  |  | 6.715 | 1.7767 |  |  |  |  | 29.5 |  |  |  | 0 | 0.5385 |  |  | 0.08 | 0.3535 | [5 empty] | 29.6 |  |  |  |  | 59.2 |  | 22.05 |  | 6.25 | 0.0255 |  | 3.85 | 77.175 | 0.91 |  |  |  |  | 14.9215 | 13.642 | [6 empty] | 31.79 | 5.9 | 7
2009-12-29 | 6.17 | 5.68 |  |  |  |  | 6.93 | 1.7767 |  |  |  |  | 30 |  |  |  | 0 | 0.53625 |  |  | 0.063 | 0.374 | [5 empty] | 30.2 |  |  |  |  | 60.4 |  | 22.2 |  | 6.4 | 0.029 |  | 3.9 | 79.38 | 0.91 |  |  |  |  | 15.384 | 13.189 | [6 empty] | 33.3 | 5.9 | 7
2009-12-30 | 6.47 | 5.55 |  |  |  |  | 6.66 | 1.7767 |  |  |  |  | 31 |  |  |  | 0 | 0.533 |  |  | 0.067 | 0.292 | [5 empty] | 29.7 |  |  |  |  | 59.4 |  | 21.9 |  | 6.2 | 0.037 |  | 3.8 | 78.2775 | 0.91 |  |  |  |  | 15.047 | 14.221 | [6 empty] | 30.09 | 5.9 | 7
2009-12-31 | 6.48 | 5.49 |  |  |  |  | 7.74 | 1.7767 |  |  |  |  | 30 |  |  |  | 0 | 0.526 |  |  | 0.078 | 0.868 | [5 empty] | 30.6 |  |  |  |  | 61.2 |  | 25.3 |  | 6 | 0.041 |  | 3.2 | 78.8287 | 0.91 |  |  |  |  | 14.889 | 10.486 | [6 empty] | 29.81 | 5.9 | 7
| 6.85 | 5.76 |  |  |  |  | 6.97 | 1.7767 |  |  |  |  | 37 |  |  |  | 0 | 0.613 |  |  | 0.137 | 0.611 | [5 empty] | 30.3 |  |  |  |  | 60.7 |  | 22.6 |  | 6.8 | 0.005 |  | 3.4 | 78.5531 | 0.91 |  |  |  |  | 14.587 | 13.293 | [6 empty] | 29.57 | 5.9 | 7

## 2023
Note: The password to unlock the sheets is "WTPLAB". Don't unlock any of them unless you plan on making permanent changes.
| pH | [6 empty] | Chlorine |  |  |  | Colour | [5 empty] | Turbidity | [5 empty] | Total Dissolved Solids |  |  |  |  | Conductivity |  |  |  |  | Hardness |  | Alkalinity |  | Aluminum | Temperature |  | Cl Demand | UVT |  | UVA |  | Flows withinin plant |  |  |  | Flows from plant |  |  | Chemical Dosages |  |  |  |  | Dennis Penney
Date | Raw | PTC | PTC (OL) | SWC | Filter | Finish (OL) | Finish | Free | Total | Sample | Analyzer | Raw A | Raw T | SWC A | Filter A | Finish A | Finish T | Raw | Raw (OL) | SWC | Filter | Finish | Finish (OL) | Raw | PTC | SWC | Filter | Finish | Raw | PTC | SWC | Filter | Finish | Raw | Finish | Raw | Finish | Finish (Free) | Raw | Finish |  | Raw | Filter | Raw | Filter | Raw | Finish | Filter | Backwash | Bishop's | Botwood | GFW | Chlorine | Alum | Lime (Pre) | Lime (Post) | Date | Jerry Loveless
2023-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.91204 | 0 | 0 | 0 | 0 | 13.09 | 11.91 | 12.84 | 0.92 | 1.295 | 2.455 | 8.443 | 2.942 | 0 | 0 | 0 | 2022-01-01 | Nolan Simms
2023-01-02 | 6.58 | 5.21 | 5.37 | 5.44 | 5.52 | 7.09 | 7.03 | 1.51 | 1.87 | 2.06 | 2.04 | 53 | 47 | 16 | 0 | 1 | 0 | 0.421 | 0.3 | 0.732 | 0.104 | 0.301 | 0.38 | 8.3 | 21.2 | 19.8 | 19.6 | 25.2 | 11.5 | 35.8 | 25.5 | 25.7 | 33.9 | 3 | 3.1 | 3 | 5.9 | 0.009 | 6.5 | 5.6 | 1.2245 | 50.9 | 91 | 0.294 | 0.0448 | 13.6 | 12.69 | 13.65 | 0.96 | 1.311 | 2.455 | 8.869 | 3.2345 | 31.6 | 5.5 | 8.9 | 2022-01-02
2023-01-03 | 6.74 | 5.39 | 5.45 | 5.47 | 5.49 | 7.31 | 7.29 | 1.52 | 1.86 | 2.11 | 2.09 | 53 | 45 | 17 | 2 | 2 | 0 | 0.454 | 0.3 | 0.784 | 0.113 | 0.306 | 0.487 | 8 | 20.1 | 19.6 | 19.4 | 26 | 11.3 | 32.2 | 25.3 | 25.2 | 34.9 | 3.02 | 3.22 | 3 | 6.1 | 0.016 | 6.9 | 5.5 | 1.0571 | 50.7 | 90.8 | 0.2942 | 0.045 | 13.6 | 12.73 | 13.59 | 0.86 | 1.36 | 2.485 | 9.113 | 3.0671 | 31.86 | 5.3 | 8.9 | 2022-01-03
2023-01-04 | 6.22 | 5.42 | 5.42 | 5.4 | 5.45 | 6.95 | 6.93 | 1.52 | 1.68 | 1.59 | 1.58 | 51 | 40 | 24 | 4 | 6 | 0 | 0.354 | 0.301 | 1.77 | 0.095 | 0.932 | 0.674 | 8.2 | 19.1 | 19.5 | 19.2 | 24.1 | 11.7 | 30.5 | 25 | 25.1 | 32.5 | 2.86 | 3.13 | 3.1 | 6 | 0.049 | 7.5 | 5.7 | 1.2653 | 50.5 | 86.4 | 0.2967 | 0.0631 | 13.24 | 12.41 | 13.22 | 0.81 | 1.372 | 2.3 | 8.553 | 3.0653 | 32.57 | 5.1 | 8.9 | 2022-01-04 | Continuous
2023-01-05 | 6.38 | 5.43 | 5.38 | 5.45 | 5.48 | 7.13 | 7.11 | 1.61 | 1.78 | 1.9 | 1.81 | 48 | 37 | 18 | 3 | 4 | 0 | 0.334 | 0.298 | 1.03 | 0.089 | 0.556 | 0.534 | 8.3 | 19.2 | 19.4 | 19 | 25.5 | 11.7 | 30.4 | 26.1 | 25.2 | 33.1 | 2.98 | 3.19 | 3 | 5.9 | 0.044 | 7.4 | 5.7 | 1.0076 | 50.8 | 90.2 | 0.2961 | 0.0585 | 13.12 | 12.31 | 13.13 | 0.82 | 1.372 | 2.185 | 8.427 | 2.9276 | 28.62 | 5.5 | 9.1 | 2022-01-05 | Grab
2023-01-06 | 6.11 | 5.445 | 5.29 | 5.55 | 5.65 | 6.92 | 6.73 | 1.58 | 1.74 | 1.93 | 1.86 | 53 | 41 | 16 | 1 | 3 | 0 | 0.114 | 0.245 | 1.76 | 0.08 | 0.468 | 0.749 | 8.4 | 21.5 | 20.2 | 19.9 | 23.7 | 11.9 | 34.8 | 26 | 26.1 | 32.3 | 3.01 | 3.22 | 3 | 5.9 | 0.098 | 7.3 | 6.1 | 1.097 | 53.1 | 86.4 | 0.2749 | 0.0635 | 13.49 | 12.63 | 13.47 | 0.84 | 2.625 | 2.123 | 8.489 | 3.027 | 32.1 | 5.7 | 9.1 | 2022-01-06 | ^ Stuff for form dropdown menus
2023-01-07 | 6.17 | 5.51 | 5.48 | 5.71 | 5.77 | 7.09 | 6.99 | 1.64 | 1.87 | 2 | 2.01 | 51 | 44 | 17 | 0 | 1 | 0 | 0.368 | 0.249 | 1.64 | 0.094 | 0.341 | 0.523 | 8.4 | 21.3 | 20.1 | 19.9 | 24.1 | 11.9 | 34.6 | 26 | 26.3 | 33.3 | 2.93 | 3.19 | 2.9 | 6 | 0.064 | 7.4 | 6.6 | 1.1612 | 50.7 | 90.9 | 0.2942 | 0.0455 | 13.54 | 12.59 | 13.45 | 0.86 | 0 | 0 | 0 | 3.1012 | 32.05 | 5.7 | 9.2 | 2022-01-07
2023-01-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-01-08
2023-01-09 | 6.61 | 5.4 | 5.45 | 5.43 | 5.47 | 7.01 | 7.05 | 1.58 | 1.75 | 1.78 | 1.85 | 52 | 41 | 16 | 4 | 1 | 0 | 0.498 | 0.233 | 1.53 | 0.102 | 0.662 | 0.721 | 8.3 | 19.4 | 20.2 | 20.2 | 24.5 | 12.5 | 33 | 26.2 | 26.4 | 33.6 | 2.92 | 3.13 | 3.1 | 6 | 0.036 | 8.6 | 6.3 | 0.94882 | 49 | 86.5 | 0.3093 | 0.0685 | 13.08 | 12.17 | 13.02 | 0.85 | 1.523 | 2.232 | 8.279 | 2.8788 | 33.44 | 5.7 | 9.2 | 2022-01-09
2023-01-10 | 6.43 | 5.44 | 5.1 | 5.49 | 5.48 | 7.06 | 7.24 | 1.64 | 1.77 | 1.87 | 1.9 | 49 | 38 | 28 | 3 | 2 | 0 | 0.322 | 0.217 | 1.45 | 0.053 | 0.658 | 0.623 | 8.4 | 20.2 | 20.3 | 20.4 | 25.1 | 12.2 | 32.8 | 26.4 | 26.8 | 34.1 | 2.85 | 3.18 | 3 | 5.9 | 0.046 | 8 | 5.9 | 1.0934 | 51.4 | 87.9 | 0.2886 | 0.0558 | 13.82 | 12.87 | 13.73 | 0.86 | 1.548 | 2.229 | 8.861 | 3.0334 | 32.36 | 5.9 | 9.4 | 2022-01-10
2023-01-11 | 6.27 | 5.51 | 5.52 | 5.57 | 5.76 | 7.33 | 7.11 | 1.65 | 1.82 | 2.01 | 1.96 | 49 | 41 | 30 | 4 | 4 | 0 | 0.619 | 0.211 | 1.24 | 0.14 | 0.486 | 0.557 | 8.6 | 20.3 | 19.5 | 19.8 | 25.6 | 12.4 | 33.1 | 25.4 | 26.2 | 34.9 | 2.91 | 3.09 | 2.9 | 6 | 0.006 | 7.7 | 6 | 1.1315 | 54.5 | 85.7 | 0.2634 | 0.067 | 13.41 | 12.51 | 13.41 | 0.9 | 1.566 | 2.176 | 8.442 | 3.0615 | 29.85 | 5.9 | 9.6 | 2022-01-11
2023-01-12 | 6.41 | 5.41 | 5.45 | 5.59 | 5.71 | 7.01 | 6.93 | 1.69 | 1.95 | 1.96 | 1.94 | 44 | 36 | 27 | 1 | 2 | 0 | 0.683 | 0.215 | 1.21 | 0.149 | 0.391 | 0.452 | 8.5 | 20.9 | 19.2 | 20 | 28.4 | 12.1 | 34.6 | 25.1 | 26.6 | 39.6 | 2.98 | 3.09 | 2.9 | 5.9 | 0.011 | 7.6 | 5.9 | 1.0298 | 54.2 | 89.7 | 0.2647 | 0.0479 | 13.97 | 13.19 | 14.03 | 0.84 | 1.622 | 2.181 | 8.788 | 2.9598 | 29.56 | 5.9 | 9.6 | 2022-01-12
2023-01-13 | 6.73 | 5.42 | 5.34 | 5.4 | 5.43 | 7.04 | 7.1 | 1.73 | 2.11 | 2.08 | 1.97 | 50 | 44 | 18 | 2 | 2 | 0 | 0.477 | 0.22 | 1.21 | 0.126 | 0.453 | 0.471 | 8.7 | 20.1 | 19.7 | 19.5 | 30.9 | 12.6 | 34.2 | 25.8 | 25.7 | 41.7 | 3.02 | 3.17 | 2.9 | 5.9 | 0.016 | 7.9 | 5.8 | 1.1732 | 54.4 | 89.4 | 0.2645 | 0.0482 | 13.51 | 12.56 | 13.43 | 0.87 | 1.646 | 2.181 | 8.452 | 3.0432 | 30.44 | 5.7 | 9.6 | 2022-01-13
2023-01-14 | 7.61 | 5.37 | 5.32 | 5.42 | 5.41 | 7.28 | 6.95 | 1.41 | 1.7 | 1.74 | 1.69 | 44 | 39 | 18 | 1 | 5 | 0 | 0.537 | 0.254 | 1.31 | 0.154 | 0.912 | 0.816 | 8.6 | 20.1 | 19.4 | 19.3 | 26.6 | 12.5 | 33.6 | 25.9 | 25.8 | 35.6 | 2.97 | 3.11 | 2.9 | 5.7 | 0.007 | 8.2 | 5.5 | 1.3239 | 54.6 | 84.4 | 0.2645 | 0.0736 | 14.08 | 13.18 | 14.02 | 0.84 | 1.812 | 2.195 | 9.052 | 3.1139 | 31.1 | 4.2 | 9.6 | 2022-01-14
2023-01-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 1.2572 | 0 | 0 | 0 | 0 | 13.44 | 12.56 | 13.37 | 0.81 | 1.759 | 2.059 | 8.557 | 3.1372 | 0 | 5.5 | 9.6 | 2022-01-15
2023-01-16 | 7.29 | 5.4 | 5.24 | 5.43 | 5.37 | 6.55 | 6.42 | 1.27 | 1.41 | 1.64 | 1.62 | 49 | 40 | 33 | 4 | 5 | 0 | 0.864 | 0.281 | 1.79 | 0.267 | 1.14 | 1.511 | 9.6 | 22.5 | 21.2 | 20.8 | 26.8 | 14.2 | 38 | 28.2 | 28.1 | 36.6 | 2.9 | 3.07 | 2.9 | 5.9 | 0.176 | 8.7 | 6.2 | 1.5753 | 53.4 | 86.5 | 27.31 | 0.0688 | 14.85 | 13.39 | 15.09 | 1.7 | 1.709 | 2.284 | 9.457 | 3.3553 | 31.44 | 5.5 | 9.6 | 2022-01-16
2023-01-17 | 7.7 | 5.86 | 5.41 | 6.2 | 6.67 | 7.65 | 7.13 | 1.34 | 1.49 | 1.9 | 1.83 | 44 | 36 | 19 | 4 | 6 | 0 | 0.861 | 0.229 | 2.48 | 0.319 | 0.823 | 1.16 | 9.4 | 22.9 | 20.9 | 20.1 | 27.5 | 13.9 | 38.6 | 27.4 | 27.8 | 37.6 | 2.879 | 3.13 | 3 | 6.1 | 0.124 | 8.7 | 6.3 | 1.4217 | 54.2 | 87.7 | 0.2651 | 0.0571 | 13.76 | 12.97 | 13.8 | 0.83 | 1.6 | 0.986 | 8.896 | 3.2417 | 31.93 | 5.5 | 9.6 | 2022-01-17
2023-01-18 | 7.46 | 5.35 | 5.82 | 5.38 | 5.39 | 7.28 | 7.59 | 1.48 | 1.64 | 1.83 | 1.77 | 50 | 39 | 49 | 16 | 6 | o | 0.781 | 0.281 | 3.17 | 0.681 | 1.811 | 1.289 | 9.1 | 21 | 20.7 | 20.9 | 33.7 | 13.3 | 35.9 | 28 | 28.1 | 46.3 | 3.03 | 3.17 | 3 | 5.8 | 0.041 | 8.3 | 6.5 | 1.3228 | 50 | 86.2 | 0.3003 | 0.0645 | 14.58 | 13.71 | 14.59 | 0.88 | 1.584 | 2.541 | 9.803 | 3.2128 | 29.62 | 4.8 | 9.6 | 2022-01-18
2023-01-19 | 7.3 | 5.39 | 5.39 | 5.48 | 5.45 | 7.28 | 7.55 | 1.42 | 1.66 | 1.84 | 1.79 | 51 | 40 | 36 | 14 | 10 | 0 | 0.444 | 0.168 | 2.607 | 1.077 | 2.107 | 1.602 | 9.4 | 20.7 | 18.7 | 19.3 | 36.2 | 13.2 | 35 | 24.8 | 25.8 | 48.9 | 3.07 | 3.24 | 3.1 | 5.9 | 0.051 | 6.9 | 5.8 | 1.3512 | 51 | 87.4 | 0.2918 | 0.0583 | 15.85 | 13.08 | 14.06 | 0.98 | 1.486 | 2.455 | 8.543 | 3.2912 | 30.4 | 5.2 | 9.4 | 2022-01-19
2023-01-20 | 7.3 | 5.53 | 5.44 | 5.59 | 5.51 | 7.3 | 7.41 | 1.46 | 1.64 | 1.94 | 1.83 | 51 | 39 | 33 | 12 | 11 | 0 | 0.282 | 0.144 | 2.42 | 0.93 | 1.73 | 1.4 | 9.6 | 19.3 | 18.4 | 19.4 | 36.1 | 13.4 | 30.8 | 24.2 | 25.8 | 48.2 | 3.09 | 3.25 | 3.1 | 6 | 0.106 | 6.8 | 5.4 | 0.65149 | 51 | 84.4 | 0.2917 | 0.0733 | 15.77 | 13.8 | 14.63 | 0.83 | 1.442 | 2.384 | 8.767 | 2.6115 | 26.65 | 5.1 | 9.4 | 2022-01-20
2023-01-21 | 7.14 | 5.37 | 5.32 | 5.3 | 5.37 | 7.53 | 7.52 | 1.5 | 1.71 | 2.19 | 2.04 | 48 | 36 | 18 | 7 | 10 | 0 | 0.161 | 0.16 | 1.08 | 0.09 | 0.898 | 0.794 | 9.3 | 22.4 | 23.2 | 21.8 | 34.9 | 13.1 | 36.4 | 30.6 | 28.9 | 47.2 | 3.06 | 3.41 | 3 | 6.1 | 0.104 | 7.2 | 5.9 | 1.2061 | 48.4 | 85.6 | 0.3145 | 0.0673 | 13.34 | 12.26 | 13.25 | 0.99 | 1.383 | 2.38 | 8.222 | 3.2661 | 36.97 | 4.8 | 9.4 | 2022-01-21
2023-01-22 | 7.29 | 5.21 | 5.39 | 5.27 | 5.33 | 7.01 | 7.02 | 1.66 | 1.78 | 2.2 | 2.1 | 47 | 35 | 25 | 3 | 14 | 1 | 0.197 | 0.13 | 1.09 | 0.258 | 1.741 | 1.422 | 9.5 | 23 | 23.4 | 22.9 | 34.7 | 13.6 | 38.4 | 30.9 | 30.5 | 46.9 | 2.9 | 3.21 | 3 | 5.9 | 0.189 | 7.4 | 5.9 | 0.63926 | 53.2 | 86.9 | 0.2738 | 0.0607 | 13.81 | 12.79 | 13.74 | 0.95 | 1.405 | 2.37 | 8.426 | 2.7393 | 37.34 | 5 | 9.4 | 2022-01-22
2023-01-23 | 7.84 | 5.38 | 5.41 | 5.35 | 5.37 | 7.4 | 7.13 | 1.74 | 1.81 | 2.13 | 2.16 | 49 | 45 | 11 | 1 | 4 | 0 | 0.896 | 0.096 | 1.04 | 0.113 | 0.963 | 0.896 | 9.3 | 23 | 23 | 22.7 | 34.4 | 13.4 | 36.1 | 30.6 | 30.4 | 45.8 | 2.93 | 3.25 | 3.1 | 6.1 | 0.112 | 7.8 | 5.3 | 1.1273 | 53.4 | 88 | 0.2736 | 0.0554 | 13.64 | 12.57 | 13.56 | 0.99 | 1.443 | 2.305 | 8.036 | 3.2773 | 36.42 | 5.2 | 9.4 | 2022-01-23
2023-01-24 | 7.7 | 5.47 | 5.55 | 5.45 | 5.46 | 7.5 | 7.31 | 1.67 | 1.95 | 2.09 | 2.12 | 50 | 46 | 8 | 0 | 3 | 0 | 0.715 | 0.069 | 0.888 | 0.103 | 0.891 | 0.738 | 9.3 | 24.1 | 23.7 | 23.8 | 36 | 13.6 | 40.7 | 29.9 | 31.4 | 47.6 | 2.92 | 3.22 | 3.1 | 6.1 | 0.017 | 8.5 | 5.2 | 1.0619 | 53.8 | 89.6 | 0.2732 | 0.0476 | 14 | 12.9 | 13.86 | 0.96 | 1.427 | 2.217 | 9.169 | 3.1819 | 38.67 | 7.6 | 9 | 2022-01-24
2023-01-25 | 7.46 | 5.45 | 5.48 | 5.53 | 5.49 | 7.32 | 7.16 | 1.84 | 1.91 | 2.28 | 2.12 | 46 | 34 | 13 | 1 | 8 | 0 | 0.499 | 0.114 | 0.681 | 0.091 | 0.751 | 0.649 | 9.6 | 23.6 | 23.4 | 23.5 | 34.9 | 18.9 | 34.1 | 29.6 | 31.2 | 46.2 | 3.05 | 3.21 | 3.1 | 6 | 0.075 | 7.8 | 5.2 | 0.7716 | 53.4 | 89.2 | 0.2722 | 0.0492 | 13.61 | 12.55 | 13.53 | 0.98 | 1.424 | 2.235 | 8.166 | 2.8716 | 38.35 | 7.2 | 9 | 2022-01-25
2023-01-26 | 7.25 | 5.3 | 5.46 | 5.4 | 5.43 | 7.26 | 7.29 | 1.57 | 1.63 | 2.16 | 2.02 | 48 | 37 | 12 | 2 | 17 | 3 | 0.427 | 0.149 | 0.84 | 0.069 | 1.52 | 1.573 | 9.6 | 24.6 | 24.3 | 24.2 | 37.4 | 13.8 | 37.7 | 31.5 | 33.4 | 49.7 | 3.13 | 3.28 | 3 | 6 | 0.064 | 7.7 | 5.3 | 0.67345 | 52.7 | 90 | 0.2775 | 0.0456 | 13.65 | 12.59 | 13.55 | 0.96 | 1.414 | 2.245 | 8.678 | 2.7034 | 36.91 | 7.3 | 9 | 2022-01-26
2023-01-27 | 6.32 | 5.42 | 5.31 | 5.52 | 5.47 | 6.41 | 6.98 | 1.61 | 1.68 | 1.94 | 1.99 | 54 | 42 | 16 | 8 | 18 | 4 | 0.291 | 0.251 | 0.847 | 0.101 | 1.38 | 1.48 | 9.1 | 23.4 | 22.9 | 22.8 | 43.7 | 12.7 | 40.6 | 29.9 | 30.3 | 58.6 | 3.18 | 3.36 | 3.2 | 6.1 | 0.004 | 6.1 | 5.7 | 0.90173 | 57.4 | 84.6 | 0.241 | 0.0723 | 13.04 | 12.87 | 12.87 | 0 | 1.386 | 2.244 | 8.105 | 2.7917 | 35.8 | 7.5 | 9 | 2022-01-27
2023-01-28 | 6.26 | 5.57 | 5.5 | 5.61 | 5.71 | 7.73 | 6.89 | 1.48 | 1.61 | 1.94 | 1.92 | 51 | 42 | 20 | 1 | 8 | 0 | 0.414 | 0.244 | 0.891 | 0.144 | 0.924 | 1.1 | 8 | 24.4 | 24 | 23.8 | 44.6 | 10.9 | 35.5 | 31.3 | 31.5 | 59.4 | 3.24 | 3.37 | 2.9 | 6 | 0.01 | 5.7 | 5.3 | 1.1806 | 57.7 | 90.2 | 0.2384 | 0.0447 | 12.76 | 11.72 | 12.7 | 0.98 | 0 | 0 | 0 | 3.1606 | 39.14 | 7.8 | 9.2 | 2022-01-28
2023-01-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-01-29
2023-01-30 | 7.6 | 5.22 | 5.59 | 5.42 | 5.45 | 7.45 | 7.58 | 2 | 2.1 | 2.03 | 1.97 | 52 | 40 | 14 | 0 | 4 | 0 | 0.215 | 0.256 | 0.952 | 0.07 | 0.551 | 1.14 | 8.7 | 24 | 23.5 | 23.4 | 27.6 | 11.9 | 35.7 | 30.6 | 30.9 | 36.3 | 3.07 | 3.29 | 3 | 6 | 0.034 | 5.7 | 4.8 | 0.52084 | 49.7 | 89 | 0.3032 | 0.0507 | 13.5 | 12.41 | 13.36 | 0.95 | 1.375 | 2.312 | 8.345 | 2.5008 | 39.03 | 7.5 | 9.2 | 2022-01-30
2023-01-31 | 7.23 | 5.38 | 5.4 | 5.42 | 5.47 | 7.12 | 7.65 | 2 | 2.22 | 2.23 | 2.08 | 55 | 42 | 24 | 5 | 3 | 0 | 0.244 | 0.251 | 0.944 | 0.023 | 0.31 | 0.443 | 8.6 | 21.5 | 21.7 | 21.9 | 26.5 | 12 | 34.9 | 28.5 | 29 | 35.8 | 2.99 | 3.18 | 3.1 | 5.9 | 0.023 | 7 | 5.9 | 1.1055 | 49 | 87.2 | 0.3098 | 0.0594 | 13.84 | 12.69 | 13.67 | 0.98 | 1.333 | 2.331 | 8.809 | 3.1555 | 29.83 | 7.5 | 9 | 2022-01-31
2023-02-01 | 6.29 | 5.54 | 5.57 | 5.71 | 5.86 | 7.23 | 7.14 | 1.96 | 2.11 | 2.08 | 2.04 | 52 | 44 | 14 | 0 | 0 | 0 | 0.914 | 0.28 | 0.895 | 0.19 | 0.541 | 0.601 | 8.7 | 21.8 | 21.5 | 21.6 | 26.7 | 11.6 | 34.5 | 28.1 | 28.5 | 36 | 2.89 | 3.21 | 2.9 | 6 | 0.012 | 5.6 | 5.7 | 1.0719 | 53 | 91.2 | 0.2756 | 0.0397 | 13.75 | 12.75 | 13.73 | 0.98 | 1.354 | 2.337 | 8.028 | 3.0819 | 30.43 | 7.2 | 9 | 2022-02-01
2023-02-02 | 6.31 | 5.49 | 5.55 | 5.61 | 5.63 | 6.92 | 7.26 | 1.8 | 1.9 | 2.01 | 1.97 | 48 | 40 | 12 | 0 | 1 | 0 | 0.427 | 0.244 | 0.817 | 0.074 | 0.541 | 0.692 | 8.6 | 21.5 | 21.2 | 21.3 | 26.8 | 11.7 | 35 | 27.7 | 28.1 | 35.9 | 2.9 | 3.23 | 2.8 | 5.9 | 0.001 | 5.6 | 5.5 | 0.95503 | 59 | 92.5 | 0.2286 | 0.0335 | 14.19 | 13.14 | 14.15 | 1.01 | 1.334 | 2.34 | 9.363 | 2.895 | 31.16 | 7 | 9 | 2022-02-02
2023-02-03 | 6.41 | 5.69 | 5.55 | 5.65 | 5.58 | 6.86 | 6.91 | 1.76 | 1.95 | 1.97 | 1.84 | 49 | 44 | 15 | 1 | 0 | 0 | 0.47 | 0.24 | 1.01 | 0.101 | 0.406 | 0.497 | 8.7 | 21.1 | 20.7 | 20.6 | 26.5 | 11.6 | 29 | 27.1 | 27 | 35.4 | 2.97 | 3.29 | 2.9 | 5.8 | 0.014 | 5 | 5.4 | 0.98456 | 59.5 | 89.7 | 0.2281 | 0.0472 | 13.42 | 12.36 | 13.33 | 0.97 | 1.301 | 2.373 | 8.614 | 2.8346 | 31.8 | 6.4 | 9.2 | 2022-02-03
2023-02-04 | 6.39 | 5.57 | 5.59 | 5.53 | 5.5 | 7.03 | 6.95 | 1.73 | 1.92 | 1.89 | 1.8 | 48 | 44 | 14 | 0 | 0 | 0 | 0.463 | 0.237 | 0.891 | 0.1 | 0.497 | 0.503 | 8.7 | 20.5 | 20.3 | 20.3 | 26.2 | 11.5 | 28.5 | 26.4 | 26.6 | 37.7 | 2.92 | 3.25 | 2.9 | 5.9 | 0.019 | 4.7 | 5.1 | 1.0388 | 59.8 | 89.9 | 0.2279 | 0.047 | 14.38 | 13.26 | 14.24 | 0.98 | 0 | 0 | 0 | 2.8288 | 31.26 | 6.2 | 9.1 | 2022-02-04
2023-02-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.99154 | 0 | 0 | 0 | 0 | 14.82 | 13.75 | 14.76 | 1.01 | 1.407 | 2.369 | 9.171 | 2.8415 | 0 | 5.9 | 9.4 | 2022-02-05
2023-02-06 | 6.31 | 5.74 | 5.47 | 5.98 | 6.15 | 7.54 | 7.02 | 1.82 | 1.89 | 1.86 | 1.88 | 65 | 53 | 19 | 3 | 6 | 0 | 0.261 | 0.24 | 0.946 | 0.094 | 0.592 | 0.647 | 8.6 | 20.3 | 20.5 | 20.2 | 26.4 | 11.4 | 29 | 26.4 | 25.8 | 35.3 | 2.94 | 3.29 | 3 | 6.1 | 0.009 | 4.7 | 5.4 | 0.98164 | 55.4 | 90.4 | 0.2562 | 0.0439 | 14.81 | 13.8 | 14.77 | 0.97 | 1.535 | 2.394 | 9.509 | 2.8016 | 30.46 | 5.9 | 9.4 | 2022-02-06
2023-02-07 | 6.25 | 5.44 | 5.49 | 5.5 | 5.58 | 7.66 | 7.39 | 1.54 | 1.69 | 1.81 | 1.78 | 60 | 51 | 41 | 12 | 14 | 2 | 0.217 | 0.237 | 1.74 | 0.122 | 0.736 | 0.782 | 8.6 | 21.2 | 20.7 | 20 | 26.7 | 11.5 | 30.8 | 26.8 | 25.7 | 36.3 | 2.94 | 3.25 | 2.8 | 5.9 | 0.004 | 5.4 | 6 | 1.1271 | 56 | 87.8 | 0.2515 | 0.0562 | 14.57 | 13.68 | 14.65 | 0.97 | 1.508 | 2.633 | 9.293 | 2.9271 | 32.03 | 5.1 | 9.4 | 2022-02-07
2023-02-08 | 6.25 | 5.35 | 5.45 | 5.42 | 5.49 | 6.82 | 6.74 | 1.71 | 1.78 | 1.93 | 1.8 | 51 | 40 | 25 | 2 | 11 | 0 | 0.221 | 0.234 | 1.73 | 0.136 | 0.72 | 0.799 | 8.6 | 21.9 | 20.9 | 20.5 | 24.8 | 11.4 | 33.7 | 27.1 | 26.1 | 33.7 | 2.99 | 3.18 | 2.9 | 5.9 | 0.036 | 4.9 | 6 |  | 51.2 | 88.9 | 0.2902 | 0.0509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29.1 | 5.1 | 9.6 | 2022-02-08
| pH | [6 empty] | Chlorine |  |  |  | Colour | [5 empty] | Turbidity | [5 empty] | Total Dissolved Solids |  |  |  |  | Conductivity |  |  |  |  | Hardness |  | Alkalinity |  | Aluminum | Temperature |  | Cl Demand | UVT |  | UVA |  | Flows withinin plant |  |  |  | Flows from plant |  |  | Chemical Dosages
| Raw | PTC | PTC (OL) | SWC | Filter | Finish (OL) | Finish | Free | Total | Sample | Analyzer | Raw A | Raw T | SWC A | Filter A | Finish A | Finish T | Raw | Raw (OL) | SWC | Filter | Finish | Finish (OL) | Raw | PTC | SWC | Filter | Finish | Raw | PTC | SWC | Filter | Finish | Raw | Finish | Raw | Finish | Finish (Free) | Raw | Finish |  | Raw | Filter | Raw | Filter | Raw | Finish | Filter | Backwash | Bishop's | Botwood | GFW | Chlorine | Alum | Lime (Pre) | Lime (Post)
January 2022 Average | 6.94 | 5.42 | 5.42 | 5.49 | 5.54 | 7.19 | 7.15 | 1.6 | 1.78 | 1.98 | 1.93 | 49.7 | 40.22 | 21.33 | 4.48 | 5.93 | 2.67 | 0.46 | 0.22 | 1.38 | 0.21 | 0.89 | 0.9 | 8.84 | 21.62 | 21.11 | 21.02 | 30.54 | 12.82 | 35.11 | 27.58 | 27.93 | 41.13 | 3 | 3.2 | 3.01 | 5.97 | 0.06 | 7.46 | 5.75 | 1.08 | 52.34 | 87.84 | 1.28 | 0.06 | 13.76 | 12.71 | 13.61 | 0.93 | 1.53 | 2.24 | 8.66 | 3.03 | 33.11 | 5.9 | 9.28
February 2022 Average | 6.32 | 5.55 | 5.52 | 5.63 | 5.68 | 7.15 | 7.06 | 1.76 | 1.89 | 1.94 | 1.87 | 53.29 | 45.14 | 20 | 4.5 | 8 | 2 | 0.42 | 0.24 | 1.15 | 0.12 | 0.58 | 0.65 | 8.64 | 21.19 | 20.83 | 20.64 | 26.3 | 11.53 | 31.5 | 27.09 | 26.83 | 35.76 | 2.94 | 3.24 | 2.89 | 5.93 | 0.01 | 5.13 | 5.59 | 1.02 | 56.27 | 90.06 | 0.25 | 0.05 | 14.28 | 13.25 | 14.23 | 0.98 | 1.41 | 2.41 | 9 | 2.89 | 30.89 | 6.1 | 9.26
March 2022 Average | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
April 2022 Average | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
May 2022 Average | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
June 2022 Average | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
July 2022 Average | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
August 2022 Average | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
September 2022 Average | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
October 2022 Average | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
November 2022 Average | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
December 2022 Average | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2022 Average | 6.81 | 5.44 | 5.44 | 5.52 | 5.57 | 7.18 | 7.13 | 1.63 | 1.81 | 1.97 | 1.92 | 50.44 | 41.24 | 21.06 | 4.48 | 6.19 | 2.5 | 0.45 | 0.22 | 1.34 | 0.19 | 0.82 | 0.84 | 8.8 | 21.53 | 21.05 | 20.94 | 29.67 | 12.56 | 34.37 | 27.48 | 27.71 | 40.03 | 2.98 | 3.21 | 2.99 | 5.96 | 0.05 | 6.98 | 5.72 | 1.07 | 53.15 | 88.3 | 1.07 | 0.06 | 13.86 | 12.82 | 13.73 | 0.94 | 1.5 | 2.27 | 8.72 | 3 | 32.66 | 5.94 | 9.28

## 2022
Note: The password to unlock the sheets is "WTPLAB". Don't unlock any of them unless you plan on making permanent changes.
|  |  | pH | [6 empty] | Chlorine |  |  |  | Colour | [5 empty] | Turbidity | [5 empty] | Total Dissolved Solids |  |  |  |  | Conductivity |  |  |  |  | Hardness |  | Alkalinity |  | Aluminum | Temperature |  | Cl Demand | UVT |  | UVA |  | Flows withinin plant |  |  |  | Flows from plant |  |  | Chemical Dosages |  |  |  |  | Dennis Penney
Date | Shortcut | Start Time | Raw | PTC | PTC (OL) | SWC | Filter | Finish (OL) | Finish | Free | Total | Sample | Analyzer | Raw A | Raw T | SWC A | Filter A | Finish A | Finish T | Raw | Raw (OL) | SWC | Filter | Finish | Finish (OL) | Raw | PTC | SWC | Filter | Finish | Raw | PTC | SWC | Filter | Finish | Raw | Finish | Raw | Finish | Finish (Free) | Raw | Finish |  | Raw | Filter | Raw | Filter | Raw | Finish | Filter | Backwash | Bishop's | Botwood | GFW | Chlorine | Alum | Lime (Pre) | Lime (Post) | Date | Jerry Loveless
2022-01-01 | Click Here | 0 | 6.23 | 5.18 | 5.16 | 5.24 | 5.28 | 6.87 | 7.56 | 1.55 | 1.76 | 1.91 | 1.88 | 62 | 55 | 23 | 3 | 1 | 0 | 0.486 | 0.387 | 1.37 | 0.228 | 0.814 | 0.703 | 13.1 | 33.5 | 27 | 28.1 | 38.7 | 26.2 | 67 | 54 | 56.2 | 77.4 | 3.45 | 3.17 | 3 | 5.9 | 0.042 | 5.8 | 6 | 1.447 | 50.2 | 87.6 | 0.2991 | 0.0589 | 13.08 | 12 | 13.03 | 1.03 | 0 | 0 | 0 | 3.357 | 30.12 | 5.2 | 11.6 | 2022-01-01 | Nolan Simms
2022-01-02 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 1.4293 | 0 | 0 | 0 | 0 | 13.28 | 12.2 | 13.26 | 1.06 | 1.315 | 1.75 | 8.405 | 3.2993 | 0 | 5.2 | 11.8 | 2022-01-02
2022-01-03 | Click Here | 0 | 6.18 | 5.16 | 5.12 | 5.2 | 5.25 | 7.14 | 7.1 | 1.57 | 1.86 | 1.91 | 1.84 | 59 | 51 | 22 | 1 | 0 | 0 | 0.419 | 0.369 | 1.44 | 0.199 | 0.746 | 0.602 | 13.7 | 34.7 | 27.2 | 28.2 | 38.6 | 27.4 | 69.4 | 54.4 | 56.4 | 77.2 | 3.45 | 3.23 | 2.9 | 6 | 0.046 | 6.2 | 7.1 | 1.4267 | 50 | 88.1 | 0.3004 | 0.0486 | 13.96 | 12.92 | 13.98 | 0 | 1.402 | 1.854 | 8.766 | 3.2767 | 30.09 | 5.2 | 11.8 | 2022-01-03
2022-01-04 | Click Here | 0 | 6.12 | 5.1 | 5.07 | 5.17 | 5.21 | 6.49 | 6.62 | 1.45 | 1.72 | 1.88 | 1.83 | 61 | 52 | 18 | 3 | 0 | 0 | 0.474 | 0.363 | 1.31 | 0.241 | 0.776 | 0.589 | 14.4 | 35.1 | 27.1 | 28 | 34.2 | 28.8 | 70.2 | 54.2 | 56 | 68.4 | 3.44 | 3.36 | 3.1 | 5.8 | 0.174 | 6.8 | 6.6 | 1.3814 | 48.9 | 85.8 | 0.31 | 0.0665 | 13.81 | 12.78 | 13.83 | 1.05 | 1.368 | 2.283 | 8.523 | 3.2114 | 30.67 | 5.2 | 11.8 | 2022-01-04 | Continuous
2022-01-05 | Click Here | 0 | 6.27 | 5.14 | 5.19 | 5.24 | 5.25 | 6.37 | 6.22 | 1.6 | 1.91 | 1.93 | 2 | 62 | 53 | 40 | 4 | 1 | 0 | 0.458 | 0.324 | 1.63 | 0.291 | 0.491 | 0.336 | 14.4 | 34.9 | 27.4 | 29.1 | 31.2 | 28.8 | 69.8 | 54.8 | 58.2 | 62.4 | 3.41 | 3.35 | 3 | 5.7 | 0.103 | 3 | 6.1 | 1.4434 | 46.6 | 85.3 | 0.331 | 0.0691 | 14.05 | 13.07 | 14.13 | 1.06 | 1.345 | 2.465 | 8.819 | 3.3034 | 32.12 | 5.2 | 12 | 2022-01-05 | Grab
2022-01-06 | Click Here | 0 | 6.2 | 5.15 | 5.18 | 5.25 | 5.28 | 6.79 | 7 | 1.48 | 1.62 | 1.77 | 1.75 | 69 | 58 | 26 | 5 | 2 | 0 | 0.54 | 0.326 | 1.87 | 0.298 | 0.991 | 0.711 | 13 | 33.8 | 27 | 29.3 | 39.5 | 26 | 67.6 | 54 | 58.6 | 79 | 3.44 | 3.29 | 3 | 5.8 | 0.173 | 6.3 | 5.9 | 1.4193 | 45.9 | 84.3 | 0.3375 | 0.0741 | 14.43 | 13.54 | 14.47 | 0.93 | 1.377 | 2.427 | 9.039 | 3.1793 | 30.63 | 5.2 | 12 | 2022-01-06 | ^ Stuff for form dropdown menus
2022-01-07 | Click Here | 0 | 6.13 | 5.17 | 5.13 | 5.24 | 5.25 | 6.25 | 6.69 | 1.58 | 1.64 | 2.07 | 1.85 | 60 | 51 | 45 | 18 | 2 | 0 | 0.538 | 0.314 | 2.35 | 0.772 | 1.05 | 0.443 | 13.9 | 32.2 | 26.7 | 27.9 | 31.7 | 27.8 | 64.4 | 53.4 | 55.8 | 63.4 | 2.99 | 2.09 | 3.1 | 6 | 0.138 | 6.6 | 6.9 | 1.5089 | 48.4 | 85.4 | 0.3144 | 0.0684 | 13.58 | 12.59 | 13.56 | 0.97 | 1.375 | 2.228 | 8.536 | 3.4189 | 30.98 | 5 | 12.2 | 2022-01-07
2022-01-08 | Click Here | 0 | 5.77 | 5.01 | 5.08 | 5.12 | 5.14 | 6.83 | 7.38 | 1.4 | 1.56 | 2.1 | 1.93 | 56 | 48 | 33 | 4 | 0 | 0 | 0.653 | 0.331 | 1.96 | 0.653 | 1.29 | 1.005 | 13.5 | 34.2 | 27.6 | 28 | 40.2 | 27 | 68.4 | 55.2 | 56 | 80.4 | 2.83 | 2.89 | 3 | 5.9 | 0.119 | 7.1 | 5.9 | 1.4567 | 49.1 | 86.6 | 0.3081 | 0.0655 | 13.09 | 12.34 | 13.28 | 0.94 | 0 | 0 | 0 | 3.3667 | 30.98 | 5 | 13.5 | 2022-01-08
2022-01-09 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-01-09
2022-01-10 | Click Here | 0 | 6.34 | 5.14 | 4.98 | 5.28 | 5.23 | 6.65 | 6.89 | 1.52 | 1.78 | 1.94 | 1.88 | 59 | 51 | 29 | 3 | 1 | 0 | 0.518 | 0.297 | 1.92 | 0.492 | 0.699 | 0.457 | 12.7 | 34.9 | 26 | 28.1 | 36.4 | 25.4 | 69.8 | 52 | 56.2 | 72.8 | 2.88 | 2.95 | 3 | 5.7 | 0.108 | 7.5 | 5.9 | 1.3896 | 48.9 | 85.3 | 0.3683 | 0.0685 | 13.88 | 12.96 | 13.93 | 0.97 | 1.479 | 1.854 | 8.392 | 3.2596 | 30.58 | 5 | 12 | 2022-01-10
2022-01-11 | Click Here | 0 | 6.29 | 5.21 | 5.2 | 5.34 | 5.3 | 6.89 | 7.02 | 1.56 | 1.77 | 1.86 | 1.81 | 58 | 50 | 39 | 5 | 2 | 0 | 0.503 | 0.287 | 2.48 | 0.5 | 1.61 | 1.21 | 12.4 | 33.4 | 21.6 | 25.9 | 36.7 | 24.8 | 66.8 | 42.2 | 51.8 | 73.4 | 2.84 | 2.89 | 3 | 5.8 | 0.141 | 6.5 | 6.1 | 1.4875 | 48.7 | 85.1 | 0.3685 | 0.0687 | 14.66 | 11.56 | 12.49 | 0.93 | 1.471 | 1.759 | 7.972 | 3.3775 | 29.83 | 5 | 13.9 | 2022-01-11
2022-01-12 | Click Here | 0 | 5.97 | 5.09 | 5.15 | 5.36 | 5.38 | 7.02 | 7.28 | 1.6 | 2.08 | 2.01 | 1.97 | 53 | 45 | 79 | 20 | 12 | 0 | 0.684 | 0.288 | 4.42 | 0.675 | 0.869 | 0.571 | 13.1 | 31.3 | 25 | 27.8 | 39.2 | 26.2 | 62.6 | 50 | 55.6 | 78.4 | 3.31 | 3.15 | 3.1 | 6 | 0.154 | 7.8 | 5.7 | 1.0171 | 50.5 | 86 | 0.2965 | 0.0654 | 15.03 | 12.77 | 13.69 | 0.92 | 1.458 | 1.88 | 8.335 | 3.0571 | 30.75 | 5 | 13.9 | 2022-01-12
2022-01-13 | Click Here | 0 | 6.1 | 5.07 | 5.41 | 5.15 | 5.16 | 6.59 | 6.39 | 1.61 | 1.73 | 2.19 | 2.05 | 59 | 50 | 29 | 5 | 0 | 0 | 0.484 | 0.284 | 1.26 | 0.199 | 0.462 | 0.337 | 13.2 | 32.2 | 26.4 | 28.3 | 34 | 26.4 | 64.4 | 52.8 | 56.6 | 68 | 2.3 | 2.65 | 3 | 6 | 0.043 | 6.7 | 5.8 | 0.69999 | 50.3 | 83.3 | 0.2977 | 0.0792 | 12.4 | 12.28 | 12.28 | 0 | 1.466 | 2.458 | 8.283 | 2.69 | 30.04 | 5 | 13.9 | 2022-01-13
2022-01-14 | Click Here | 0 | 6.18 | 5.17 | 5.17 | 5.34 | 5.38 | 6.74 | 6.47 | 1.57 | 1.81 | 1.98 | 1.95 | 57 | 48 | 18 | 1 | 0 | 0 | 0.429 | 0.275 | 0.986 | 0.174 | 0.822 | 1.375 | 13.3 | 33.8 | 25.1 | 27.6 | 33.3 | 26.6 | 67.6 | 50.2 | 55.2 | 66.6 | 2.4 | 2.79 | 3 | 5.9 | 0.038 | 7.2 | 5.9 | 1.5291 | 51.4 | 88.2 | 0.2889 | 0.0541 | 14.18 | 12.4 | 14.3 | 1.9 | 1.464 | 1.979 | 8.431 | 3.4691 | 30.71 | 5.2 | 14.1 | 2022-01-14
2022-01-15 | Click Here | 0 | 6.17 | 5.15 | 5.13 | 5.28 | 5.35 | 7.26 | 7.48 | 1.79 | 1.98 | 2.01 | 2.06 | 67 | 59 | 11 | 1 | 0 | 0 | 0.684 | 0.29 | 1.17 | 0.103 | 0.412 | 0.479 | 12.9 | 33.5 | 25.2 | 27.2 | 38.3 | 256.8 | 67 | 50.4 | 54.4 | 76.6 | 2.45 | 2.74 | 2.9 | 6 | 0.049 | 7.4 | 5.8 | 1.2873 | 50.5 | 86.4 | 0.2967 | 0.0632 | 13.95 | 13.15 | 14.07 | 0.92 | 0 | 0 | 0 | 3.1973 | 30.39 | 5.3 | 14.1 | 2022-01-15
2022-01-16 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-01-16
2022-01-17 | Click Here | 0 | 5.74 | 5.06 | 5.06 | 5.24 | 5.25 | 6.65 | 6.91 | 1.6 | 1.78 | 2.08 | 1.93 | 67 | 58 | 27 | 9 | 0 | 0 | 0.547 | 0.226 | 1.28 | 0.392 | 2.07 | 0.737 | 13.3 | 35.7 | 26.7 | 28.5 | 38 | 26.6 | 71.4 | 53.4 | 57 | 76 | 2.9 | 3.39 | 3 | 5.9 | 0.061 | 7.4 | 6.4 | 1.1105 | 48.3 | 85.8 | 0.3155 | 0.0664 | 13.3 | 12.34 | 13.28 | 0.94 | 1.531 | 2.086 | 8.372 | 2.9205 | 30.51 | 5.3 | 14.1 | 2022-01-17
2022-01-18 | Click Here | 0 | 6.04 | 5.05 | 5.06 | 5.18 | 5.2 | 6.83 | 7.04 | 1.62 | 1.78 | 2.05 | 1.92 | 66 | 58 | 22 | 4 | 0 | 0 | 0.573 | 0.298 | 1.39 | 0.176 | 1.12 | 0.738 | 13.1 | 35.1 | 26.8 | 29.5 | 38.4 | 26.2 | 70.2 | 53.6 | 59 | 76.8 | 2.05 | 2.85 | 3.1 | 5.8 | 0.056 | 7.2 | 5.5 | 1.335 | 45.4 | 86 | 0.3423 | 0.0654 | 13.6 | 12.64 | 13.57 | 0.93 | 1.481 | 2.008 | 8.614 | 3.265 | 30.04 | 5.3 | 14.1 | 2022-01-18
2022-01-19 | Click Here | 0 | 6.18 | 5.15 | 5.03 | 5.26 | 5.3 | 6.92 | 6.77 | 1.51 | 1.6 | 1.88 | 1.94 | 60 | 54 | 20 | 1 | 0 | 0 | 0.499 | 0.289 | 1.17 | 0.182 | 0.811 | 0.484 | 12.8 | 35.8 | 26.1 | 29 | 37.4 | 25.8 | 71.6 | 52.2 | 58 | 74.8 | 2.21 | 2.89 | 2.9 | 5.8 | 0.031 | 7.8 | 5.6 | 1.2592 | 48.2 | 86.2 | 0.3163 | 0.0644 | 13.02 | 12.96 | 12.96 | 0 | 1.479 | 1.977 | 8.428 | 3.1892 | 30.19 | 5.4 | 14.5 | 2022-01-19
2022-01-20 | Click Here | 0 | 6.14 | 5.1 | 5.15 | 5.27 | 5.7 | 6.98 | 6.85 | 1.39 | 1.56 | 1.94 | 1.99 | 58 | 50 | 19 | 0 | 0 | 0 | 0.486 | 0.298 | 1.14 | 0.186 | 0.914 | 0.778 | 12.3 | 35.4 | 25.7 | 28.4 | 35.2 | 24.6 | 70.8 | 51.4 | 56.8 | 70.4 | 2.14 | 2.83 | 3 | 5.8 | 0.029 | 7.2 | 6.6 | 1.6047 | 45.7 | 86.3 | 0.3394 | 0.0639 | 13.4 | 12.55 | 13.5 | 0.95 | 1.466 | 1.975 | 8.46 | 3.5047 | 29.76 | 5.4 | 14.5 | 2022-01-20
2022-01-21 | Click Here | 0 | 5.83 | 5.09 | 5.28 | 5.16 | 5.15 | 6.72 | 6.91 | 1.46 | 1.75 | 1.83 | 1.81 | 59 | 52 | 20 | 1 | 0 | 0 | 0.417 | 0.326 | 1.18 | 0.191 | 0.586 | 0.427 | 12.4 | 35.2 | 25.8 | 28.7 | 35.7 | 24.8 | 70.4 | 51.6 | 57.4 | 71.4 | 2.19 | 2.85 | 3 | 5.8 | 0.037 | 7.2 | 6.7 | 1.0591 | 45.9 | 86.6 | 0.3396 | 0.0636 | 12.78 | 11.88 | 12.8 | 0.92 | 1.463 | 1.981 | 8 | 2.9491 | 30.84 | 5.5 | 14.6 | 2022-01-21
2022-01-22 | Click Here | 0 | 5.81 | 5.03 | 4.97 | 5.16 | 5.14 | 6.69 | 7.15 | 1.61 | 1.79 | 1.87 | 1.89 | 58 | 51 | 24 | 2 | 0 | 0 | 0.546 | 0.296 | 1.66 | 0.203 | 0.629 | 0.514 | 12.8 | 33.6 | 26.4 | 29.8 | 38.1 | 25.6 | 67.2 | 52.8 | 59.6 | 76.2 | 2.15 | 2.81 | 3 | 5.8 | 0.061 | 6.7 | 5.8 | 1.4271 | 45.8 | 85.4 | 0.3397 | 0.0684 | 12.99 | 11.99 | 12.96 | 0.97 | 0 | 0 | 0 | 3.3571 | 29.73 | 5.5 | 14.6 | 2022-01-22
2022-01-23 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 1.4292 | 0 | 0 | 0 | 0 | 13.57 | 12.64 | 13.56 | 0.92 | 1.491 | 1.978 | 8.191 | 3.2692 | 29.04 | 5.4 | 14.6 | 2022-01-23
2022-01-24 | Click Here | 0 | 6 | 5.01 | 5.24 | 5.06 | 5.2 | 7.25 | 7.07 | 1.53 | 1.61 | 1.89 | 1.94 | 57 | 48 | 19 | 1 | 0 | 0 | 0.481 | 0.291 | 1.33 | 0.214 | 0.924 | 0.901 | 12.1 | 33.3 | 26.1 | 25.7 | 37.3 | 24.2 | 66.6 | 52.2 | 51.4 | 74.6 | 2.33 | 2.77 | 2.9 | 5.9 | 0.064 | 7.1 | 5.5 | 1.4136 | 43.9 | 88.9 | 0.3571 | 0.0507 | 13.59 | 12.67 | 13.61 | 0.94 | 1.461 | 1.978 | 8.371 | 3.2536 | 29.04 | 5.4 | 14.6 | 2022-01-24
2022-01-25 | Click Here | 0 | 5.98 | 5.02 | 5.06 | 5.18 | 5.26 | 6.8 | 6.86 | 1.44 | 1.67 | 1.83 | 1.82 | 59 | 50 | 21 | 1 | 0 | 0 | 0.627 | 0.297 | 1.44 | 0.267 | 0.998 | 0.945 | 11.9 | 34.4 | 26 | 25.4 | 34.9 | 23.8 | 68.8 | 52 | 50.8 | 69.8 | 2.18 | 2.68 | 2.7 | 5.9 | 0.044 | 7.7 | 6 | 1.5286 | 45 | 87.8 | 0.3463 | 0.0563 | 13.28 | 12.22 | 13.17 | 0.95 | 1.429 | 1.981 | 8.007 | 3.3586 | 29.92 | 5.4 | 14.6 | 2022-01-25
2022-01-26 | Click Here | 0 | 5.84 | 4.82 | 5.04 | 5.09 | 5.04 | 6.63 | 7.08 | 1.44 | 1.69 | 1.83 | 1.8 | 72 | 69 | 38 | 4 | 2 | 0 | 0.526 | 0.296 | 2.04 | 0.248 | 0.792 | 0.694 | 11.6 | 33.6 | 25.3 | 25 | 36.6 | 23.2 | 67.2 | 50.6 | 50 | 73.2 | 2.23 | 2.77 | 2.9 | 5.8 | 0.052 | 7.9 | 5.4 | 1.3916 | 42.6 | 81.8 | 0.37 | 0.0871 | 12.73 | 11.89 | 12.83 | 0.94 | 1.447 | 1.981 | 8.272 | 3.3216 | 33.2 | 5.5 | 14.8 | 2022-01-26
2022-01-27 | Click Here | 0 | 6.01 | 6.02 | 5.42 | 6.21 | 5.51 | 5.31 | 5.87 | 1.89 | 2.09 | 2.04 | 2.01 | 91 | 85 | 39 | 4 | 2 | 0 | 0.614 | 0.216 | 2.69 | 0.336 | 0.607 | 0.421 | 11.9 | 39.2 | 31.1 | 31.4 | 33.7 | 23.8 | 78.4 | 62.2 | 62.8 | 67.4 | 2.18 | 2.73 | 2.9 | 5.6 | 0.206 | 7.4 | 5.1 | 1.4602 | 43.2 | 98.4 | 0.3641 | 0.0069 | 13.45 | 12.55 | 13.49 | 0.94 | 1.432 | 1.978 | 8.483 | 3.3502 | 29.7 | 5.5 | 14.8 | 2022-01-27
2022-01-28 | Click Here | 0 | 5.83 | 5.02 | 5.08 | 5.14 | 5.23 | 7.14 | 7.22 | 1.69 | 1.82 | 2.18 | 1.82 | 73 | 60 | 35 | 7 | 7 | 0 | 0.467 | 0.281 | 1.81 | 0.325 | 0.702 | 0.552 | 11.5 | 33.2 | 26.1 | 25.6 | 39.2 | 23 | 66.4 | 52.2 | 51.2 | 78.4 | 2.29 | 2.43 | 2.6 | 5.6 | 0.042 | 6.7 | 5.7 | 0.90946 | 43.1 | 89 | 0.3647 | 0.0506 | 13.37 | 12.47 | 13.37 | 0.9 | 1.423 | 1.979 | 8.907 | 2.7295 | 30.98 | 5.6 | 15 | 2022-01-28
2022-01-29 | Click Here | 0 | 5.7 | 5.13 | 5.2 | 5.28 | 5.33 | 7.26 | 7.5 | 1.72 | 1.84 | 2.16 | 1.95 | 75 | 65 | 31 | 4 | 3 | 0 | 0.466 | 0.284 | 1.7 | 0.089 | 0.745 | 0.518 | 11.8 | 33.4 | 25.7 | 26.4 | 41.3 | 23.6 | 66.8 | 51.4 | 52.8 | 82.6 | 2.53 | 2.57 | 2.9 | 5.7 | 0.039 | 7.1 | 5.3 |  | 42.5 | 90.6 | 0.3711 | 0.0427 | 13.14 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30.04 | 6.6 | 14.4 | 2022-01-29
2022-01-30 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-01-30
2022-01-31 | Click Here | 0 | 5.67 | 5.21 | 5.22 | 5.25 | 5.26 | 6.84 | 6.94 | 1.75 | 1.94 | 1.99 | 1.86 | 64 | 56 | 17 | 0 | 0 | 0 | 0.56 | 0.274 | 1.29 | 0.18 | 0.501 | 0.413 | 12.9 | 34.1 | 26 | 27.1 | 40.2 | 25.8 | 68.2 | 52 | 54.2 | 80.4 | 2.5 | 2.6 | 3 | 5.9 | 0.084 | 3 | 5.9 |  | 46 | 89.2 | 0.3371 | 0.0496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28.6 | 7.2 | 13.8 | 2022-01-31
2022-02-01 | Click Here | 0 | 5.95 | 5.15 | 5.33 | 5.27 | 5.29 | 7.19 | 7 | 1.83 | 1.94 | 2.03 | 1.91 | 75 | 68 | 30 | 1 | 0 | 0 | 0.494 | 0.292 | 1.53 | 0.122 | 0.713 | 0.655 | 11.5 | 34.5 | 26 | 27.1 | 42.8 | 23 | 69 | 52 | 54.2 | 86.6 | 2.53 | 2.64 | 3 | 6.4 | 0.039 | 7.3 | 5.1 | 1.2989 | 41.9 | 89.6 | 0.3771 | 0.0476 | 13.37 | 12.44 | 13.37 | 0.93 | 1.454 | 2.021 | 8.326 | 3.2189 | 29.3 | 7.3 | 14 | 2022-02-01
2022-02-02 | Click Here | 0 | 5.92 | 5.24 | 5.24 | 5.31 | 5.33 | 7.18 | 7.03 | 1.73 | 1.92 | 1.99 | 1.82 | 70 | 61 | 30 | 3 | 1 | 0 | 0.472 | 0.278 | 2.14 | 0.198 | 0.475 | 0.345 | 11.8 | 32.5 | 26.2 | 26.4 | 40.8 | 23.6 | 65 | 52.4 | 52.8 | 81.6 | 2.77 | 2.72 | 3.2 | 5.7 | 0.036 | 7 | 5.3 | 0.97456 | 42.9 | 86.3 | 0.367 | 0.0638 | 13.36 | 12.36 | 13.31 | 0.95 | 1.452 | 2.032 | 8.289 | 2.8346 | 30.98 | 7.1 | 14 | 2022-02-02
2022-02-03 | Click Here | 0 | 5.81 | 5.35 | 5.23 | 5.38 | 5.39 | 7.22 | 7.78 | 1.64 | 1.79 | 1.93 | 1.8 | 63 | 52 | 35 | 6 | 0 | 0 | 0.451 | 0.277 | 2.11 | 0.137 | 0.348 | 0.333 | 11.6 | 31.4 | 25.5 | 26.2 | 41 | 23.2 | 62.8 | 51 | 52.4 | 82 | 2.64 | 2.78 | 3.2 | 5.9 | 0.033 | 7 | 5.3 | 1.3383 | 43.3 | 87.1 | 0.3634 | 0.0599 | 13.33 | 12.4 | 13.34 | 0.94 | 1.46 | 2.033 | 8.17 | 3.1483 | 29.8 | 7.1 | 14 | 2022-02-03
2022-02-04 | Click Here | 0 | 6.09 | 5.35 | 5.35 | 5.33 | 5.51 | 7.9 | 7.7 | 1.74 | 1.84 | 1.84 | 1.78 | 71 | 65 | 39 | 4 | 0 | 0 | 0.741 | 0.276 | 2.17 | 0.177 | 0.386 | 0.209 | 11.9 | 32.5 | 24.6 | 24.7 | 39.6 | 23.8 | 65 | 49.2 | 49.4 | 79.2 | 2.6 | 2.84 | 3 | 6.1 | -0.027 | 7.5 | 5.8 | 1.3417 | 42.9 | 88.2 | 0.3681 | 0.0544 | 13.16 | 12.27 | 13.2 | 0.93 | 1.423 | 2.024 | 7.773 | 3.1517 | 28.95 | 7.1 | 14 | 2022-02-04
2022-02-05 | Click Here | 0 | 6.04 | 5.26 | 5.36 | 5.29 | 5.46 | 7.47 | 7.67 | 1.67 | 1.89 | 1.8 | 1.77 | 68 | 61 | 30 | 1 | 0 | 0 | 0.617 | 0.267 | 1.98 | 0.144 | 0.298 | 0.316 | 12.2 | 32.8 | 26.4 | 26 | 38.8 | 24.4 | 65.6 | 52.8 | 52 | 77.6 | 2.67 | 2.96 | 3 | 5.9 | 0.149 | 7 | 5.3 | 1.3205 | 49 | 95.2 | 0.3092 | 0.0214 | 12.89 | 11.91 | 12.86 | 0.95 | 0 | 0 | 0 | 3.1105 | 29.68 | 7 | 14 | 2022-02-05
2022-02-06 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-02-06
2022-02-07 | Click Here | 0 | 5.47 | 5.11 | 5.26 | 5.26 | 5.4 | 7.26 | 7.15 | 1.34 | 1.43 | 1.98 | 1.88 | 63 | 53 | 22 | 3 | 2 | 0 | 0.504 | 0.265 | 1.7 | 0.134 | 0.487 | 0.367 | 12.4 | 34.3 | 26.4 | 26.1 | 39 | 24.8 | 68.6 | 52.8 | 52.2 | 78 | 2.91 | 3.19 | 2.9 | 5.8 | 0.028 | 6.9 | 5.2 | 1.0823 | 49.5 | 99 | 0.3046 | 0.0044 | 12.55 | 12.03 | 12.95 | 0.92 | 1.423 | 2.017 | 7.735 | 2.9123 | 30.28 | 7 | 14 | 2022-02-07
2022-02-08 | Click Here | 0 | 5.81 | 5.28 | 5.28 | 5.4 | 5.37 | 7.31 | 7.5 | 1.34 | 1.64 | 1.9 | 1.72 | 62 | 51 | 20 | 2 | 1 | 0 | 0.538 | 0.269 | 5.38 | 0.63 | 0.542 | 0.519 | 12.1 | 33.2 | 23.7 | 26.2 | 40.8 | 24.2 | 66.4 | 47.4 | 52.4 | 81.6 | 2.71 | 2.93 | 3.2 | 5.9 | 0.042 | 6.8 | 5.3 | 1.2919 | 48.7 | 95.8 | 0.3314 | 0.0201 | 13.13 | 12.75 | 13.72 | 0.97 | 2.983 | 2.001 | 8.186 | 3.0619 | 30.04 | 7.2 | 14 | 2022-02-08
2022-02-09 | Click Here | 0 | 5.96 | 5.08 | 5.28 | 5.41 | 5.34 | 7.12 | 6.67 | 1.68 | 1.77 | 1.88 | 1.81 | 69 | 62 | 24 | 3 | 0 | 0 | 0.49 | 0.295 | 2.4 | 0.233 | 0.253 | 0.187 | 12.5 | 33.2 | 25.2 | 25 | 34 | 25 | 66.4 | 50.4 | 50 | 68 | 2.77 | 2.95 | 3 | 5.8 | 0.024 | 7.2 | 5.8 | 1.1622 | 45.4 | 87.3 | 0.3422 | 0.0587 | 16.15 | 14.11 | 15.09 | 0.98 | 1.796 | 1.996 | 9.607 | 2.9122 | 29.6 | 7.2 | 14 | 2022-02-09
2022-02-10 | Click Here | 0 | 6.01 | 5.11 | 5.13 | 5.29 | 5.31 | 7.39 | 7.48 | 1.61 | 1.74 | 1.81 | 1.84 | 65 | 58 | 10 | 1 | 0 | 0 | 0.391 | 0.037 | 0.682 | 0.174 | 0.292 | 0.786 | 12.4 | 32.1 | 24.3 | 25.6 | 38.5 | 24.8 | 64.2 | 48.6 | 51.2 | 77 | 2.69 | 2.95 | 2.9 | 6 | 0.034 | 7.6 | 5.6 | 0.91712 | 43.8 | 87.9 | 0.3579 | 0.0556 | 13.86 | 12.8 | 13.75 | 0.95 | 1.494 | 1.997 | 9.328 | 2.7371 | 29.62 | 7.2 | 14 | 2022-02-10
2022-02-11 | Click Here | 0 | 5.52 | 5.07 | 5.11 | 5.12 | 5.2 | 6.93 | 7.42 | 1.44 | 1.73 | 1.87 | 1.83 | 79 | 68 | 34 | 3 | 1 | 0 | 1.08 | 0.871 | 1.71 | 0.2 | 0.59 | 0.349 | 12.1 | 34.3 | 26.5 | 26.8 | 38.4 | 24.2 | 58.6 | 53 | 53.6 | 76.8 | 2.72 | 2.9 | 3 | 5.7 | 0.14 | 7.2 | 5 | 0.66546 | 45.1 | 89.5 | 0.3456 | 0.048 | 13.16 | 13.08 | 13.08 | 0 | 1.429 | 2.004 | 8.189 | 2.5255 | 30.76 | 7.2 | 14 | 2022-02-11
2022-02-12 | Click Here | 0 | 6.18 | 5.22 | 5.25 | 5.25 | 5.27 | 6.89 | 7.26 | 1.54 | 1.7 | 1.95 | 1.93 | 72 | 64 | 22 | 1 | 0 | 0 | 0.434 | 0.282 | 1.55 | 0.146 | 0.414 | 0.375 | 12.3 | 32.1 | 26 | 26.4 | 37.6 | 24.6 | 64.2 | 52 | 52.8 | 75.2 | 2.75 | 2.92 | 3 | 5.8 | 0.058 | 6.9 | 5.2 | 1.0546 | 45.3 | 89.8 | 0.3455 | 0.0474 | 12.39 | 11.39 | 12.35 | 0.96 | 1.35 | 1.997 | 7.6 | 3.0146 | 28.78 | 7.2 | 14 | 2022-02-12
2022-02-13 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.86822 | 0 | 0 | 0 | 0 | 12.63 | 12.56 | 12.56 | 0 | 1.373 | 1.99 | 7.885 | 2.8382 | 0 | 7.2 | 14.2 | 2022-02-13
2022-02-14 | Click Here | 0 | 5.97 | 5.12 | 5.24 | 5.3 | 5.33 | 6.87 | 7.26 | 1.56 | 1.79 | 1.94 | 1.96 | 68 | 60 | 17 | 0 | 0 | 0 | 0.435 | 0.275 | 1.43 | 0.237 | 1.14 | 0.994 | 12.3 | 33.6 | 26.1 | 26.4 | 38 | 24.6 | 67.2 | 52.2 | 52.8 | 76 | 2.71 | 2.96 | 2.9 | 5.9 | 0.018 | 7.1 | 5.9 | 1.1311 | 45.3 | 85.8 | 0.3432 | 0.0661 | 13.29 | 12.36 | 13.31 | 0.95 | 1.442 | 1.986 | 8.437 | 3.0711 | 29.71 | 7.2 | 14.2 | 2022-02-14
2022-02-15 | Click Here | 0 | 6 | 5.07 | 5.12 | 5.11 | 5.21 | 6.59 | 6.63 | 1.47 | 1.69 | 1.97 | 1.93 | 64 | 56 | 12 | 0 | 0 | 0 | 0.46 | 0.255 | 1.8 | 0.192 | 0.741 | 0.981 | 12.6 | 33.1 | 26.2 | 26.1 | 33.5 | 25.2 | 66.2 | 52.4 | 52.2 | 67 | 2.85 | 2.96 | 3 | 5.9 | 0.005 | 6.5 | 5 | 1.1864 | 47.1 | 85.1 | 0.3269 | 0.0698 | 13.19 | 12.24 | 13.18 | 0.94 | 1.48 | 1.977 | 8.4909 | 3.0964 | 31.76 | 7.2 | 14.4 | 2022-02-15
2022-02-16 | Click Here | 0 | 5.91 | 5.09 | 5.15 | 5.18 | 5.2 | 6.84 | 6.59 | 1.41 | 1.63 | 1.8 | 1.83 | 68 | 60 | 19 | 1 | 0 | 0 | 0.514 | 0.271 | 1.49 | 0.298 | 0.926 | 1.154 | 11.2 | 30.7 | 24.2 | 24.5 | 31.9 | 22.4 | 61.4 | 48.4 | 49 | 63.8 | 2.71 | 2.91 | 3 | 6 | 0.01 | 7.3 | 5.7 | 0.96182 | 52.3 | 87.5 | 0.2807 | 0.0579 | 13.23 | 13.14 | 13.14 | 0 | 1.668 | 1.976 | 8.929 | 2.8418 | 30.02 | 7.2 | 14.4 | 2022-02-16
2022-02-17 | Click Here | 0 | 5.96 | 5.09 | 5.12 | 5.24 | 5.29 | 6.97 | 7.04 | 1.59 | 1.64 | 1.86 | 1.83 | 67 | 58 | 19 | 0 | 0 | 0 | 0.417 | 0.279 | 1.54 | 0.211 | 0.709 | 0.683 | 10.9 | 30.8 | 23.4 | 24.3 | 33.3 | 21.8 | 61.6 | 46.8 | 48.6 | 66.6 | 2.94 | 3.08 | 2.8 | 5.9 | 0.01 | 7.9 | 5.5 | 1.1716 | 46.7 | 89 | 0.3305 | 0.0503 | 13.31 | 12.22 | 13.13 | 0.91 | 1.413 | 2.004 | 8.46 | 3.0316 | 28.57 | 7.4 | 14.8 | 2022-02-17
2022-02-18 | Click Here | 0 | 5.8 | 5.06 | 5.12 | 5.19 | 5.28 | 6.8 | 7.2 | 1.62 | 1.81 | 1.91 | 1.83 | 66 | 56 | 17 | 1 | 0 | 0 | 0.416 | 0.282 | 1.96 | 0.259 | 0.514 | 0.438 | 11.2 | 31 | 23.8 | 24.1 | 34.9 | 22.4 | 62 | 47.6 | 48.2 | 69.8 | 2.85 | 2.98 | 3.1 | 5.8 | 0.021 | 7.9 | 5.5 | 1.1058 | 46.6 | 89.3 | 0.3294 | 0.0491 | 13.79 | 12.87 | 13.8 | 0.93 | 1.812 | 2.008 | 7.998 | 2.9558 | 29.81 | 7.6 | 15 | 2022-02-18
2022-02-19 | Click Here | 0 | 5.97 | 5.2 | 5.14 | 5.25 | 5.25 | 6.75 | 6.85 | 1.62 | 1.79 | 1.86 | 1.8 | 64 | 53 | 16 | 1 | 0 | 0 | 0.652 | 0.436 | 1.49 | 0.191 | 0.782 | 0.769 | 11 | 31.6 | 29.4 | 26.3 | 35.1 | 22 | 63.2 | 58.8 | 52.6 | 70.2 | 2.84 | 3.13 | 3 | 5.9 | 0.024 | 7.7 | 5.4 | 1.1893 | 46.8 | 90 | 0.3298 | 0.0492 | 13.46 | 12.35 | 13.3 | 0.95 | 0 | 0 | 0 | 2.9993 | 29.57 | 7.6 | 15 | 2022-02-19
2022-02-20 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-02-20
2022-02-21 | Click Here | 0 | 5.68 | 5.12 | 5.22 | 5.21 | 5.24 | 6.8 | 7.37 | 1.41 | 1.58 | 1.89 | 1.77 | 68 | 57 | 40 | 6 | 10 | 0 | 0.519 | 0.358 | 2.13 | 0.313 | 1.09 | 0.907 | 10.7 | 28.8 | 23.3 | 23.8 | 35.5 | 21.4 | 57.6 | 46.6 | 47.6 | 71 | 2.91 | 3.19 | 3.1 | 5.9 | 0.058 | 3.1 | 5.9 | 1.0677 | 45.1 | 87.5 | 0.3455 | 0.058 | 12.89 | 12.17 | 12.92 | 0.75 | 1.408 | 2.02 | 8.593 | 2.9277 | 30.04 | 7.6 | 17 | 2022-02-21
2022-02-22 | Click Here | 0 | 5.81 | 5.09 | 5.12 | 5.19 | 5.24 | 7.04 | 7.12 | 1.5 | 1.62 | 1.86 | 1.83 | 69 | 58 | 29 | 2 | 1 | 0 | 0.492 | 0.376 | 1.94 | 0.284 | 0.926 | 1.01 | 11.2 | 30.4 | 24.1 | 24.8 | 36.3 | 22.4 | 60.8 | 48.2 | 49.6 | 72.6 | 2.95 | 3.13 | 2.9 | 6 | 0.047 | 7.4 | 5.4 | 1.2576 | 45.9 | 88.9 | 0.3404 | 0.0508 | 13.7 | 12.71 | 13.66 | 0.95 | 1.46 | 2.008 | 8.762 | 3.0576 | 29.36 | 7.6 | 17 | 2022-02-22
2022-02-23 | Click Here | 0 | 5.64 | 5.08 | 5.13 | 5.21 | 5.23 | 6.86 | 7.15 | 1.39 | 1.56 | 1.93 | 1.79 | 77 | 65 | 35 | 5 | 11 | 0 | 0.613 | 0.358 | 2.02 | 0.17 | 0.819 | 1.021 | 9.2 | 29.5 | 22.8 | 23.2 | 32.1 | 18.4 | 59 | 45.6 | 46.4 | 64.2 | 2.88 | 3.35 | 3 | 6 | 0.044 | 6.9 | 5.3 | 0.77066 | 46.1 | 88.9 | 0.3389 | 0.0502 | 13.67 | 12.85 | 13.79 | 0.92 | 1.418 | 2.019 | 8.416 | 2.5707 | 30.04 | 7.6 | 17 | 2022-02-23
2022-02-24 | Click Here | 0 | 5.53 | 5.03 | 5.12 | 5.16 | 5.18 | 6.95 | 7.25 | 1.38 | 1.49 | 1.84 | 1.78 | 76 | 65 | 7 | 6 | 10 | 0 | 0.629 | 0.397 | 2.18 | 0.258 | 1.09 | 0.904 | 9.9 | 29 | 23.4 | 23.2 | 33.9 | 19.8 | 58 | 46.8 | 46.4 | 67.8 | 3.09 | 3.22 | 3.1 | 5.9 | 0.075 | 7.7 | 5.3 | 0.85694 | 44.4 | 85.6 | 0.3517 | 0.0673 | 12.74 | 12.72 | 12.72 | 0 | 1.317 | 2.006 | 8.115 | 2.5969 | 29.81 | 8 | 17 | 2022-02-24
2022-02-25 | Click Here | 0 | 5.64 | 5.14 | 5.11 | 5.18 | 5.24 | 7.098 | 7.37 | 1.44 | 1.61 | 1.77 | 1.73 | 79 | 69 | 11 | 4 | 7 | 0 | 0.698 | 0.504 | 1.97 | 0.204 | 1.12 | 1.402 | 9.4 | 29.1 | 22.8 | 23.3 | 34.1 | 18.8 | 58.2 | 45.6 | 46.6 | 68.2 | 3.1 | 3.29 | 3 | 5.6 | 0.061 | 7.3 | 5.6 | 1.3665 | 44.5 | 87.4 | 0.331 | 0.058 | 13.15 | 12.18 | 13.11 | 0.93 | 1.357 | 2.004 | 8.769 | 3.1165 | 30.08 | 8.8 | 17 | 2022-02-25
2022-02-26 | Click Here | 0 | 5.87 | 5.01 | 5.09 | 5.14 | 5.17 | 6.94 | 7.16 | 1.39 | 1.54 | 1.82 | 1.77 | 74 | 68 | 19 | 1 | 2 | 0 | 0.633 | 0.501 | 1.85 | 0.167 | 0.712 | 0.646 | 9.2 | 29.6 | 22.6 | 22.8 | 33.4 | 18.4 | 59.2 | 45.2 | 45.6 | 66.8 | 3.03 | 3.22 | 2.9 | 5.9 | 0.043 | 7.4 | 5.7 | 1.0718 | 43.6 | 87.1 | 0.3482 | 0.0599 | 13.28 | 12.33 | 13.28 | 0.95 | 0 | 0 | 0 | 2.8418 | 29.03 | 8.8 | 14 | 2022-02-26
2022-02-27 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-02-27
2022-02-28 | Click Here | 0 | 5.49 | 5.01 | 5.1 | 5.1 | 5.07 | 6.44 | 6.89 | 1.43 | 1.51 | 1.79 | 1.65 | 77 | 68 | 37 | 7 | 11 | 0 | 0.738 | 0.528 | 2.68 | 0.501 | 0.821 | 0.887 | 8.9 | 29.4 | 23.8 | 23.1 | 30.4 | 17.8 | 58.8 | 47.6 | 46.2 | 60.8 | 3.05 | 3.16 | 3.1 | 6 | 0.037 | 7.3 | 0 | 0 | 43.9 | 86 | 0.3569 | 0.0655 | 13.63 | 12.7 | 13.66 | 0.96 | 1.51 | 2.007 | 8.227 | 2.601 | 29.34 | 9.2 | 14 | 2022-02-28
2022-03-01 | Click Here | 0 | 5.63 | 5.06 | 5.1 | 5.17 | 5.19 | 6.92 | 6.81 | 1.43 | 1.51 | 1.87 | 1.73 | 76 | 67 | 35 | 6 | 8 | 0 | 0.569 | 0.542 | 2.53 | 0.205 | 0.993 | 0.918 | 8.6 | 29.2 | 23.3 | 24.1 | 31.8 | 17.2 | 58.4 | 46.6 | 48.2 | 63.6 | 2.98 | 3.38 | 2.8 | 5.8 | 0.042 | 7.1 | 5.1 | 1.0117 | 44.1 | 86.5 | 0.3558 | 0.0641 | 13.39 | 12.46 | 13.43 | 0.95 | 1.546 | 2.009 | 8.425 | 2.7317 | 30.04 | 9.2 | 16 | 2022-03-01
2022-03-02 | Click Here | 0 | 5.94 | 4.97 | 5.11 | 5.12 | 5.09 | 6.44 | 6.3 | 1.35 | 1.41 | 1.62 | 1.57 | 81 | 74 | 30 | 4 | 9 | 0 | 0.621 | 0.482 | 2.55 | 0.294 | 1.07 | 1.136 | 8.6 | 30.7 | 23 | 23.3 | 30.4 | 17.2 | 61.4 | 46 | 46.6 | 60.8 | 3.04 | 3.33 | 3 | 5.7 | 0.047 | 8.3 | 5.3 | 0.88531 | 45.5 | 85.7 | 0.3406 | 0.0669 | 13.48 | 13.46 | 13.46 | 0 | 1.557 | 2.007 | 8.891 | 2.4953 | 30.02 | 9.2 | 16 | 2022-03-02
2022-03-03 | Click Here | 0 | 5.92 | 4.98 | 5.07 | 5.14 | 5.19 | 6.74 | 6.64 | 1.14 | 1.29 | 1.61 | 1.59 | 74 | 67 | 26 | 4 | 8 | 0 | 0.655 | 0.487 | 2.47 | 0.214 | 1.26 | 1.298 | 8.9 | 31 | 23.5 | 23.4 | 28.1 | 17.8 | 62 | 47 | 46.8 | 56.2 | 2.94 | 3.29 | 2.8 | 5.8 | 0.057 | 8.9 | 5.9 | 1.0247 | 43.1 | 84.2 | 0.3647 | 0.0744 | 13.83 | 12.88 | 13.85 | 0.97 | 1.527 | 2.003 | 8.362 | 2.5647 | 29.64 | 9.2 | 16 | 2022-03-03
2022-03-04 | Click Here | 0 | 5.98 | 5.06 | 5.08 | 5.12 | 5.17 | 6.99 | 6.94 | 1.21 | 1.37 | 1.53 | 1.45 | 72 | 65 | 29 | 5 | 7 | 0 | 0.642 | 0.486 | 2.59 | 0.386 | 1.516 | 1.734 | 9.1 | 31.6 | 23.2 | 23.4 | 27.3 | 18.2 | 63.2 | 46.4 | 46.8 | 54.6 | 2.91 | 3.29 | 2.9 | 5.9 | 0.059 | 8.8 | 5.7 | 1.0508 | 43.2 | 84.6 | 0.3645 | 0.0741 | 13.57 | 12.75 | 13.71 | 0.96 | 1.495 | 1.998 | 8.865 | 2.5908 | 30.04 | 8 | 18 | 2022-03-04
2022-03-05 | Click Here | 0 | 6.19 | 5.06 | 5.09 | 5.11 | 5.13 | 6.83 | 6.67 | 1.3 | 1.46 | 1.58 | 1.61 | 74 | 63 | 32 | 4 | 3 | 0 | 0.577 | 0.486 | 2.41 | 0.361 | 1.31 | 1.2 | 8.6 | 28.1 | 21.3 | 21.1 | 24.1 | 17.2 | 56.2 | 42.6 | 42.2 | 48.2 | 2.93 | 3.22 | 2.9 | 5.8 | 0.068 | 8.1 | 6.6 | 1.2955 | 43.4 | 84.8 | 0.3643 | 0.0738 | 13.32 | 12.31 | 13.28 | 0.97 | 0 | 0 | 0 | 2.9055 | 29.95 | 8 | 14 | 2022-03-05
2022-03-06 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 1.3986 | 0 | 0 | 0 | 0 | 13.28 | 12.36 | 13.27 | 0.91 | 12.62 | 2.005 | 8.505 | 2.9286 | 0 | 7.3 | 13.5 | 2022-03-06
2022-03-07 | Click Here | 0 | 6.09 | 5.01 | 5.09 | 5.17 | 5.21 | 7.01 | 7.37 | 1.29 | 1.44 | 1.57 | 1.52 | 79 | 70 | 30 | 5 | 2 | 0 | 0.624 | 0.501 | 2.39 | 0.296 | 0.996 | 1.31 | 8.5 | 28.7 | 22.1 | 21.9 | 31.7 | 17 | 57.4 | 44.2 | 43.8 | 63.4 | 2.96 | 3.24 | 2.8 | 5.9 | 0.057 | 8.2 | 6.7 | 1.3644 | 45.8 | 85.8 | 0.3406 | 0.066 | 13.88 | 12.98 | 13.93 | 0.95 | 1.429 | 2.012 | 7.993 | 2.9244 | 29.15 | 7.3 | 13.5 | 2022-03-07
2022-03-08 | Click Here | 0 | 6.12 | 5.11 | 5.08 | 5.16 | 5.2 | 7.8 | 7.22 | 1.44 | 1.67 | 1.68 | 1.61 | 80 | 72 | 29 | 7 | 8 | 0 | 0.782 | 0.502 | 3.26 | 0.385 | 1.04 | 1.13 | 8.4 | 26.8 | 21.1 | 22.3 | 26.1 | 16.8 | 53.6 | 42.2 | 44.6 | 52.1 | 3.13 | 3.17 | 2.7 | 5.8 | 0.014 | 9.6 | 6.4 | 1.2926 | 45.4 | 82.4 | 0.3421 | 0.0839 | 14.58 | 12.76 | 13.68 | 0.92 | 1.498 | 2.012 | 8.421 | 2.9026 | 29.64 | 7.3 | 13.5 | 2022-03-08
2022-03-09 | Click Here | 0 | 5.5 | 5.21 | 9.51 | 5.05 | 5.1 | 6.61 | 3.71 | 1.29 | 1.61 | 1.74 | 1.72 | 78 | 70 | 31 | 6 | 4 | 1 | 0.761 | 0.506 | 2.01 | 0.406 | 1.26 | 1.35 | 8.7 | 28.4 | 23.4 | 23.3 | 27.4 | 17.4 | 56.8 | 46.8 | 46.6 | 54.8 | 3.09 | 3.13 | 2.7 | 5.9 | 0.046 | 8.9 | 6.7 | 1.4871 | 45.6 | 85.6 | 0.3429 | 0.0659 | 17.01 | 13.89 | 14.85 | 0.96 | 1.445 | 1.991 | 8.503 | 3.1371 | 30.05 | 5 | 14 | 2022-03-09
2022-03-10 | Click Here | 0 | 7.05 | 5.12 | 5.29 | 5.02 | 5.01 | 6.2 | 6.61 | 1.56 | 1.65 | 1.74 | 1.72 | 79 | 68 | 22 | 3 | 0 | 0 | 0.561 | 0.476 | 2.52 | 0.287 | 1.11 | 1.07 | 9.04 | 28.9 | 23.5 | 23.6 | 27.7 | 18.08 | 57.8 | 47 | 47.2 | 55.4 | 3.11 | 3.16 | 2.9 | 5.9 | 0.033 | 8.6 | 6.6 | 1.5593 | 45.8 | 78.7 | 0.3427 | 0.1076 | 15.65 | 13.78 | 14.72 | 0.94 | 1.443 | 2.011 | 8.218 | 3.2693 | 29.82 | 6.8 | 16 | 2022-03-10
2022-03-11 | Click Here | 0 | 6.28 | 5.08 | 4.81 | 5.13 | 5.08 | 6.46 | 6.59 | 1.55 | 1.75 | 2.07 | 1.75 | 73 | 62 | 44 | 5 | 11 | 0 | 0.572 | 0.499 | 2.64 | 0.257 | 1.41 | 1.181 | 9.3 | 29 | 21.9 | 22.5 | 27.7 | 18.6 | 58 | 43.8 | 45 | 55.4 | 3.16 | 3.15 | 2.9 | 5.8 | 0.139 | 2.9 | 5.8 | 1.1425 | 48.6 | 80.2 | 0.3126 | 0.0551 | 14.4 | 12.59 | 13.51 | 0.92 | 1.424 | 2 | 8.309 | 2.8625 | 30.28 | 7.3 | 16.5 | 2022-03-11
2022-03-12 | Click Here | 0 | 5.7 | 4.98 | 5.4 | 5.53 | 5.41 | 6.6 | 6.64 | 1.61 | 1.74 | 2.17 | 1.8 | 74 | 65 | 32 | 1 | 8 | 0 | 0.539 | 0.519 | 2.48 | 0.227 | 1.3 | 1.386 | 8.7 | 28.6 | 21.9 | 22.2 | 27.4 | 17.4 | 57.2 | 43.8 | 44.4 | 54.8 | 3.21 | 3.19 | 3.1 | 6 | 0.152 | 8.9 | 6.6 | 1.4105 | 61.3 | 82 | 0.2122 | 0.0859 | 14.36 | 12.63 | 13.56 | 0.93 | 0 | 0 | 0 | 3.1705 | 30.28 | 7.5 | 16.5 | 2022-03-12
2022-03-13 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-03-13
2022-03-14 | Click Here | 0 | 6.4 | 5.31 | 5.3 | 5.4 | 5.44 | 6.28 | 6.55 | 1.73 | 1.96 | 1.87 | 1.81 | 72 | 63 | 35 | 4 | 1 | 0 | 0.594 | 0.556 | 2.05 | 0.218 | 1.06 | 0.973 | 9.6 | 30.7 | 23.2 | 23.4 | 28.2 | 18.2 | 61.4 | 46.4 | 46.8 | 56.4 | 3.2 | 3.18 | 3 | 5.9 | 0.196 | 7.7 | 6 | 1.577 | 47.8 | 83.4 | 0.3199 | 0.0787 | 14.34 | 13.02 | 13.93 | 0.91 | 1.495 | 2.021 | 8.777 | 3.277 | 30.16 | 8 | 16.5 | 2022-03-14
2022-03-15 | Click Here | 0 | 6.37 | 5.34 | 5.13 | 5.2 | 5.25 | 6.46 | 6.92 | 1.6 | 1.79 | 1.74 | 1.71 | 77 | 70 | 37 | 5 | 4 | 1 | 0.554 | 0.526 | 2.23 | 0.212 | 1.509 | 1.514 | 9.7 | 30.5 | 23.4 | 23.6 | 28.7 | 19.4 | 61 | 46.8 | 47.2 | 57.4 | 3.23 | 3.15 | 2.9 | 5.8 | 0.206 | 7.7 | 6.1 | 1.6063 | 42.4 | 83.8 | 0.3718 | 0.0767 | 14.01 | 12.64 | 13.53 | 0.89 | 1.448 | 2.011 | 8.444 | 3.3263 | 28.21 | 7.7 | 17.5 | 2022-03-15
2022-03-16 | Click Here | 0 | 5.54 | 5.12 | 5.24 | 5.21 | 5.23 | 6.22 | 6.99 | 1.7 | 1.76 | 2.1 | 1.89 | 76 | 65 | 39 | 5 | 11 | 0 | 0.602 | 0.546 | 2.23 | 0.218 | 1.04 | 1.038 | 9.4 | 28.6 | 22.8 | 23.1 | 30.7 | 18.8 | 57.2 | 45.6 | 46.2 | 61.4 | 3.03 | 3.35 | 3 | 6 | 0.018 | 6.7 | 4.9 | 1.1053 | 45.1 | 85.1 | 0.3451 | 0.07 | 14.75 | 12.99 | 13.93 | 0.94 | 1.445 | 2.017 | 8.033 | 3.0053 | 30.75 | 8 | 18 | 2022-03-16
2022-03-17 | Click Here | 0 | 6.04 | 5.14 | 5.22 | 5.25 | 5.26 | 6.36 | 6.4 | 1.53 | 1.66 | 2.11 | 1.87 | 74 | 63 | 32 | 1 | 9 | 0 | 0.551 | 0.466 | 2.36 | 0.213 | 1.18 | 1.017 | 9.7 | 29.3 | 23.1 | 24 | 31.2 | 19.4 | 58.6 | 46.2 | 48 | 62.4 | 2.97 | 3.58 | 3.1 | 5.9 | 0.067 | 7 | 5.9 | 1.3618 | 45 | 83.9 | 0.3468 | 0.0759 | 14.85 | 12.89 | 13.87 | 0.98 | 2.204 | 2.013 | 8.544 | 3.2618 | 29.81 | 8 | 18 | 2022-03-17
2022-03-18 | Click Here | 0 | 6.11 | 5.19 | 5.42 | 5.26 | 5.29 | 6.67 | 6.36 | 1.6 | 1.66 | 1.82 | 1.76 | 71 | 62 | 33 | 1 | 6 | 0 | 0.514 | 0.447 | 2.1 | 0.194 | 0.916 | 0.899 | 8.9 | 29.1 | 22.3 | 22.4 | 30.9 | 17.8 | 58.2 | 44.6 | 44.8 | 61.8 | 3.02 | 3.47 | 3 | 6 | 0.056 | 8 | 7.8 | 1.2111 | 45.2 | 83.8 | 0.3454 | 0.0768 | 14.33 | 13.37 | 13.37 | 0 | 1.644 | 2.011 | 8.38 | 3.0211 | 28.81 | 7.5 | 18 | 2022-03-18
2022-03-19 | Click Here | 0 | 6.04 | 5.12 | 5.23 | 5.28 | 5.31 | 6.69 | 7.01 | 1.74 | 1.89 | 1.94 | 1.92 | 77 | 68 | 31 | 2 | 5 | 0 | 0.617 | 0.477 | 2.09 | 0.182 | 0.924 | 1.016 | 8.9 | 29.4 | 22.7 | 22.4 | 32 | 17.8 | 58.8 | 45.4 | 44.8 | 64 | 3.12 | 3.61 | 3 | 5.9 | 0.048 | 7 | 5.8 | 1.4925 | 49.5 | 85.4 | 0.305 | 0.0682 | 14.13 | 12.28 | 13.26 | 0.98 | 0 | 0 | 0 | 3.3425 | 29.6 | 7.5 | 22 | 2022-03-19
2022-03-20 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-03-20
2022-03-21 | Click Here | 0 | 5.53 | 5.07 | 5.23 | 5.15 | 5.19 | 6.49 | 6.37 | 1.66 | 1.78 | 2.1 | 1.85 | 70 | 58 | 36 | 3 | 11 | 0 | 0.633 | 0.454 | 2.19 | 0.18 | 1.38 | 1.019 | 8.6 | 30.4 | 23.3 | 22.8 | 30.3 | 17.2 | 60.8 | 46.6 | 45.6 | 60.6 | 1.89 | 1.89 | 3.1 | 5.9 | 0.045 | 7.3 | 4.9 | 0.89559 | 45 | 82.1 | 0.3466 | 0.0857 | 14.55 | 12.58 | 13.59 | 1.01 | 1.618 | 2.015 | 8.442 | 2.7056 | 30.04 | 7.5 | 22 | 2022-03-21
2022-03-22 | Click Here | 0 | 5.45 | 5.01 | 5.28 | 5.07 | 5.27 | 6.7 | 7.04 | 1.63 | 1.68 | 2.02 | 1.8 | 71 | 59 | 28 | 1 | 9 | 0 | 0.582 | 0.503 | 2.05 | 0.243 | 1.08 | 0.862 | 9 | 30.6 | 23.1 | 23 | 32.7 | 18 | 61.2 | 46.2 | 46 | 65.4 | 2.4 | 2.67 | 3.1 | 6 | 0.041 | 7.3 | 4.9 | 1.5139 | 46.7 | 84.3 | 0.3302 | 0.074 | 14.6 | 12.85 | 13.82 | 0.97 | 1.628 | 2.209 | 8.304 | 3.1939 | 30.04 | 7.5 | 22 | 2022-03-22
2022-03-23 | Click Here | 0 | 6.05 | 5.16 | 5.1 | 5.28 | 5.31 | 6.79 | 6.73 | 1.66 | 1.74 | 1.92 | 1.83 | 78 | 70 | 26 | 1 | 6 | 0 | 0.514 | 0.486 | 1.94 | 0.167 | 0.962 | 1.053 | 9.4 | 34.3 | 22.2 | 21.7 | 31.8 | 18.8 | 68.6 | 44.4 | 43.4 | 63.6 | 2.5 | 2.79 | 3 | 5.9 | 0.039 | 9 | 5.9 | 1.1692 | 47.8 | 87 | 0.3203 | 0.0602 | 14.36 | 13.47 | 13.47 | 0 | 1.62 | 2.039 | 8.638 | 3.0492 | 29.05 | 7.5 | 22 | 2022-03-23
2022-03-24 | Click Here | 0 | 6.09 | 5.14 | 5.09 | 5.09 | 5.13 | 6.87 | 6.79 | 1.61 | 1.74 | 1.9 | 1.95 | 74 | 67 | 24 | 1 | 4 | 0 | 0.514 | 0.506 | 2.09 | 0.192 | 1.01 | 1.035 | 9.2 | 30.5 | 22.4 | 22.2 | 33.2 | 18.4 | 61 | 44.8 | 44.4 | 66.4 | 2.59 | 2.9 | 3 | 5.9 | 0.067 | 9.1 | 5.4 | 1.4649 | 47 | 84.5 | 0.3272 | 0.0728 | 14.33 | 12.57 | 13.53 | 0.96 | 1.619 | 2.043 | 8.62 | 3.3449 | 29.53 | 7.5 | 22 | 2022-03-24
2022-03-25 | Click Here | 0 | 6.4 | 5.12 | 4.93 | 5.25 | 5.3 | 6.01 | 5.94 | 1.53 | 1.85 | 1.92 | 1.9 | 73 | 66 | 34 | 5 | 1 | 0 | 1.11 | 0.522 | 2 | 0.178 | 0.991 | 1.028 | 6.14 | 17.8 | 16.74 | 16.64 | 23.3 | 9.06 | 30.9 | 22.5 | 22.3 | 31.5 | 2.64 | 2.82 | 2.9 | 5.8 | 0.161 | 8.4 | 5.8 | 1.1793 | 47.2 | 83.2 | 0.327 | 0.0796 | 14.62 | 12.93 | 13.85 | 0.92 | 1.612 | 2.039 | 8.524 | 3.0193 | 30.26 | 7.5 | 22 | 2022-03-25
2022-03-26 | Click Here | 0 | 6.6 | 5.23 | 4.72 | 5.33 | 4.97 | 6.67 | 6.81 | 1.51 | 1.8 | 1.74 | 1.76 | 72 | 67 | 37 | 3 | 1 | 0 | 0.725 | 0.568 | 2.01 | 0.214 | 0.814 | 0.796 | 6.3 | 17.5 | 16.5 | 16.1 | 23.7 | 9.5 | 29.6 | 22.2 | 21.5 | 31.8 | 2.68 | 2.9 | 3 | 5.8 | 0.191 | 9.3 | 5.5 | 1.4026 | 47 | 85.4 | 0.3269 | 0.0684 | 14.65 | 12.73 | 13.71 | 0.98 | 0 | 0 | 0 | 3.2126 | 28.82 | 7.3 | 22 | 2022-03-26
2022-03-27 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 1.262 | 0 | 0 | 0 | 0 | 14.92 | 13.26 | 14.11 | 0.85 | 1.544 | 2.034 | 8.204 | 3.152 | 0 | 8.2 | 24 | 2022-03-27
2022-03-28 | Click Here | 0 | 5.96 | 4.34 | 5.3 | 4.68 | 4.96 | 6.79 | 7.23 | 1.48 | 1.69 | 1.94 | 1.96 | 74 | 68 | 24 | 2 | 0 | 0 | 0.59 | 0.451 | 2.29 | 0.168 | 0.53 | 0.464 | 9.9 | 30.3 | 22.3 | 21.6 | 33.6 | 19.8 | 60.6 | 44.6 | 43.2 | 67.2 | 2.69 | 3 | 3.1 | 5.9 | 0.104 | 8.6 | 5.7 | 1.1485 | 48.8 | 87.1 | 0.311 | 0.0596 | 14.68 | 12.35 | 13.37 | 1.02 | 1.647 | 2.039 | 9.033 | 2.9585 | 29.76 | 8.2 | 24 | 2022-03-28
2022-03-29 | Click Here | 0 | 5.46 | 5.19 | 5.17 | 5.06 | 5.17 | 6.79 | 7.23 | 1.66 | 1.85 | 1.89 | 1.87 | 74 | 67 | 20 | 0 | 0 | 0 | 0.581 | 0.361 | 2.01 | 0.214 | 0.461 | 0.374 | 10.1 | 31.9 | 23.1 | 23 | 33.4 | 20.2 | 63.8 | 46.2 | 46 | 66.8 | 2.66 | 3.01 | 3 | 5.9 | 0.124 | 9.5 | 7.4 | 1.338 | 48.8 | 85.6 | 0.3114 | 0.0672 | 15.39 | 13.63 | 14.57 | 0.94 | 1.706 | 2.019 | 8.575 | 3.158 | 29.45 | 10 | 22 | 2022-03-29
2022-03-30 | Click Here | 0 | 6.86 | 5.65 | 5.1 | 5.51 | 5.52 | 6.8 | 7.61 | 1.59 | 1.72 | 1.81 | 1.79 | 66 | 59 | 41 | 7 | 4 | 1 | 0.635 | 0.418 | 2.21 | 0.223 | 0.947 | 0.99 | 5.94 | 17.5 | 16 | 15.9 | 21.1 | 8.97 | 30.7 | 21.6 | 21.7 | 28.9 | 2.71 | 2.97 | 3 | 5.9 | 0.206 | 9.4 | 6.1 | 1.3306 | 44 | 83.6 | 0.3518 | 0.0774 | 16 | 14.1 | 15.09 | 0.98 | 1.718 | 2.03 | 8.992 | 3.1406 | 29.27 | 6 | 11.5 | 2022-03-30
2022-03-31 | Click Here | 0 | 6.49 | 5.23 | 5.09 | 5.3 | 5.35 | 6.63 | 6.74 | 1.81 | 1.97 | 1.95 | 1.93 | 68 | 60 | 22 | 3 | 1 | 0 | 0.611 | 0.441 | 2.09 | 0.226 | 0.539 | 0.638 | 5.5 | 17.1 | 16.4 | 16.3 | 22.5 | 8.7 | 27.7 | 21.5 | 21.6 | 30.6 | 2.71 | 3.01 | 3 | 5.8 | 0.104 | 9 | 6 | 1.1266 | 44.2 | 89.4 | 0.3517 | 0.0484 | 15.42 | 14.65 | 14.65 | 0 | 1.615 | 2.027 | 8.115 | 3.0066 | 29.73 | 6.5 | 12 | 2022-03-31
2022-04-01 | Click Here | 0 | 5.79 | 5.43 | 5.41 | 5.55 | 5.44 | 8.25 | 7.68 | 1.59 | 1.73 | 2.01 | 1.85 | 70 | 60 | 27 | 8 | 12 | 0 | 0.886 | 0.456 | 1.7 | 0.359 | 0.839 | 0.738 | 8.4 | 26.7 | 22.1 | 23.8 | 40.4 | 16.8 | 53.4 | 44.2 | 47.6 | 80.8 | 2.38 | 2.19 | 3.1 | 5.9 | 0.182 | 7.1 | 4.9 | 0.79398 | 47.2 | 90.2 | 0.3256 | 0.0446 | 15.16 | 13.4 | 14.35 | 0.95 | 1.436 | 2.019 | 8.833 | 2.764 | 29.56 | 6 | 12 | 2022-04-01
2022-04-02 | Click Here | 0 | 5.09 | 3.6 | 5.03 | 4.18 | 4.4 | 5.9 | 6.69 | 1.68 | 1.83 | 2 | 1.87 | 71 | 60 | 21 | 2 | 8 | 0 | 0.82 | 0.424 | 2.26 | 0.399 | 0.66 | 0.428 | 8.4 | 27.8 | 21.3 | 21.6 | 30.7 | 16.8 | 55.6 | 42.6 | 43.2 | 61.4 | 2.47 | 2.42 | 3 | 6 | 0.131 | 7 | 4.9 | 1.0233 | 47.4 | 88.1 | 0.3241 | 0.0522 | 14.85 | 13.13 | 14.06 | 0.93 | 0 | 0 | 0 | 2.9733 | 30.04 | 7 | 11.8 | 2022-04-02
2022-04-03 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-04-03
2022-04-04 | Click Here | 0 | 6.28 | 5.25 | 5.01 | 5.21 | 5.26 | 7.28 | 7.1 | 1.81 | 1.97 | 2.06 | 2.08 | 73 | 68 | 22 | 2 | 0 | 0 | 0.471 | 0.398 | 1.33 | 0.191 | 0.246 | 0.221 | 5.7 | 17.1 | 16.6 | 16.5 | 25.6 | 8.2 | 27.8 | 21.7 | 21.6 | 34.5 | 2.49 | 2.46 | 3 | 6.1 | 0.104 | 7.5 | 5.6 | 1.1929 | 51.5 | 86.5 | 0.2875 | 0.0629 | 15.86 | 13.22 | 15.13 | 1.91 | 1.341 | 2.018 | 9.172 | 3.1629 | 29.82 | 9 | 14 | 2022-04-04
2022-04-05 | Click Here | 0 | 5.83 | 5.02 | 5.34 | 4.89 | 5.01 | 6.98 | 7.05 | 1.64 | 1.87 | 1.93 | 1.94 | 64 | 57 | 22 | 1 | 0 | 0 | 0.485 | 0.386 | 1.53 | 0.176 | 0.297 | 0.25 | 5.4 | 16.5 | 15.9 | 15.8 | 23.7 | 7.8 | 26.9 | 21 | 21.1 | 32.1 | 2.48 | 2.49 | 3 | 6.1 | 0.121 | 7.6 | 5.8 | 0.77649 | 51.7 | 95.3 | 0.2873 | 0.0209 | 15.05 | 14.16 | 14.16 | 0 | 1.257 | 2.017 | 8.341 | 2.6865 | 29.44 | 8.5 | 13.8 | 2022-04-05
2022-04-06 | Click Here | 0 | 6.22 | 5.33 | 5.79 | 5.26 | 5.35 | 7.74 | 7.51 | 1.68 | 1.88 | 1.97 | 1.84 | 70 | 60 | 37 | 0 | 2 | 0 | 0.459 | 0.386 | 1.66 | 0.315 | 0.402 | 0.204 | 7.3 | 26.7 | 20.9 | 21.4 | 35.4 | 14.6 | 53.4 | 41.8 | 42.8 | 70.8 | 2.77 | 2.83 | 3.1 | 6 | 0.249 | 8.6 | 5 | 0.81591 | 49.7 | 91 | 0.3033 | 0.0408 | 14.71 | 12.9 | 13.08 | 0.98 | 1.258 | 2.019 | 8.542 | 2.7159 | 30.75 | 8.2 | 13.8 | 2022-04-06
2022-04-07 | Click Here | 0 | 5.9 | 5.16 | 5.26 | 5.23 | 5.3 | 7.23 | 7.02 | 1.75 | 1.84 | 2.02 | 1.87 | 52 | 39 | 14 | 10 | 6 | 0 | 0.463 | 0.411 | 1.42 | 0.265 | 0.707 | 0.372 | 7.7 | 27.6 | 21.5 | 21.8 | 33 | 15.4 | 55.2 | 43 | 43.6 | 66 | 2.64 | 2.74 | 3.1 | 6 | 0.214 | 7.6 | 5.1 | 1.0547 | 46.3 | 91.6 | 0.334 | 0.0377 | 15.3 | 13.44 | 14.38 | 0.94 | 1.231 | 2.011 | 9.011 | 2.9047 | 30.37 | 7.7 | 13.2 | 2022-04-07
2022-04-08 | Click Here | 0 | 5.99 | 4.89 | 5.08 | 4.92 | 5.21 | 7.26 | 7.22 | 1.7 | 1.86 | 1.88 | 1.8 | 60 | 51 | 19 | 7 | 4 | 0 | 0.493 | 0.412 | 1.92 | 0.119 | 0.58 | 0.445 | 5.2 | 15.7 | 14.6 | 15.2 | 24.8 | 7.9 | 26.1 | 19.5 | 20.3 | 33.3 | 2.71 | 2.85 | 2.9 | 5.9 | 0.014 | 9.1 | 5.5 | 0.90037 | 52.9 | 91.9 | 0.2759 | 0.0365 | 17.63 | 14.22 | 14.22 | 0 | 1.225 | 2.007 | 8.225 | 2.7004 | 29.35 | 7.9 | 13.5 | 2022-04-08
2022-04-09 | Click Here | 0 | 5.94 | 4.96 | 5.15 | 5.02 | 5.09 | 6.79 | 6.87 | 1.79 | 1.93 | 1.88 | 1.86 | 69 | 62 | 11 | 2 | 1 | 0 | 0.494 | 0.374 | 1.48 | 0.141 | 0.328 | 0.253 | 5.2 | 17 | 15.9 | 15.6 | 22.6 | 7.9 | 28.4 | 21 | 20.8 | 30.7 | 2.72 | 2.97 | 3 | 6.1 | 0.019 | 9.7 | 6.1 | 0.72636 | 53.7 | 91.2 | 0.2699 | 0.0396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29.49 | 8.1 | 13.5 | 2022-04-09
2022-04-10 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-04-10
2022-04-11 | Click Here | 0 | 5.54 | 5.04 | 5.33 | 5.29 | 5.34 | 7.59 | 6.83 | 1.56 | 1.72 | 1.86 | 1.66 | 64 | 55 | 25 | 2 | 2 | 0 | 0.44 | 0.365 | 1.48 | 0.262 | 0.196 | 0.178 | 7.8 | 28.1 | 21.6 | 21.4 | 33.9 | 15.6 | 56.2 | 43.2 | 42.8 | 67.8 | 2.78 | 2.78 | 3.1 | 5.9 | 0.21 | 7.4 | 4.9 | 0.91951 | 49.5 | 90.4 | 0.305 | 0.0436 | 16.6 | 13.95 | 13.95 | 0 | 1.262 | 1.994 | 8.76 | 2.2964 | 29.29 | 8.3 | 13.7 | 2022-04-11
2022-04-12 | Click Here | 0 | 5.51 | 4.95 | 5.16 | 4.99 | 5.01 | 7.22 | 7.73 | 1.57 | 1.67 | 1.98 | 1.81 | 62 | 53 | 18 | 2 | 1 | 0 | 0.68 | 0.363 | 0.984 | 0.235 | 0.343 | 0.259 | 7.4 | 28.1 | 20.2 | 20.6 | 32.2 | 14.8 | 56.1 | 40.4 | 41.2 | 64.4 | 2.74 | 3.01 | 3 | 6 | 0.125 | 7.6 | 5.1 | 0.93768 | 49.8 | 94.7 | 0.302 | 0.0236 | 14.21 | 13.35 | 14.29 | 0.94 | 1.238 | 1.982 | 8.76 | 2.6995 | 29.58 | 8.4 | 13.2 | 2022-04-12
2022-04-13 | Click Here | 0 | 5.82 | 4.84 | 5.17 | 5.27 | 5.36 | 6.89 | 7.31 | 1.59 | 1.69 | 1.84 | 1.76 | 59 | 50 | 16 | 2 | 0 | 0 | 0.491 | 0.012 | 1.13 | 0.157 | 0.269 | 0.314 | 4.9 | 16.6 | 15.2 | 15.4 | 21.7 | 7.4 | 26.9 | 20.5 | 21.1 | 30.2 | 2.83 | 2.96 | 3 | 6.1 | 0.08 | 9.2 | 6.8 | 0.80644 | 50.4 | 92 | 0.2974 | 0.0358 | 15.47 | 14.47 | 15.49 | 1.02 | 1.238 | 1.982 | 8.524 | 2.7077 | 29.5 | 8.9 | 13.2 | 2022-04-13
2022-04-14 | Click Here | 0 | 5.788 | 4.99 | 5.08 | 4.92 | 4.95 | 6.71 | 7.1 | 1.53 | 1.67 | 1.86 | 1.83 | 61 | 54 | 14 | 1 | 0 | 0 | 0.374 | 0.004 | 0.962 | 0.098 | 0.166 | 0.147 | 4.9 | 16.2 | 15.7 | 15.8 | 23.6 | 7.3 | 26.1 | 20.9 | 21.4 | 32.5 | 2.76 | 2.96 | 2.9 | 6 | 0.008 | 8.7 | 6.4 | 0.9617 | 50.8 | 92 | 0.2936 | 0.0361 | 13.99 | 13.88 | 13.88 | 0 | 1.236 | 1.973 | 8.533 | 2.5964 | 29.69 | 9 | 13.2 | 2022-04-14
2022-04-15 | Click Here | 0 | 5.11 | 4.92 | 5.12 | 5.33 | 4.96 | 6.91 | 6.85 | 1.34 | 1.79 | 1.82 | 1.84 | 65 | 57 | 13 | 0 | 0 | 0 | 0.613 | 0.005 | 0.988 | 0.101 | 0.171 | 0.185 | 5.1 | 16.5 | 15.8 | 16 | 23.5 | 7.6 | 27.1 | 21 | 21.5 | 32 | 2.85 | 3 | 3 | 6.1 | 0.161 | 9.2 | 6.1 | 0.98611 | 50.6 | 90.6 | 0.2938 | 0.0425 | 13.79 | 12.72 | 13.85 | 0.93 | 1.236 | 1.973 | 8.533 | 2.7117 | 29.79 | 9.1 | 13.5 | 2022-04-15
2022-04-16 | Click Here | 0 | 5.7 | 4.88 | 5.31 | 4.82 | 5.01 | 7.63 | 7.1 | 1.58 | 1.66 | 1.74 | 1.77 | 68 | 59 | 24 | 3 | 1 | 0 | 0.397 | 0.276 | 1.7 | 0.209 | 0.181 | 0.162 | 4.7 | 15.9 | 14.2 | 12.8 | 23.2 | 7.1 | 26.8 | 19.8 | 17.8 | 32 | 2.81 | 2.97 | 2.9 | 5.9 | 0.153 | 8.8 | 6.5 | 0.86383 | 50.8 | 87 | 0.2936 | 0.0602 | 14.91 | 13.87 | 14.88 | 1.01 | 0 | 0 | 0 | 2.7361 | 29.57 | 4.2 | 9.5 | 2022-04-16
2022-04-17 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 15.27 | 14.48 | 15.26 | 0.78 | 1.236 | 2.03 | 8.721 | 2.6738 | 0 | 5.7 | 9.4 | 2022-04-17
2022-04-18 | Click Here | 0 | 5.79 | 5.65 | 5.39 | 5.26 | 5.31 | 7.45 | 7.47 | 1.69 | 1.75 | 1.78 | 1.74 | 64 | 55 | 21 | 2 | 0 | 0 | 0.435 | 0.323 | 1.01 | 0.114 | 0.242 | 0.218 | 4.7 | 16.8 | 15.5 | 15.9 | 26.3 | 7.2 | 27.3 | 20.6 | 21.3 | 35.5 | 2.91 | 3 | 3.1 | 6 | 0.147 | 9.9 | 5.8 | 0.81794 | 53.2 | 93.1 | 0.274 | 0.031 | 14.1 | 14.01 | 14.01 | 0 | 1.241 | 2.036 | 8.947 | 2.5979 | 29.78 | 5.7 | 9.4 | 2022-04-18
2022-04-19 | Click Here | 0 | 5.71 | 5.6 | 5.5 | 5.71 | 5.99 | 8.04 | 7.55 | 1.7 | 1.72 | 1.76 | 1.74 | 63 | 55 | 19 | 2 | 0 | 0 | 0.664 | 0.33 | 1.01 | 0.182 | 0.435 | 0.488 | 4.8 | 17.1 | 15.2 | 15.7 | 25 | 7.3 | 27.4 | 20.6 | 21.5 | 34.5 | 2.94 | 2.94 | 3 | 5.9 | 0.078 | 9.6 | 6.2 | 0.62424 | 50.8 | 91.7 | 0.2939 | 0.0373 | 15.15 | 14.16 | 15.15 | 1.02 | 1.212 | 2.03 | 9.346 | 2.4742 | 29.47 | 5.6 | 9.4 | 2022-04-19
2022-04-20 | Click Here | 0 | 5.95 | 4.85 | 5.43 | 5.09 | 5.11 | 7.77 | 7.85 | 1.45 | 1.8 | 1.9 | 1.94 | 67 | 60 | 15 | 1 | 0 | 0 | 0.399 | 0.287 | 0.898 | 0.131 | 0.241 | 0.228 | 4.6 | 15.4 | 15.1 | 14.9 | 24.2 | 6.8 | 25.2 | 20.6 | 20.8 | 33.2 | 2.94 | 2.91 | 3 | 6.2 | 0.181 | 8.9 | 6.3 | 0.75934 | 50.6 | 86.3 | 0.294 | 0.0636 | 14.26 | 13.29 | 14.27 | 0.98 | 1.16 | 1.739 | 8.153 | 2.6593 | 27.94 | 5.5 | 9.3 | 2022-04-20
2022-04-21 | Click Here | 0 | 5.33 | 5.12 | 5 | 4.95 | 4.87 | 7.54 | 7.41 | 1.4 | 1.64 | 1.73 | 1.75 | 64 | 58 | 16 | 1 | 0 | 0 | 0.409 | 0.298 | 0.859 | 0.105 | 0.218 | 0.189 | 5.2 | 15.6 | 15.3 | 14.8 | 24.1 | 8.1 | 25.9 | 21 | 20.8 | 33.4 | 2.92 | 2.9 | 2.9 | 6.1 | 0.113 | 10.3 | 6.7 | 0.93744 | 50.9 | 91 | 0.2938 | 0.0407 | 14.33 | 13.41 | 14.36 | 0.95 | 1.264 | 2.013 | 8.053 | 2.6874 | 29.39 | 5.7 | 9 | 2022-04-21
2022-04-22 | Click Here | 0 | 5.84 | 5.34 | 5.15 | 5.33 | 5.42 | 8.64 | 7.28 | 1.64 | 1.73 | 2.21 | 1.79 | 65 | 54 | 16 | 3 | 3 | 0 | 0.424 | 0.324 | 0.865 | 0.103 | 0.293 | 0.272 | 8.4 | 28.1 | 22.3 | 22.5 | 35.2 | 16.8 | 56.2 | 44.6 | 45 | 70.4 | 2.9 | 3.19 | 3 | 6 | 0.286 | 6.8 | 4.3 | 0.63712 | 51.6 | 93.5 | 0.2869 | 0.0288 | 14.57 | 13.61 | 14.6 | 0.99 | 1.301 | 2.01 | 7.48 | 2.4271 | 29.35 | 5.6 | 8 | 2022-04-22
2022-04-23 | Click Here | 0 | 6.12 | 5.34 | 5.15 | 5.54 | 5.67 | 8.28 | 7.66 | 1.77 | 1.84 | 2.15 | 1.78 | 60 | 50 | 10 | 1 | 1 | 0 | 0.582 | 0.498 | 0.995 | 0.108 | 0.313 | 0.222 | 7.2 | 27.2 | 20.9 | 21.7 | 32.4 | 14.4 | 54.4 | 41.8 | 43.4 | 64.8 | 2.85 | 3.15 | 3.1 | 5.9 | 0.262 | 7.8 | 5.2 | 0.85833 | 47.7 | 94.3 | 0.3217 | 0.0255 | 14.12 | 13.13 | 14.09 | 0.96 | 0 | 0 | 0 | 2.6683 | 30.49 | 5.6 | 7.5 | 2022-04-23
2022-04-24 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-04-24
2022-04-25 | Click Here | 0 | 7.57 | 6.07 | 5.1 | 5.62 | 5.64 | 7.55 | 7.63 | 1.73 | 1.88 | 1.9 | 1.91 | 62 | 54 | 14 | 1 | 0 | 0 | 0.486 | 0.364 | 0.997 | 0.114 | 0.295 | 0.287 | 4.8 | 17.7 | 15.4 | 15.4 | 24.1 | 7.4 | 29.2 | 21 | 21.2 | 32.6 | 2.86 | 3.11 | 3 | 6 | 0.126 | 10.1 | 5.8 | 0.90877 | 47.5 | 91.4 | 0.3219 | 0.0403 | 13.88 | 12.91 | 13.87 | 0.96 | 1.256 | 1.998 | 7.176 | 2.7388 | 29.62 | 5.6 | 7.2 | 2022-04-25
2022-04-26 | Click Here | 0 | 7.22 | 5.45 | 5.41 | 5.33 | 5.44 | 7.49 | 7.28 | 1.59 | 1.71 | 1.75 | 1.77 | 71 | 64 | 25 | 2 | 0 | 0 | 0.453 | 0.345 | 1.48 | 0.156 | 0.171 | 0.148 | 4.9 | 16 | 15.1 | 13.5 | 22.2 | 7.6 | 25.9 | 20.6 | 19.1 | 30.7 | 2.91 | 3.04 | 2.9 | 5.9 | 0.148 | 9.7 | 6.7 | 0.96266 | 47.7 | 89.9 | 0.3217 | 0.0449 | 14.04 | 13.14 | 14.12 | 0.98 | 1.241 | 1.995 | 7.342 | 2.7427 | 29.55 | 4.7 | 7.2 | 2022-04-26
2022-04-27 | Click Here | 0 | 5.88 | 5.07 | 5.21 | 5.11 | 5.22 | 7.4 | 7.07 | 1.39 | 1.51 | 1.81 | 1.66 | 67 | 56 | 28 | 4 | 7 | 0 | 0.403 | 0.339 | 1.52 | 0.142 | 0.782 | 0.605 | 5.9 | 23.8 | 20.6 | 19.8 | 30.4 | 11.8 | 47.6 | 41.2 | 39.6 | 60.8 | 3.02 | 3.01 | 3 | 5.9 | 0.208 | 4.9 | 4.9 | 0.528 | 50.6 | 92 | 0.2957 | 0.0358 | 14.47 | 13.62 | 14.57 | 0.95 | 1.266 | 1.976 | 7.721 | 2.278 | 29.21 | 4.2 | 7.2 | 2022-04-27
2022-04-28 | Click Here | 0 | 5.77 | 5.09 | 5.21 | 5.05 | 5.13 | 7.12 | 6.8 | 1.38 | 1.59 | 1.86 | 1.77 | 67 | 58 | 29 | 3 | 2 | 0 | 0.409 | 0.342 | 1 | 0.174 | 0.413 | 0.236 | 4.5 | 14.9 | 14.3 | 14.4 | 21.4 | 7.2 | 25.5 | 20.3 | 20.6 | 30.2 | 2.85 | 3.19 | 3 | 6 | 0.078 | 11.6 | 7.2 | 1.0228 | 44.5 | 76.8 | 0.3513 | 0.1141 | 14.65 | 13.67 | 14.63 | 0.96 | 1.263 | 1.96 | 8.183 | 2.7828 | 29.33 | 4.2 | 7.2 | 2022-04-28
2022-04-29 | Click Here | 0 | 5.89 | 5.19 | 5.04 | 5.21 | 5.24 | 7.17 | 7.25 | 1.5 | 1.62 | 1.74 | 1.71 | 58 | 50 | 24 | 0 | 0 | 0 | 0.398 | 0.39 | 1.05 | 0.117 | 0.417 | 0.324 | 4.7 | 15.9 | 14.6 | 14.4 | 21.8 | 7.2 | 25.1 | 20.3 | 20 | 30.1 | 2.84 | 3.23 | 3 | 5.9 | 0.042 | 10.1 | 6.5 | 0.7744 | 60.7 | 92.2 | 0.2167 | 0.035 | 13.93 | 13.84 | 13.84 | 0 | 1.259 | 1.969 | 8.055 | 2.5344 | 29.2 | 4.5 | 7.2 | 2022-04-29
2022-04-30 | Click Here | 0 | 5.67 | 4.99 | 5.2 | 4.98 | 5.19 | 7.08 | 7.55 | 1.49 | 1.61 | 1.72 | 1.69 | 64 | 55 | 22 | 1 | 0 | 0 | 0.469 | 0.352 | 0.967 | 0.123 | 0.402 | 0.376 | 4.6 | 17.9 | 14.9 | 15.2 | 23.8 | 7 | 29.2 | 20.3 | 20.9 | 32.5 | 2.82 | 3.19 | 3 | 6 | 0.02 | 9.7 | 6.2 | 1.0118 | 54.8 | 92.8 | 0.2605 | 0.0324 | 13.78 | 12.78 | 13.76 | 0.98 | 0 | 0 | 0 | 2.7418 | 29.08 | 4.5 | 7.2 | 2022-04-30
2022-05-01 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-05-01
2022-05-02 | Click Here | 0 | 5.86 | 5.27 | 5.57 | 5.34 | 5.28 | 7.91 | 8.02 | 1.42 | 1.6 | 1.81 | 1.6 | 56 | 45 | 15 | 11 | 10 | 0 | 0.445 | 0.365 | 1.23 | 0.185 | 0.75 | 0.824 | 4.9 | 15.3 | 14.7 | 15.3 | 24 | 7.5 | 25.6 | 20.3 | 20.9 | 33 | 3.01 | 3.32 | 3.1 | 6 | 0.171 | 9.6 | 6.4 | 1.0161 | 60.5 | 95.2 | 0.2178 | 0.0212 | 14.66 | 13.79 | 14.75 | 0.96 | 1.209 | 1.955 | 7.922 | 2.6861 | 29.05 | 4.3 | 7.3 | 2022-05-02
2022-05-03 | Click Here | 0 | 5.92 | 5.31 | 5.27 | 5.38 | 5.4 | 7.7 | 7.4 | 1.46 | 1.58 | 1.76 | 1.62 | 55 | 44 | 10 | 1 | 6 | 0 | 0.454 | 0.424 | 0.805 | 0.451 | 1.87 | 1.512 | 4.8 | 15.5 | 15.4 | 15.3 | 22.5 | 7.9 | 26.9 | 21.1 | 21.1 | 31 | 2.94 | 3.15 | 2.9 | 5.8 | 0.149 | 12.5 | 6.4 | 0.84983 | 57 | 93.8 | 0.2441 | 0.0277 | 15.23 | 15.23 | 15.23 | 0 | 1.069 | 1.928 | 8.43 | 2.4998 | 29.2 | 4.4 | 7 | 2022-05-03
2022-05-04 | Click Here | 0 | 6.25 | 5.18 | 5.16 | 5.31 | 5.32 | 7.22 | 7.25 | 1.35 | 1.47 | 1.65 | 1.63 | 52 | 41 | 9 | 1 | 0 | 0 | 0.456 | 0.377 | 0.651 | 0.177 | 0.242 | 0.193 | 5.2 | 15.6 | 14.7 | 14.5 | 20.9 | 8.4 | 26.7 | 20.5 | 20.3 | 29.1 | 2.99 | 3.22 | 3 | 5.9 | 0.009 | 12 | 7.1 | 0.92375 | 58 | 92.8 | 0.2364 | 0.0321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29.12 | 4.2 | 7 | 2022-05-04
2022-05-05 | Click Here | 0 | 6.09 | 5.07 | 5.04 | 5.24 | 5.26 | 7.19 | 6.69 | 1.42 | 1.61 | 1.59 | 1.51 | 61 | 54 | 19 | 1 | 1 | 0 | 0.399 | 0.417 | 0.899 | 0.174 | 0.314 | 0.216 | 5.1 | 15.4 | 14.8 | 14.6 | 21.1 | 8.2 | 26.3 | 20.7 | 20.4 | 29.4 | 3 | 3.13 | 2.9 | 5.8 | 0.067 | 12.3 | 7.2 | 1.0046 | 58.2 | 91.4 | 0.2351 | 0.0403 | 13.34 | 13.11 | 13.34 | 0.13 | 3.292 | 1.422 | 13.585 | 2.5837 | 29.19 | 4.2 | 7 | 2022-05-05
2022-05-06 | Click Here | 0 | 6.03 | 5.05 | 5.09 | 4.98 | 5.12 | 7.11 | 7.31 | 1.42 | 1.58 | 1.83 | 1.7 | 60 | 52 | 18 | 0 | 0 | 0 | 0.392 | 0.386 | 0.871 | 0.142 | 0.246 | 0.251 | 5.4 | 16.3 | 14.6 | 14.1 | 23.7 | 7.9 | 27.9 | 20.2 | 20.1 | 28.6 | 2.97 | 3.11 | 3 | 6 | 0.077 | 10.4 | 7.8 | 1.1544 | 58.4 | 91.6 | 0.2349 | 0.0401 | 15.54 | 14.62 | 15.57 | 0.95 | 1.265 | 1.805 | 7.648 | 2.6346 | 29.46 | 4.2 | 6.4 | 2022-05-06
2022-05-07 | Click Here | 0 | 5.98 | 5.07 | 5.13 | 5.01 | 5.03 | 7.01 | 7.67 | 1.44 | 1.6 | 1.79 | 1.66 | 61 | 54 | 20 | 1 | 1 | 0 | 0.427 | 0.406 | 1.01 | 0.168 | 0.246 | 0.237 | 5.7 | 17.2 | 14.3 | 14 | 24.1 | 8.1 | 28.4 | 21.1 | 20 | 29.5 | 3 | 3.09 | 2.9 | 5.9 | 0.086 | 10.2 | 7.1 | 0.85555 | 58.1 | 91.3 | 0.2351 | 0.0405 | 16.64 | 14.62 | 15.57 | 0.95 | 0 | 0 | 0 | 2.8544 | 29.09 | 4.3 | 6.7 | 2022-05-07
2022-05-08 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 16.75 | 15.83 | 16.78 | 0.95 | 1.112 | 1.94 | 7.634 | 2.6056 | 0 | 5.1 | 6.8 | 2022-05-08
2022-05-09 | Click Here | 0 | 5.92 | 5.68 | 4.9 | 5.4 | 5.42 | 8.03 | 7.53 | 1.35 | 1.49 | 1.68 | 1.77 | 59 | 52 | 18 | 1 | 0 | 0 | 0.573 | 0.407 | 0.773 | 0.134 | 0.231 | 0.204 | 5.1 | 16.1 | 15.3 | 16 | 23.2 | 8.2 | 27.8 | 22.7 | 23.6 | 32.7 | 3.01 | 3.17 | 3 | 5.9 | 0.06 | 11.6 | 7.3 | 0.88681 | 57.5 | 92.8 | 0.2398 | 0.0321 | 17.42 | 16.61 | 17.59 | 0.98 | 1.285 | 1.916 | 8.419 | 2.6368 | 29.34 | 5.1 | 6.8 | 2022-05-09
2022-05-10 | Click Here | 0 | 6.04 | 5.67 | 5.33 | 5.42 | 5.49 | 7.69 | 6.94 | 1.4 | 1.56 | 1.61 | 1.64 | 57 | 49 | 26 | 4 | 1 | 0 | 0.492 | 0.397 | 2.41 | 0.314 | 0.604 | 0.428 | 5.5 | 15.1 | 14.3 | 15 | 21.2 | 9.1 | 25.7 | 21.9 | 22.9 | 30.3 | 2.94 | 3.05 | 3 | 6.1 | 0.046 | 13.5 | 7.8 | 0.99792 | 57.9 | 92 | 0.2367 | 0.0362 | 16.81 | 12.71 | 13.67 | 0.96 | 4.118 | 1.869 | 17.461 | 2.6779 | 29.52 | 4.3 | 6.6 | 2022-05-10
2022-05-11 | Click Here | 0 | 6.49 | 4.92 | 4.8 | 4.83 | 4.98 | 6.89 | 7.64 | 1.53 | 1.67 | 1.89 | 1.85 | 55 | 49 | 14 | 2 | 0 | 0 | 0.469 | 0.397 | 0.614 | 0.097 | 0.173 | 0.14 | 5.2 | 15.8 | 15.7 | 14.6 | 21.5 | 8.9 | 28.2 | 24.7 | 23 | 31.2 | 2.89 | 3.04 | 3 | 6 | 0.163 | 14.3 | 8.4 | 0.99246 | 57.7 | 87.5 | 0.2369 | 0.0576 | 14.5 | 13.49 | 14.44 | 0.95 | 1.507 | 3.162 | 8.496 | 2.7725 | 27.28 | 4.2 | 6.6 | 2022-05-11
2022-05-12 | Click Here | 0 | 5.96 | 5.21 | 5.4 | 5.17 | 5.09 | 7.11 | 7.33 | 1.47 | 1.64 | 1.78 | 1.74 | 57 | 50 | 16 | 1 | 0 | 0 | 0.497 | 0.463 | 0.817 | 0.089 | 0.151 | 0.134 | 5.4 | 15.9 | 15.4 | 14.8 | 21.7 | 9 | 29.1 | 24.3 | 23.1 | 31.3 | 2.93 | 3.01 | 2.9 | 6 | 0.101 | 14.6 | 9.5 | 1.0492 | 57.9 | 91.4 | 0.2369 | 0.0404 | 15.13 | 13.59 | 14.54 | 0.95 | 1.428 | 3.301 | 7.966 | 2.7992 | 28.77 | 4.4 | 6.8 | 2022-05-12
2022-05-13 | Click Here | 0 | 5.41 | 4.95 | 5.01 | 4.93 | 5.03 | 7.19 | 6.99 | 1.39 | 1.54 | 1.9 | 1.81 | 51 | 40 | 9 | 0 | 2 | 0 | 0.609 | 0.448 | 0.471 | 0.133 | 0.197 | 0.113 | 5.1 | 15.5 | 15.2 | 14.6 | 21.6 | 8.9 | 28.1 | 25.1 | 24.1 | 32.3 | 3.01 | 3.22 | 3.1 | 5.9 | 0.113 | 15.8 | 9.6 | 1.1447 | 56.5 | 92.7 | 0.2479 | 0.033 | 13.21 | 12.28 | 13.25 | 0.97 | 1.308 | 1.981 | 7.839 | 2.9347 | 28.66 | 4.3 | 6.8 | 2022-05-13
2022-05-14 | Click Here | 0 | 6.01 | 4.77 | 4.99 | 4.8 | 4.81 | 6.93 | 6.94 | 1.41 | 1.59 | 1.95 | 1.84 | 50 | 39 | 8 | 0 | 1 | 0 | 0.628 | 0.477 | 0.503 | 0.127 | 0.201 | 0.147 | 5.2 | 15.4 | 15.3 | 14.4 | 22.1 | 9 | 28.2 | 25 | 24.3 | 34.2 | 3.11 | 3.23 | 3 | 6 | 0.096 | 15.9 | 9.6 | 0.99416 | 56.6 | 92 | 0.2471 | 0.0342 | 13.23 | 12.22 | 13.19 | 0.97 | 0 | 0 | 0 | 2.7742 | 28.27 | 4.4 | 6.8 | 2022-05-14
2022-05-15 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 12.412 | 11.313 | 12.288 | 0.975 | 7.9 | 1.159 | 1.968 |  | 0 | 0 | 0 | 2022-05-15
2022-05-16 | Click Here | 0 | 6.18 | 4.99 | 4.86 | 4.97 | 5.03 | 7.24 | 6.92 | 1.5 | 1.68 | 1.87 | 1.82 | 51 | 46 | 9 | 0 | 0 | 0 | 0.554 | 0.436 | 0.517 | 0.104 | 0.148 | 0.127 | 5.3 | 14.4 | 14.7 | 15 | 21.3 | 9.3 | 28 | 24 | 24.4 | 32.8 | 3.1 | 3.2 | 2.9 | 5.9 | 0.084 | 15.3 | 10.6 | 0.97057 | 56.4 | 89.5 | 0.2473 | 0.0482 | 13.54 | 12.51 | 13.48 | 0.97 | 1.595 | 1.981 | 8.297 | 2.7106 | 28.84 | 4.3 | 6.8 | 2022-05-16
2022-05-17 | Click Here | 0 | 6.37 | 5.18 | 4.92 | 5.21 | 5.19 | 7.02 | 7.27 | 1.48 | 1.63 | 1.83 | 1.8 | 54 | 49 | 9 | 1 | 0 | 0 | 0.573 | 0.429 | 0.485 | 0.106 | 0.242 | 0.167 | 5.6 | 16 | 15.8 | 15.2 | 22.4 | 9.8 | 29.1 | 25.6 | 24.7 | 33.8 | 3.13 | 3.23 | 3 | 6 | 0.101 | 15.6 | 9.8 | 1.2167 | 56.8 | 92.4 | 0.247 | 0.0343 | 13.58 | 12.61 | 13.57 | 0.96 | 1.583 | 1.949 | 8.201 | 3.0167 | 28.52 | 4.2 | 6.8 | 2022-05-17
2022-05-18 | Click Here | 0 | 5.69 | 4.59 | 5.16 | 4.8 | 4.93 | 6.9 | 7.42 | 1.46 | 1.61 | 1.89 | 1.74 | 50 | 39 | 10 | 3 | 2 | 0 | 0.619 | 0.468 | 0.504 | 0.17 | 0.239 | 0.147 | 5.4 | 15.9 | 15.6 | 15.4 | 23 | 9.4 | 25.1 | 25.6 | 25.3 | 34.8 | 3.18 | 3.21 | 3.1 | 6 | 0.296 | 16.3 | 10.1 | 0.59506 | 58.1 | 92 | 0.2354 | 0.0359 | 13.94 | 13.85 | 13.85 | 0 | 1.482 | 1.937 | 9.18 | 2.3851 | 28.39 | 4.2 | 6.8 | 2022-05-18
2022-05-19 | Click Here | 0 | 6.28 | 5.06 | 4.96 | 5.09 | 5.16 | 7.66 | 7.48 | 1.5 | 1.57 | 2.06 | 1.89 | 42 | 31 | 4 | 2 | 1 | 0 | 0.553 | 0.442 | 0.49 | 0.172 | 0.195 | 0.157 | 5.1 | 16.5 | 15.5 | 14.9 | 22.3 | 9.2 | 30.5 | 25.7 | 24.9 | 35.2 | 3.1 | 3.22 | 3.1 | 5.9 | 0.138 | 16.4 | 11.5 | 1.1161 | 62.5 | 98.7 | 0.2038 | 0.0057 | 14.5 | 13.56 | 14.51 | 0.95 | 1.562 | 1.924 | 8.365 | 2.9661 | 28.58 | 4.4 | 6.9 | 2022-05-19
2022-05-20 | Click Here | 0 | 6.3 | 5.17 | 5.3 | 5.27 | 5.73 | 7.35 | 7.2 | 1.52 | 1.67 | 1.9 | 1.84 | 40 | 33 | 7 | 0 | 0 | 0 | 0.488 | 0.428 | 0.475 | 0.106 | 0.178 | 0.106 | 5.5 | 15.3 | 15.1 | 14.8 | 21.8 | 9.7 | 27.7 | 24.5 | 23.9 | 33.9 | 3.12 | 3.24 | 3 | 6.1 | 0.147 | 15.5 | 6.1 | 1.1561 | 63.1 | 98.2 | 0.1994 | 0.0077 | 14.11 | 13.09 | 14.04 | 0.95 | 1.507 | 1.916 | 8.59 | 3.0361 | 28.35 | 4.3 | 6.8 | 2022-05-20
2022-05-21 | Click Here | 0 | 6.09 | 5.01 | 5.04 | 5.39 | 5.38 | 6.79 | 6.84 | 1.55 | 1.64 | 1.9 | 1.94 | 38 | 30 | 3 | 0 | 0 | 0 | 0.492 | 0.478 | 0.418 | 0.096 | 0.267 | 0.166 | 5.2 | 23.6 | 15.6 | 15.3 | 21.3 | 9.5 | 42.4 | 26.1 | 25.6 | 33.4 | 3.05 | 3.31 | 2.9 | 5.8 | 0.153 | 16.7 | 11.2 | 1.0549 | 63 | 97.5 | 0.2002 | 0.0106 | 12.1 | 11.98 | 11.98 | 0 | 0 | 0 | 0 | 2.9249 | 28.86 | 4.3 | 6.8 | 2022-05-21
2022-05-22 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-05-22
2022-05-23 | Click Here | 0 | 5.74 | 5.38 | 5.52 | 4.9 | 5.08 | 7.67 | 6.82 | 1.59 | 1.75 | 2.12 | 1.84 | 54 | 43 | 8 | 0 | 1 | 0 | 0.636 | 0.495 | 0.504 | 0.153 | 0.256 | 0.143 | 5.3 | 16.7 | 15.4 | 14.9 | 23 | 9.7 | 31.5 | 26 | 25.1 | 36.1 | 3.1 | 3.11 | 3 | 6 | 0.24 | 17.4 | 12.6 | 1.1928 | 61.4 | 99.3 | 0.2113 | 0.0031 | 12.3 | 11.26 | 12.23 | 0.97 | 1.016 | 1.279 | 7.74 | 3.0228 | 28.68 | 4.3 | 6.9 | 2022-05-23
2022-05-24 | Click Here | 0 | 6.26 | 5.17 | 5.23 | 5.29 | 5.35 | 7.73 | 7.61 | 1.6 | 1.72 | 2.15 | 1.86 | 47 | 36 | 9 | 1 | 0 | 0 | 0.728 | 0.521 | 0.483 | 0.089 | 0.243 | 0.142 | 5.2 | 15.8 | 15.1 | 14.8 | 22.1 | 9.4 | 29.7 | 25.5 | 25 | 35.1 | 3 | 3.43 | 3.1 | 5.9 | 0.194 | 17.1 | 11.8 | 1.0588 | 62 | 98.7 | 0.2076 | 0.0057 | 12.3 | 12.17 | 12.17 | 0 | 1.385 | 1.244 | 7.832 | 2.8788 | 27.56 | 4.4 | 6.7 | 2022-05-24
2022-05-25 | Click Here | 0 | 6.75 | 5.47 | 5.16 | 5.53 | 5.65 | 7.59 | 7.17 | 1.61 | 1.78 | 1.91 | 1.83 | 44 | 36 | 8 | 1 | 0 | 0 | 0.745 | 0.499 | 0.467 | 0.114 | 0.239 | 0.162 | 5.4 | 15.4 | 15.3 | 14.9 | 21.6 | 9.7 | 29.3 | 25.9 | 25 | 34.3 | 3.06 | 3.43 | 3 | 5.9 | 0.099 | 16.4 | 11.9 | 1.1601 | 64.7 | 98.4 | 0.189 | 0.0069 | 11.55 | 11.42 | 11.42 | 0 | 1.398 | 1.406 | 7.159 | 2.9601 | 27.96 | 4.4 | 6.5 | 2022-05-25
2022-05-26 | Click Here | 0 | 6.36 | 5.06 | 5.16 | 5.11 | 5.19 | 6.89 | 7.25 | 1.57 | 1.69 | 1.77 | 1.79 | 49 | 40 | 5 | 1 | 0 | 0 | 0.612 | 0.011 | 0.478 | 0.115 | 0.284 | 0.202 | 5.3 | 15.3 | 14.9 | 14.6 | 21.2 | 9.5 | 28.2 | 25.6 | 25.3 | 33.8 | 3.2 | 3.31 | 2.9 | 5.9 | 0.019 | 16.9 | 11.8 | 1.7762 | 64.8 | 98.5 | 0.188 | 0.0063 | 12.87 | 11.04 | 12.92 | 1.88 | 1.209 | 1.356 | 7.228 | 3.5362 | 27.45 | 4.3 | 6.5 | 2022-05-26
2022-05-27 | Click Here | 0 | 6.99 | 5.28 | 5.04 | 5.22 | 5.21 | 6.96 | 7.11 | 1.55 | 1.67 | 1.79 | 1.71 | 54 | 39 | 2 | 0 | 0 | 0 | 0.539 | 0.639 | 0.538 | 0.114 | 0.254 | 0.218 | 5.5 | 17.7 | 15.2 | 14.3 | 22 | 9.9 | 32.9 | 26.8 | 25.2 | 34.4 | 1.95 | 2.34 | 2.9 | 5.9 | 0.121 | 16.6 | 11.9 | 1.4277 | 64.6 | 92.8 | 0.1882 | 0.032 | 12.24 | 11.28 | 12.25 | 0.97 | 1.109 | 1.836 | 7.618 | 3.1877 | 27.71 | 4.3 | 6.5 | 2022-05-27
2022-05-28 | Click Here | 0 | 6.51 | 5.16 | 4.96 | 5.29 | 5.35 | 7.27 | 7.44 | 1.55 | 1.72 | 1.78 | 1.76 | 50 | 41 | 7 | 0 | 0 | 0 | 0.56 | 0.476 | 0.506 | 0.108 | 0.181 | 0.12 | 5.4 | 15.5 | 15.6 | 15.3 | 21.3 | 9.8 | 28.9 | 26.5 | 26.2 | 34.1 | 2.34 | 2.59 | 2.9 | 6 | 0.067 | 16.4 | 12.1 | 1.4073 | 64.8 | 92.4 | 0.188 | 0.0341 | 11.89 | 10.77 | 11.83 | 1.06 | 0 | 0 | 0 | 3.1573 | 28.48 | 4.3 | 6.7 | 2022-05-28
2022-05-29 | Click Here | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.76 | 11.62 | 11.62 | 0 | 1.156 | 1.575 | 6.949 | 2.8842 | 0 | 4.3 | 6.7 | 2022-05-29
2022-05-30 | Click Here | 0 | 6.35 | 5.41 | 5.1 | 5.39 | 5.78 | 7.95 | 7.37 | 1.51 | 1.59 | 1.78 | 1.8 | 47 | 40 | 6 | 0 | 0 | 0 | 0.585 | 0.476 | 0.469 | 0.132 | 0.218 | 0.168 | 5.4 | 15.3 | 15.2 | 14.4 | 21.1 | 9.6 | 28.9 | 25.9 | 24.8 | 33.9 | 2.34 | 2.51 | 3 | 5.9 | 0.069 | 16.1 | 12.2 | 1.1142 | 66 | 96.7 | 0.1801 | 0.0142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28.45 | 4.3 | 6.7 | 2022-05-30
2022-05-31 | Click Here |  | 6.3 | 5.52 | 5.19 | 5.67 | 6.23 | 7.94 | 7.68 | 1.55 | 1.65 | 1.8 | 1.77 | 49 | 43 | 5 | 0 | 0 | 0 | 0.499 | 0.453 | 0.461 | 0.104 | 0.162 | 0.117 | 6.1 | 15.6 | 15.5 | 14.9 | 21.1 | 10.9 | 29.4 | 26.8 | 25.9 | 34.1 | 2.41 | 2.57 | 3 | 6 | 0.129 | 16.8 | 13.2 | 1.4948 | 62.9 | 95.7 | 0.2009 | 0.019 | 13.13 | 11.76 | 13.18 | 1.43 | 1.095 | 1.584 | 8.214 | 3.2348 | 28.28 | 4.3 | 6.5 | 2022-05-31
2022-06-01 | Click Here |  | 6.58 | 5.61 | 5.85 | 5.64 | 5.69 | 7.53 | 7.71 | 1.55 | 1.66 | 1.8 | 1.78 | 49 | 40 | 19 | 3 | 0 | 0 | 0.602 | 0.539 | 0.936 | 0.137 | 0.205 | 0.135 | 5.7 | 18.3 | 15.1 | 14.4 | 21.1 | 10.1 | 33.8 | 25 | 24.1 | 34 | 2.37 | 2.56 | 2.9 | 6.1 | 0.116 | 15.2 | 12.2 | 1.1496 | 62.7 | 93.8 | 0.201 | 0.0277 | 12.07 | 11.82 | 11.82 | 0 | 1.081 | 1.754 | 8.232 | 2.8796 | 28.68 | 4.2 | 6.3 | 2022-06-01
2022-06-02 | Click Here |  | 6.76 | 5.17 | 5.66 | 5.28 | 5.37 | 7.11 | 7.57 | 1.59 | 1.78 | 1.79 | 1.75 | 54 | 43 | 7 | 0 | 0 | 0 | 1.63 | 1.52 | 0.523 | 0.113 | 0.217 | 0.14 | 5.4 | 15.2 | 14.9 | 14.5 | 20.5 | 9.1 | 27.5 | 23.9 | 23.7 | 32.7 | 2.34 | 2.48 | 3 | 6 | 0.05 | 13.8 | 11.9 | 1.4764 | 62.5 | 94.8 | 0.2012 | 0.0232 | 12.28 | 11.31 | 12.23 | 0.92 | 1.119 | 2.099 | 7.441 | 3.1864 | 28.19 | 4.2 | 6.1 | 2022-06-02
2022-06-03 | Click Here |  | 6.55 | 5.3 | 5.09 | 5.41 | 5.38 | 7.65 | 7.24 | 1.64 | 1.74 | 2.15 | 1.74 | 46 | 35 | 14 | 2 | 1 | 0 | 0.568 | 0.515 | 0.722 | 0.133 | 0.257 | 0.152 | 5.5 | 15.3 | 14.9 | 14.4 | 20.3 | 9.1 | 26.3 | 23.1 | 23 | 32.8 | 3.13 | 3.21 | 3 | 6 | 0.043 | 13.2 | 12.5 | 1.339 | 60.2 | 96.3 | 0.2199 | 0.016 | 13.39 | 12.35 | 13.33 | 0.98 | 1.102 | 2.236 | 8.236 | 2.999 | 28.79 | 4.1 | 6.1 | 2022-06-03
2022-06-04 | Click Here |  | 6.56 | 5.18 | 5.35 | 5.32 | 5.38 | 7.41 | 7.36 | 1.68 | 1.84 | 2.16 | 2.12 | 45 | 34 | 12 | 1 | 0 | 0 | 0.656 | 0.597 | 0.741 | 0.129 | 0.221 | 0.184 | 5.6 | 15.4 | 14.8 | 14.1 | 20.1 | 9.2 | 27.1 | 23.2 | 22.9 | 32.7 | 3.12 | 3.29 | 3.1 | 5.9 | 0.061 | 13.3 | 12.5 | 1.0225 | 59.9 | 96.8 | 0.2204 | 0.014 | 11.94 | 10.99 | 11.91 | 0.92 | 0 | 0 | 0 | 3.1425 | 28.48 | 4 | 5.9 | 2022-06-04
2022-06-05 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.06 | 1.99 | 7.316 |  | 0 | 0 | 0 | 2022-06-05
2022-06-06 | Click Here |  | 7.53 | 5.05 | 5.11 | 5.3 | 5.35 | 7.08 | 7.38 | 1.47 | 1.67 | 2.04 | 2 | 67 | 58 | 13 | 2 | 0 | 0 | 0.606 | 0.582 | 0.725 | 0.125 | 0.268 | 0.248 | 5.5 | 15.6 | 15.2 | 16.9 | 22.9 | 9.3 | 28.4 | 23.8 | 26.8 | 32.9 | 2.98 | 3.16 | 3 | 5.9 | 0.132 | 13.9 | 11.5 | 1.1308 | 59.7 | 96.1 | 0.2206 | 0.0171 | 13.68 | 12.64 | 13.64 | 1 | 1.197 | 2.761 | 8.193 | 3.1608 | 28.23 | 4 | 5.9 | 2022-06-06
2022-06-07 | Click Here |  | 6.77 | 5.21 | 5.17 | 5.27 | 5.35 | 7 | 7.14 | 1.48 | 1.73 | 2 | 2.04 | 46 | 38 | 15 | 1 | 0 | 0 | 0.74 | 0.554 | 1.07 | 0.131 | 0.236 | 0.197 | 5.6 | 16.3 | 15.6 | 15.5 | 20.5 | 9.6 | 29.5 | 24.9 | 25.2 | 32.4 | 3.02 | 3.05 | 3 | 5.9 | 0.052 | 14.1 | 11.6 | 1.1795 | 59.5 | 95.2 | 0.2208 | 0.0212 | 14.14 | 13.1 | 14.24 | 1.14 | 1.196 | 2.742 | 8.667 | 3.2095 | 27.52 | 4 | 5.9 | 2022-06-07
2022-06-08 | Click Here |  | 6.52 | 5.27 | 5.11 | 5.45 | 5.4 | 7.04 | 6.99 | 1.53 | 1.69 | 2.06 | 2.03 | 49 | 38 | 17 | 0 | 1 | 0 | 0.606 | 0.512 | 0.782 | 0.199 | 0.325 | 0.208 | 5.3 | 15.4 | 14.9 | 15 | 21.2 | 9.2 | 28 | 23.9 | 24.5 | 33.4 | 3.16 | 3.45 | 3.1 | 6 | 0.071 | 14.6 | 11.6 | 1.0043 | 58.3 | 94.1 | 0.234 | 0.0261 | 13.84 | 12.62 | 13.76 | 1.14 | 1.196 | 2.193 | 8.899 | 3.0143 | 27.38 | 4 | 5.9 | 2022-06-08
2022-06-09 | Click Here |  | 6.56 | 5.35 | 5.43 | 5.67 | 5.49 | 7.58 | 7.14 | 1.49 | 1.61 | 2 | 1.91 | 48 | 37 | 22 | 2 | 0 | 0 | 0.574 | 0.515 | 0.319 | 0.181 | 0.34 | 0.22 | 5.3 | 15.3 | 15 | 14.9 | 22.5 | 9.5 | 28.5 | 24.8 | 25 | 33 | 2.96 | 3.4 | 3.1 | 6 | 0.064 | 16.4 | 12.3 | 0.59479 | 58.4 | 94.2 | 0.2331 | 0.0256 | 15.45 | 12.49 | 13.43 | 0.94 | 1.245 | 2.248 | 9.017 | 2.5648 | 27.48 | 4 | 5.8 | 2022-06-09
2022-06-10 | Click Here |  | 6.47 | 5.24 | 5.36 | 5.49 | 5.41 | 7.36 | 7.27 | 1.51 | 1.71 | 1.88 | 1.81 | 51 | 42 | 26 | 4 | 0 | 0 | 0.521 | 0.554 | 2.96 | 0.149 | 0.284 | 0.21 | 5.4 | 15.1 | 14.8 | 14.9 | 22.9 | 9.7 | 27.9 | 24.7 | 24.9 | 34.1 | 3.03 | 3.46 | 3 | 5.9 | 0.052 | 16.5 | 12.4 | 1.1672 | 57.6 | 94.9 | 0.239 | 0.0218 | 15.98 | 12.58 | 13.54 | 0.96 | 1.177 | 2.298 | 8.434 | 3.0972 | 27.65 | 4 | 5.8 | 2022-06-10
2022-06-11 | Click Here |  | 6.4 | 5.74 | 5.47 | 5.68 | 5.57 | 8.04 | 7.84 | 1.52 | 1.61 | 1.84 | 1.92 | 49 | 42 | 9 | 0 | 0 | 0 | 0.491 | 0.529 | 0.86 | 0.125 | 0.282 | 0.218 | 5.5 | 17.1 | 15.3 | 15.1 | 23.9 | 10 | 31.6 | 26.2 | 26 | 38.6 | 2.91 | 3.35 | 2.8 | 5.9 | 0.142 | 16.8 | 12.5 | 1.1663 | 60.3 | 92.7 | 0.2196 | 0.0326 | 13.3 | 12.61 | 12.61 | 0 | 0 | 0 | 0 | 3.0963 | 27.82 | 4 | 5.8 | 2022-06-11
2022-06-12 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-06-12
2022-06-13 | Click Here |  | 6.32 | 5.38 | 5.88 | 6.37 | 5.68 | 8.86 | 8.6 | 1.59 | 1.69 | 2.09 | 1.79 | 52 | 40 | 15 | 0 | 1 | 0 | 0.672 | 0.529 | 1.53 | 0.386 | 0.651 | 0.34 | 5.5 | 17.2 | 15.6 | 15.4 | 22.9 | 10.3 | 33.2 | 27.7 | 27.8 | 38.1 | 3.19 | 3.31 | 3 | 6 | 0.318 | 18.4 | 13.8 | 1.322 | 59.6 | 94.2 | 0.2243 | 0.0259 | 16.3 | 13.93 | 15.87 | 1.94 | 1.388 | 2.349 | 10.633 | 3.162 | 28.91 | 3.7 | 5.5 | 2022-06-13
2022-06-14 | Click Here |  | 6.53 | 5.77 | 5.27 | 5.74 | 5.63 | 8.41 | 7.58 | 1.52 | 1.66 | 2.03 | 1.88 | 46 | 35 | 13 | 1 | 2 | 0 | 0.617 | 0.525 | 0.645 | 0.088 | 0.476 | 0.506 | 5.3 | 15.5 | 15.5 | 14.4 | 23.6 | 10.3 | 33.4 | 28.4 | 26.4 | 38.8 | 3.05 | 3.23 | 3.1 | 5.8 | 0.332 | 19.8 | 13.4 | 0.98312 | 61.5 | 93.9 | 0.211 | 0.0273 | 16.19 | 15.57 | 15.57 | 0 | 1.385 | 2.862 | 11.066 | 2.8931 | 27.38 | 3.5 | 5 | 2022-06-14
2022-06-15 | Click Here |  | 6.31 | 5.45 | 5.2 | 5.77 | 5.92 | 8.53 | 7.27 | 1.5 | 1.63 | 1.9 | 1.89 | 48 | 39 | 11 | 2 | 0 | 0 | 0.492 | 0.514 | 0.594 | 0.094 | 0.541 | 0.781 | 5.8 | 14.5 | 15.8 | 15.5 | 22.2 | 10.9 | 27.7 | 28.7 | 28.2 | 37.3 | 3.07 | 3.24 | 3 | 6 | 0.229 | 18.5 | 14.1 | 1.0317 | 61.3 | 94.4 | 0.2122 | 0.0248 | 16.43 | 15.82 | 15.82 | 0 | 1.288 | 3.153 | 11.644 | 2.9117 | 27.76 | 3.3 | 4.8 | 2022-06-15
2022-06-16 | Click Here |  | 6.42 | 5.42 | 5.48 | 5.71 | 5.68 | 7.59 | 7.61 | 1.59 | 1.71 | 1.88 | 1.83 | 47 | 40 | 8 | 0 | 0 | 0 | 0.592 | 0.554 | 0.481 | 0.091 | 0.204 | 0.17 | 5.7 | 16 | 15.2 | 14.5 | 21.3 | 10.8 | 30.8 | 28.1 | 26.7 | 36.3 | 2.97 | 3.31 | 3 | 6 | 0.104 | 19.1 | 14.9 | 1.1224 | 61 | 95.6 | 0.2109 | 0.0185 | 17.23 | 15.76 | 16.74 | 0.98 | 1.51 | 2.938 | 11.348 | 2.9824 | 27.52 | 3.2 | 4.4 | 2022-06-16
2022-06-17 | Click Here |  | 6.83 | 5.34 | 5.31 | 5.31 | 5.34 | 6.96 | 7.68 | 1.49 | 1.65 | 1.94 | 1.91 | 44 | 36 | 9 | 0 | 0 | 0 | 0.452 | 0.445 | 0.592 | 0.081 | 0.171 | 0.146 | 5.6 | 16.7 | 14.9 | 14.8 | 20.4 | 11.1 | 33.4 | 28.6 | 28.4 | 35 | 3.02 | 3.21 | 2.9 | 6 | 0.042 | 20.9 | 15 |  | 77.5 | 90.5 | 0.1103 | 0.043 | 16.52 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28.44 | 3.2 | 4.4 | 2022-06-17
2022-06-18 | Click Here |  | 6.82 | 5.27 | 5.3 | 5.29 | 5.33 | 7.04 | 7.26 | 1.53 | 1.7 | 1.95 | 1.93 | 43 | 37 | 10 | 1 | 0 | 0 | 0.483 | 0.476 | 0.596 | 0.093 | 0.127 | 0.094 | 5.7 | 17.2 | 15.2 | 15.1 | 16.4 | 11.2 | 34.5 | 29.2 | 29 | 28.7 | 2.95 | 2.98 | 3 | 5.9 | 0.046 | 20.8 | 15.6 | 1.2347 | 59 | 90.9 | 0.2291 | 0.0414 | 14.07 | 12.61 | 13.58 | 0.97 | 0 | 0 | 0 | 3.0747 | 28.4 | 3.2 | 4.4 | 2022-06-18
2022-06-19 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-06-19
2022-06-20 | Click Here |  | 6.55 | 5.4 | 5.16 | 5.33 | 5.3 | 7.19 | 6.74 | 1.5 | 1.55 | 1.95 | 1.75 | 44 | 32 | 9 | 0 | 0 | 0 | 0.585 | 0.524 | 1.03 | 0.101 | 0.578 | 0.543 | 5.7 | 15.7 | 15.4 | 15.1 | 20.8 | 11.1 | 31 | 28.7 | 28 | 36.1 | 3.02 | 3.25 | 3.1 | 6 | 0.022 | 20 | 15.5 | 1.2898 | 60.6 | 93.6 | 0.2172 | 0.0287 | 14.96 | 13.52 | 14.46 | 0.94 | 1.231 | 2.681 | 9.746 | 3.1098 | 27.44 | 3.2 | 4.5 | 2022-06-20
2022-06-21 | Click Here |  | 6.4 | 5.15 | 5.38 | 4.97 | 5.02 | 5.52 | 5.94 | 1.64 | 1.78 | 2.06 | 1.86 | 44 | 32 | 9 | 1 | 0 | 0 | 0.57 | 0.494 | 0.587 | 0.084 | 0.365 | 0.373 | 5.7 | 15.4 | 15.6 | 14.9 | 15.6 | 11 | 30 | 29.5 | 28 | 26.8 | 3.18 | 3.53 | 3.1 | 6 | 0.252 | 19.4 | 15.1 | 1.0717 | 61 | 94.2 | 0.2143 | 0.026 | 15.12 | 13.8 | 14.73 | 0.93 | 1.31 | 2.609 | 9.178 | 2.9017 | 28.61 | 3.2 | 4.5 | 2022-06-21
2022-06-22 | Click Here |  | 6.85 | 5.22 | 5.06 | 5.26 | 5.24 | 6.79 | 7.14 | 1.62 | 1.77 | 2.03 | 1.86 | 43 | 34 | 8 | 0 | 0 | 0 | 0.58 | 0.438 | 0.59 | 0.088 | 0.517 | 0.614 | 5.7 | 15.5 | 15.1 | 14.9 | 20.4 | 11.1 | 30.8 | 28.8 | 28.2 | 35.3 | 3.12 | 3.46 | 3 | 5.9 | 0.085 | 19.7 | 15.3 | 1.4866 | 59.8 | 98.1 | 0.2145 | 0.0081 | 16.42 | 14.97 | 15.93 | 0.96 | 1.367 | 2.4 | 10.555 | 3.2766 | 27.43 | 3.2 | 4.5 | 2022-06-22
2022-06-23 | Click Here |  | 6.98 | 5.43 | 5.27 | 5.16 | 5.24 | 6.73 | 6.72 | 1.49 | 1.62 | 1.91 | 1.76 | 46 | 38 | 16 | 1 | 0 | 0 | 0.501 | 0.436 | 0.871 | 0.092 | 0.248 | 0.25 | 5.8 | 15.4 | 15.1 | 14.4 | 20.7 | 11.3 | 30.1 | 29.2 | 27.4 | 36.3 | 3.15 | 3.51 | 2.9 | 5.9 | 0.091 | 20.1 | 15.8 |  | 59.8 | 92.9 | 0.2144 | 0.0317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.93 | 3 | 5.3 | 2022-06-23
2022-06-24 | Click Here |  | 6.61 | 5.12 | 5.11 | 5.18 | 5.28 | 7.88 | 6.74 | 1.52 | 1.59 | 1.93 | 1.74 | 40 | 30 | 8 | 0 | 0 | 0 | 0.57 | 0.445 | 0.629 | 0.121 | 0.286 | 0.246 | 5.7 | 15.4 | 15.7 | 15.6 | 20.3 | 11.4 | 30.7 | 30 | 30.1 | 35.6 | 3.18 | 3.21 | 3 | 6 | 0.052 | 21.2 | 16 |  | 61.4 | 92.6 | 0.2115 | 0.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.93 | 3 | 5.6 | 2022-06-24
2022-06-25 | Click Here |  | 6.64 | 5.12 | 5.15 | 5.16 | 5.3 | 7.48 | 7.54 | 1.54 | 1.62 | 1.99 | 1.75 | 41 | 30 | 10 | 1 | 0 | 0 | 0.621 | 0.557 | 0.707 | 0.109 | 0.309 | 0.231 | 5.7 | 15.1 | 15.5 | 15.7 | 21.4 | 11.5 | 30.5 | 30.9 | 30.2 | 36.2 | 3.18 | 3.41 | 3 | 5.9 | 0.041 | 21.2 | 16.1 | 1.7346 | 61.2 | 92.8 | 0.2122 | 0.0326 | 14.72 | 13.33 | 14.8 | 0.97 | 0 | 0 | 0 | 3.4546 | 27.54 | 3 | 5.4 | 2022-06-25
2022-06-26 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 16.77 | 15.48 | 16.45 | 0.97 | 1.466 | 2.882 | 11.57 |  | 0 | 0 | 0 | 2022-06-26
2022-06-27 | Click Here |  | 7.31 | 5.32 | 5.02 | 5.23 | 5.2 | 5.64 | 5.59 | 1.56 | 1.72 | 1.86 | 1.77 | 35 | 28 | 16 | 0 | 0 | 0 | 0.546 | 0.521 | 1.21 | 0.121 | 0.134 | 0.08 | 6.1 | 15.3 | 15.6 | 15.3 | 15.5 | 12.5 | 31.1 | 31.1 | 30.6 | 27.5 | 3.15 | 3.38 | 3 | 5.7 | 0.181 | 22.3 | 16.4 | 1.3415 | 61.4 | 92.5 | 0.212 | 0.0338 | 18.37 | 17.11 | 18.1 | 0.99 | 1.608 | 2.836 | 12.1 | 3.0915 | 27.15 | 3 | 3 | 2022-06-27
2022-06-28 | Click Here |  | 7.53 | 5.32 | 5.18 | 5.16 | 5.15 | 6.89 | 7.39 | 1.43 | 1.69 | 1.78 | 1.7 | 41 | 34 | 14 | 1 | 0 | 0 | 0.617 | 0.518 | 1.2 | 0.11 | 0.19 | 0.147 | 5.9 | 15.3 | 15.2 | 15.2 | 21.6 | 11.3 | 31.7 | 30.3 | 21.3 | 38.9 | 3.19 | 3.33 | 2.9 | 5.9 | 0.097 | 21.8 | 17 | 1.387 | 61.7 | 91 | 0.2119 | 0.041 | 17.43 | 16.11 | 17.07 | 0.96 | 1.522 | 2.623 | 12.323 | 3.107 | 26.96 | 2.8 | 5.6 | 2022-06-28
2022-06-29 | Click Here |  | 6.6 | 5.13 | 4.97 | 5 | 5.11 | 7.19 | 7.31 | 1.37 | 1.42 | 1.89 | 1.68 | 40 | 31 | 12 | 1 | 0 | 0 | 0.747 | 0.507 | 1.08 | 0.137 | 0.277 | 0.208 | 5.8 | 14.8 | 15.8 | 15.1 | 21.7 | 11.8 | 30.1 | 31 | 29.9 | 38.9 | 3.26 | 3.27 | 3 | 6 | 0.061 | 22 | 16.9 | 1.2948 | 62.7 | 91.2 | 0.2022 | 0.0398 | 17.84 | 16.49 | 17.5 | 1.01 | 1.621 | 2.415 | 13.898 | 3.0348 | 26.1 | 2.4 | 5.7 | 2022-06-29
2022-06-30 | Click Here |  | 6.58 | 5.11 | 5.05 | 5.06 | 5.18 | 7.38 | 7.53 | 1.42 | 1.6 | 1.91 | 1.78 | 39 | 30 | 11 | 1 | 0 | 0 | 0.564 | 0.495 | 1.05 | 0.122 | 0.198 | 0.14 | 5.9 | 15 | 15.7 | 15.3 | 22.2 | 12.1 | 31.2 | 29.8 | 30.2 | 39.4 | 3.22 | 3.26 | 3.1 | 5.9 | 0.046 | 22.1 | 17 | 1.1273 | 62.5 | 91.4 | 0.2029 | 0.0385 | 18.76 | 17.56 | 18.52 | 0.96 | 1.62 | 2.556 | 13.08 | 2.7773 | 27.7 | 2.4 | 5.7 | 2022-06-30
2022-07-01 | Click Here |  | 6.19 | 4.9 | 4.95 | 5.04 | 5.23 | 7.81 | 7.1 | 1.35 | 1.45 | 1.71 | 1.63 | 40 | 33 | 9 | 1 | 0 | 0 | 0.576 | 0.486 | 0.652 | 0.126 | 0.328 | 0.262 | 5.9 | 15.1 | 15.7 | 15.3 | 20.8 | 12.2 | 31 | 31.9 | 31.2 | 38.2 | 3.17 | 3.27 | 3 | 6 | 0.026 | 22.5 | 17.8 | 1.4708 | 66.1 | 91.9 | 0.1798 | 0.0364 | 14.69 | 13.31 | 14.27 | 0.96 | 1.261 | 2.632 | 8.609 | 3.1708 | 27.78 | 2.6 | 5.7 | 2022-07-01
2022-07-02 | Click Here |  | 6.19 | 5.07 | 5.03 | 5.1 | 5.49 | 7.62 | 7.6 | 1.39 | 1.57 | 1.88 | 1.86 | 41 | 33 | 9 | 0 | 0 | 0 | 0.492 | 0.452 | 0.701 | 0.107 | 0.261 | 0.282 | 5.9 | 15.6 | 15.8 | 15.5 | 20.7 | 12 | 31.7 | 31.4 | 31.1 | 38 | 3.07 | 3.2 | 2.9 | 6.1 | 0.037 | 21.5 | 17.8 | 1.5101 | 66.7 | 92.4 | 0.1762 | 0.0344 | 14.94 | 13.65 | 14.6 | 0.95 | 0 | 0 | 0 | 3.3001 | 27.71 | 2.7 | 5.6 | 2022-07-02
2022-07-03 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 1.3401 | 0 | 0 | 0 | 0 | 15.54 | 14.42 | 15.4 | 0.98 | 1.42 | 2.56 | 10.135 | 3.1201 | 0 | 2.7 | 5.6 | 2022-07-03
2022-07-04 | Click Here |  | 6.91 | 5.22 | 5.07 | 5.12 | 5.09 | 6.81 | 7.68 | 1.53 | 1.67 | 1.84 | 1.79 | 41 | 34 | 12 | 1 | 0 | 0 | 0.519 | 0.457 | 0.639 | 0.114 | 0.613 | 0.679 | 6.1 | 15.7 | 15 | 15 | 20.3 | 12.4 | 32.1 | 30.4 | 30.6 | 37.8 | 3.05 | 3.13 | 3 | 6 | 0.091 | 21.9 | 18.4 | 1.1177 | 66.9 | 90.3 | 0.176 | 0.0441 | 15.59 | 14.56 | 15.53 | 0.97 | 1.42 | 2.534 | 10.601 | 2.8877 | 26.52 | 2.7 | 5.5 | 2022-07-04
2022-07-05 | Click Here |  | 6.94 | 5.2 | 5.17 | 5.03 | 5.12 | 6.52 | 6.48 | 1.61 | 1.74 | 2.04 | 1.97 | 40 | 33 | 11 | 1 | 0 | 0 | 0.587 | 0.563 | 0.614 | 0.112 | 0.471 | 0.446 | 6 | 15.5 | 14.8 | 14.8 | 20.5 | 12.1 | 32.1 | 30.2 | 30.5 | 37.9 | 3.08 | 3.17 | 2.9 | 5.8 | 0.074 | 21.8 | 18.4 | 1.4845 | 66.7 | 91.3 | 0.1762 | 0.0386 | 18.02 | 15.12 | 16.05 | 0.93 | 1.387 | 2.509 | 11.577 | 3.2945 | 26.07 | 2.6 | 5.6 | 2022-07-05
2022-07-06 | Click Here |  | 6.26 | 5.12 | 5.15 | 5.15 | 5.47 | 8.34 | 6.75 | 1.48 | 1.63 | 1.79 | 1.83 | 38 | 30 | 9 | 0 | 0 | 0 | 0.555 | 0.496 | 0.403 | 0.12 | 0.559 | 0.508 | 5.8 | 15 | 15.2 | 14.9 | 20.8 | 11.3 | 29.4 | 29.3 | 28.9 | 38 | 3.1 | 3.11 | 3 | 5.9 | 0.089 | 19.8 | 17.8 | 1.4068 | 65.3 | 91.3 | 0.1851 | 0.0391 | 15.2 | 14.14 | 15.11 | 0.97 | 1.421 | 2.484 | 9.646 | 3.2368 | 26.4 | 2.6 | 5.8 | 2022-07-06
2022-07-07 | Click Here |  | 6.24 | 5.36 | 5.32 | 5.17 | 5.38 | 7.82 | 7.99 | 1.38 | 1.49 | 1.76 | 1.83 | 48 | 42 | 9 | 1 | 0 | 0 | 0.612 | 0.499 | 0.894 | 0.127 | 0.417 | 0.329 | 6 | 15.3 | 15.1 | 14.7 | 20.8 | 11.7 | 29.7 | 28.6 | 28.4 | 38.3 | 3.17 | 3.25 | 2.9 | 6.1 | 0.046 | 19.8 | 18 | 1.4573 | 67.7 | 91.2 | 0.1732 | 0.4 | 14.97 | 12.79 | 13.78 | 0.99 | 1.285 | 2.435 | 8.213 | 3.2873 | 26.83 | 2.6 | 5.8 | 2022-07-07
2022-07-08 | Click Here |  | 7.03 | 5.29 | 5.33 | 5.15 | 4.86 | 7.22 | 8.14 | 1.64 | 1.75 | 1.96 | 1.87 | 39 | 31 | 3 | 0 | 0 | 0 | 0.569 | 0.488 | 0.383 | 0.112 | 0.151 | 0.116 | 6 | 16.1 | 15 | 14.9 | 23 | 11.3 | 30.7 | 27.8 | 28.2 | 41.6 | 3.13 | 3.22 | 2.9 | 6.1 | 0.103 | 18.2 | 17.4 | 1.4844 | 67.5 | 91.7 | 0.1754 | 0.0374 | 14.86 | 13.86 | 14.82 | 0.96 | 1.318 | 2.476 | 9.56 | 3.3844 | 26.52 | 2.6 | 5.8 | 2022-07-08
2022-07-09 | Click Here |  | 6.74 | 5.13 | 5.18 | 5.1 | 5.22 | 7.2 | 7.17 | 1.58 | 1.79 | 1.96 | 1.88 | 37 | 30 | 7 | 0 | 0 | 0 | 0.598 | 0.462 | 0.466 | 0.12 | 0.146 | 0.109 | 6.1 | 16.2 | 15 | 14.9 | 22.7 | 11.6 | 31.5 | 28.4 | 28.8 | 41.1 | 3.18 | 3.23 | 2.9 | 6 | 0.087 | 19.2 | 17.4 | 1.514 | 67.9 | 93.2 | 0.1751 | 0.0302 | 13.34 | 12.3 | 13.27 | 0.97 | 0 | 0 | 0 | 3.384 | 26.55 | 2.5 | 5.8 | 2022-07-09
2022-07-10 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 1.31 | 0 | 0 | 0 | 0 | 12.97 | 12.83 | 12.83 | 0 | 1.183 | 2.428 | 8.641 | 3.16 | 0 | 2.5 | 5.8 | 2022-07-10
2022-07-11 | Click Here |  | 6.57 | 5.09 | 5.14 | 5.19 | 5.29 | 7.04 | 6.95 | 1.54 | 1.76 | 1.94 | 1.88 | 34 | 26 | 6 | 0 | O | O | 0.521 | 0.487 | 0.429 | 0.107 | 0.124 | 0.113 | 5.9 | 16.4 | 14.8 | 14.7 | 23.1 | 11.4 | 31.9 | 28.7 | 28.4 | 42.6 | 3.11 | 3.23 | 3 | 6.1 | 0.056 | 19.3 | 17.5 | 1.5032 | 67 | 93.6 | 0.1784 | 0.0289 | 14.48 | 13.53 | 14.53 | 1 | 1.337 | 2.036 | 9.868 | 3.3632 | 27.42 | 2.5 | 5.8 | 2022-07-11
2022-07-12 | Click Here |  | 6.38 | 5.18 | 5.21 | 5.31 | 5.56 | 8.19 | 6.85 | 1.63 | 1.82 | 1.84 | 1.8 | 33 | 24 | 7 | 0 | 0 | 0 | 0.514 | 0.471 | 0.396 | 0.15 | 0.219 | 0.116 | 6 | 14.9 | 15.3 | 15.1 | 23.2 | 11.1 | 28.4 | 27.8 | 28.2 | 41.6 | 3.05 | 3.21 | 2.8 | 5.9 | 0.209 | 17.8 | 16.9 | 1.5268 | 67 | 92.5 | 0.1736 | 0.0335 | 15.56 | 14.57 | 15.56 | 0.99 | 1.429 | 1.861 | 10.578 | 3.3668 | 26.61 | 2.5 | 5.8 | 2022-07-12
2022-07-13 | Click Here |  | 6.78 | 5.61 | 5.29 | 5.2 | 5.08 | 6.88 | 7.63 | 1.61 | 1.71 | 1.8 | 1.7 | 36 | 28 | 8 | 0 | 0 | 0 | 0.557 | 0.467 | 0.857 | 0.128 | 0.191 | 0.15 | 6.2 | 15.4 | 14.7 | 14.8 | 22.2 | 11.6 | 30.1 | 27.1 | 28 | 40.2 | 3.06 | 3.26 | 2.9 | 5.8 | 0.104 | 18.5 | 17.3 | 1.5333 | 68.5 | 90.5 | 0.1642 | 0.0434 | 15.63 | 14.67 | 15.63 | 0.96 | 1.484 | 2.214 | 11.37 | 3.2733 | 26.03 | 2.5 | 5.6 | 2022-07-13
2022-07-14 | Click Here |  | 6.72 | 5.17 | 5.25 | 4.99 | 5 | 7.19 | 7.37 | 1.64 | 1.78 | 1.93 | 1.79 | 36 | 27 | 14 | 1 | 0 | 0 | 0.739 | 0.568 | 0.833 | 0.139 | 0.159 | 0.114 | 6.1 | 15 | 14.7 | 14.6 | 22.9 | 11.6 | 28.6 | 27.2 | 27.7 | 41.2 | 3.09 | 3.2 | 2.9 | 5.9 | 0.116 | 18.4 | 17 |  | 68.9 | 89.7 | 0.1639 | 0.0472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25.52 | 2.4 | 5.6 | 2022-07-14
2022-07-15 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-07-15
2022-07-16 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-07-16
2022-07-17 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-07-17
2022-07-18 | Click Here |  | 6.68 | 5.39 | 5.04 | 5.02 | 5.12 | 6.94 | 7.41 | 1.42 | 1.61 | 1.99 | 1.93 | 35 | 26 | 13 | 0 | 0 | 0 | 0.558 | 0.145 | 1.27 | 0.144 | 0.193 | 0.161 | 6.3 | 16 | 15.6 | 14.9 | 21.4 | 12.3 | 31.4 | 29.9 | 29.4 | 39.2 | 2.9 | 3.13 | 3 | 5.9 | 0.245 | 20.1 | 17.8 | 1.2225 | 86 | 89.7 | 0.0654 | 0.0472 | 16.09 | 15.29 | 16.22 | 0.93 | 1.756 | 2.608 | 10.66 | 3.1825 | 28.18 | 2.4 | 5.3 | 2022-07-18
2022-07-19 | Click Here |  | 6.74 | 4.99 | 5.05 | 4.7 | 4.72 | 6.38 | 6.45 | 1.59 | 1.7 | 2.06 | 1.98 | 37 | 29 | 16 | 1 | 0 | 0 | 0.581 | 0.445 | 0.918 | 0.14 | 0.338 | 0.333 | 6.2 | 14.5 | 14.7 | 13.8 | 16.8 | 12.1 | 28.7 | 28.6 | 27.4 | 30.8 | 2.94 | 3.19 | 2.9 | 5.8 | 0.082 | 20.3 | 17.9 | 1.3523 | 87.2 | 89.9 | 0.0594 | 0.0459 | 16.39 | 14.81 | 16.48 | 1.67 | 1.47 | 2.57 | 9.932 | 3.3123 | 24.23 | 2.4 | 5.5 | 2022-07-19
2022-07-20 | Click Here |  | 6.32 | 5.06 | 5.13 | 5.04 | 5.09 | 7.84 | 7.68 | 1.44 | 1.55 | 1.88 | 1.85 | 35 | 26 | 8 | 0 | 0 | 0 | 0.536 | 0.466 | 0.55 | 0.198 | 0.225 | 0.121 | 6.2 | 15.4 | 14.8 | 14.7 | 22.3 | 12.3 | 30.6 | 29 | 29.4 | 40.8 | 3.33 | 3.46 | 3 | 6 | 0.197 | 20.9 | 18 | 0.88801 | 65 | 90.6 | 0.1869 | 0.0426 | 14.45 | 14.26 | 14.26 | 0 | 1.47 | 2.57 | 9.932 | 2.738 | 24.32 | 2.5 | 5.5 | 2022-07-20
2022-07-21 | Click Here |  | 6.3 | 5.06 | 5.17 | 5.18 | 5.12 | 7.75 | 7.67 | 1.54 | 1.64 | 1.84 | 1.92 | 36 | 27 | 19 | 1 | 0 | 0 | 0.716 | 0.515 | 1.02 | 0.141 | 0.183 | 0.095 | 6.1 | 15 | 14.6 | 14.7 | 22.3 | 11.9 | 29.5 | 27.7 | 29 | 41.2 | 3.01 | 3.14 | 3 | 5.9 | 0.165 | 20.2 | 18.1 | 1.2375 | 65.8 | 91.3 | 0.1815 | 0.0394 | 15.8 | 14.88 | 15.84 | 0.96 | 1.388 | 2.483 | 11.101 | 3.2375 | 23.89 | 2.5 | 5 | 2022-07-21
2022-07-22 | Click Here |  | 5.9 | 5.27 | 5.01 | 5.23 | 5.8 | 7.8 | 7.77 | 1.5 | 1.66 | 2 | 1.94 | 34 | 27 | 17 | 0 | 0 | 0 | 0.593 | 0.489 | 1.49 | 0.138 | 0.206 | 0.09 | 6.1 | 14.7 | 14.1 | 14.2 | 21.9 | 12.1 | 29.4 | 27.7 | 28.4 | 40.5 | 2.99 | 3.15 | 3 | 5.9 | 0.07 | 20.9 | 18.2 | 1.2194 | 67.9 | 91.5 | 0.1678 | 0.0385 | 16.89 | 15.92 | 16.9 | 0.98 | 1.625 | 2.5 | 12.568 | 3.2094 | 24.62 | 2.5 | 4.8 | 2022-07-22
2022-07-23 | Click Here |  | 6.09 | 5.17 | 5.25 | 5.26 | 5.51 | 7.51 | 7.62 | 1.56 | 1.67 | 2.01 | 1.98 | 38 | 29 | 19 | 1 | 0 | 0 | 0.565 | 0.459 | 0.737 | 0.153 | 0.194 | 0.13 | 6.2 | 14.2 | 14.3 | 14.4 | 21.6 | 12.7 | 29.1 | 29 | 29.5 | 40.4 | 3.06 | 3.27 | 2.9 | 5.8 | 0.092 | 22.2 | 18.7 | 1.2242 | 66.4 | 91.2 | 0.1773 | 0.0399 | 16.59 | 15.67 | 16.65 | 0.98 | 0 | 0 | 0 | 3.1942 | 25.25 | 2.5 | 4.8 | 2022-07-23
2022-07-24 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-07-24
2022-07-25 | Click Here |  | 6.5 | 5.2 | 5.24 | 5.16 | 5 | 7.74 | 7.68 | 1.49 | 1.58 | 2.02 | 1.93 | 34 | 25 | 10 | 1 | 0 | 0 | 0.521 | 0.391 | 1.3 | 0.158 | 0.203 | 0.145 | 6.3 | 14.7 | 14.2 | 14.2 | 21.4 | 13.1 | 30.9 | 29.6 | 29.6 | 40.7 | 3.18 | 3.21 | 3.1 | 5.9 | 0.16 | 23.3 | 19.4 | 0.97376 | 65.6 | 90.4 | 0.1831 | 0.0438 | 17.15 | 16.26 | 17.2 | 0.94 | 1.624 | 2.573 | 11.605 | 2.8938 | 22.19 | 2.3 | 4.8 | 2022-07-25
2022-07-26 | Click Here |  | 6.26 | 4.99 | 5.44 | 4.87 | 4.72 | 7.05 | 7.33 | 1.55 | 1.68 | 2.11 | 1.92 | 34 | 25 | 13 | 1 | 0 | 0 | 0.542 | 0.383 | 1.54 | 0.163 | 0.225 | 0.159 | 6.5 | 14.7 | 13.9 | 13.8 | 20.9 | 13.4 | 30.7 | 28.5 | 29 | 39.6 | 3.2 | 3.31 | 3 | 5.9 | 0.099 | 22.9 | 19.5 | 1.5328 | 65.6 | 91.1 | 0.1828 | 0.0403 | 15.91 | 14.83 | 15.79 | 0.96 | 1.363 | 2.523 | 10.773 | 3.4428 | 22.47 | 2.5 | 4.6 | 2022-07-26
2022-07-27 | Click Here |  | 5.98 | 5.08 | 5.14 | 4.95 | 5.08 | 7.31 | 7.23 | 1.52 | 1.59 | 2.01 | 1.83 | 36 | 27 | 12 | 1 | 0 | 0 | 0.542 | 0.423 | 1.58 | 0.132 | 0.212 | 0.165 | 6.6 | 14.5 | 13.8 | 14.3 | 21.5 | 13.4 | 30.3 | 28.5 | 29.6 | 40.9 | 3.18 | 3.35 | 2.9 | 6 | 0.12 | 22.3 | 19.6 | 1.4025 | 66.2 | 90.9 | 0.1787 | 0.0413 | 15.47 | 14.55 | 15.5 | 0.95 | 1.196 | 2.487 | 9.781 | 3.3025 | 21.17 | 2.5 | 4.6 | 2022-07-27
2022-07-28 | Click Here |  | 6.74 | 5.06 | 5.09 | 4.98 | 5.07 | 7.24 | 7.66 | 1.63 | 1.7 | 1.99 | 1.81 | 33 | 36 | 19 | 2 | 0 | 0 | 0.541 | 0.437 | 1.43 | 0.101 | 0.159 | 0.138 | 6.5 | 14.5 | 13.7 | 14.1 | 21.8 | 13.3 | 30 | 28.1 | 29.2 | 41.8 | 3.15 | 3.27 | 2.9 | 5.9 | 0.084 | 22.1 | 19.7 | 1.2694 | 66.5 | 90 | 0.1784 | 0.0457 | 14.41 | 13.35 | 14.72 | 0.97 | 1.159 | 2.44 | 9.221 | 3.1494 | 0 | 0 | 0 | 2022-07-28
2022-07-29 | Click Here |  | 6.58 | 5.19 | 5.11 | 5.17 | 5.18 | 7.21 | 7.43 | 1.56 | 1.7 | 1.96 | 1.89 | 34 | 26 | 7 | 0 | 0 | 0 | 0.509 | 0.427 | 0.989 | 0.103 | 0.192 | 0.171 | 6.4 | 13.4 | 13.3 | 13.6 | 20.4 | 13.2 | 26.1 | 26.5 | 27.4 | 39.2 | 3.18 | 3.3 | 2.9 | 5.9 | 0.052 | 21.3 | 19.2 | 1.4418 | 66.3 | 90.4 | 0.1786 | 0.0453 | 14.81 | 13.52 | 14.78 | 0.96 | 1.224 | 2.408 | 9.202 | 3.3318 | 21.49 | 2.3 | 4.6 | 2022-07-29
2022-07-30 | Click Here |  | 6.54 | 5.48 | 5.24 | 5.46 | 5.42 | 6.94 | 7.73 | 1.47 | 1.69 | 1.95 | 1.84 | 33 | 26 | 19 | 1 | 0 | 0 | 0.561 | 0.477 | 1.24 | 0.113 | 0.187 | 0.142 | 6.7 | 13.3 | 13.3 | 13.1 | 20.5 | 13.4 | 26.6 | 26.1 | 26.6 | 39.1 | 3.21 | 3.31 | 2.9 | 5.9 | 0.104 | 20.9 | 19.7 | 1.3777 | 66.8 | 90.1 | 0.1782 | 0.0457 | 13.75 | 12.71 | 13.65 | 0.94 | 0 | 0 | 0 | 3.2577 | 21.48 | 2 | 4.7 | 2022-07-30
2022-07-31 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 1.3917 | 0 | 0 | 0 | 0 | 15.27 | 14.27 | 15.23 | 0.96 | 1.239 | 2.432 | 11.164 | 3.2817 | 0 | 2 | 4.8 | 2022-07-31
2022-08-01 | Click Here |  | 5.59 | 4.74 | 5.19 | 5.48 | 6.67 | 7.89 | 7.29 | 1.56 | 1.61 | 1.86 | 1.81 | 36 | 28 | 19 | 1 | 0 | 0 | 0.481 | 0.387 | 1.01 | 0.141 | 0.256 | 0.166 | 6.5 | 13.1 | 13.5 | 13.8 | 20.7 | 13 | 26.5 | 26.8 | 27.9 | 39.4 | 3.13 | 3.33 | 2.8 | 5.9 | 0.072 | 21.3 | 19.6 | 1.3975 | 67.2 | 91.3 | 0.1722 | 0.0392 | 17.17 | 16.27 | 17.21 | 0.94 | 1.287 | 2.476 | 11.461 | 3.2475 | 21.61 | 2 | 4.8 | 2022-08-01
2022-08-02 | Click Here |  | 5.29 | 4.64 | 5.46 | 5.18 | 5.87 | 7.59 | 7.26 | 1.51 | 1.53 | 1.8 | 1.79 | 31 | 24 | 26 | 2 | 1 | 0 | 0.495 | 0.366 | 2.97 | 0.236 | 0.267 | 0.198 | 6.6 | 13.4 | 12.6 | 14.2 | 22.1 | 13.5 | 27.1 | 25.5 | 29.1 | 42 | 3.21 | 3.37 | 2.9 | 5.9 | 0.136 | 22.6 | 19.5 | 1.4994 | 67.8 | 88.9 | 0.1683 | 0.0508 | 19.4 | 16.02 | 16.97 | 0.96 | 1.287 | 2.476 | 11.461 | 3.2494 | 21.22 | 2.3 | 4.7 | 2022-08-02
2022-08-03 | Click Here |  | 5.22 | 4.94 | 4.68 | 5.68 | 5.54 | 7.73 | 7.88 | 1.42 | 1.57 | 1.76 | 1.75 | 32 | 26 | 19 | 1 | 0 | 0 | 0.504 | 0.386 | 1.91 | 0.198 | 0.261 | 0.197 | 6.8 | 14.9 | 14.1 | 14.3 | 22.4 | 14.5 | 31.6 | 29.2 | 30 | 43.3 | 3.15 | 3.33 | 2.7 | 5.9 | 0.179 | 24 | 20.3 | 1.4791 | 69.8 | 91.6 | 0.1558 | 0.038 | 17.17 | 16.05 | 17.02 | 0.97 | 1.368 | 2.509 | 11.155 | 3.2391 | 21.6 | 2.7 | 4.7 | 2022-08-03
2022-08-04 | Click Here |  | 6.89 | 5.64 | 5.45 | 5.41 | 5.69 | 7.09 | 7.05 | 1.51 | 1.7 | 1.88 | 1.86 | 37 | 28 | 16 | 1 | 0 | 0 | 0.564 | 0.375 | 1.13 | 0.201 | 0.269 | 0.184 | 6.8 | 14.9 | 14.3 | 15.4 | 22.3 | 14.1 | 31.4 | 29.6 | 32.1 | 42.8 | 3.13 | 3.26 | 2.9 | 6 | 0.098 | 23.3 | 20 | 1.6938 | 69.7 | 90.2 | 0.1562 | 0.0446 | 16.94 | 15.54 | 16.93 | 1.39 | 1.427 | 2.559 | 11.336 | 3.5438 | 21.37 | 2.9 | 4.5 | 2022-08-04
2022-08-05 | Click Here |  | 5.8 | 5.38 | 5.43 | 5.16 | 5.18 | 7.53 | 7.35 | 1.52 | 1.64 | 2.33 | 1.92 | 27 | 19 | 42 | 2 | 0 | 0 | 0.474 | 0.359 | 2.78 | 0.357 | 0.247 | 0.178 | 6.8 | 13.7 | 12.9 | 13.7 | 21.9 | 14.2 | 28.9 | 26.7 | 28.9 | 42.5 | 3.19 | 3.39 | 3 | 6 | 0.159 | 23.3 | 22.5 | 1.889 | 67.6 | 90 | 0.17 | 0.0455 | 20.08 | 17.85 | 18.15 | 0.3 | 1.623 | 2.612 | 13.079 | 3.309 | 21.33 | 2.6 | 4.7 | 2022-08-05
2022-08-06 | Click Here |  | 6.22 | 5.33 | 5.09 | 5.1 | 5.17 | 7.5 | 7.51 | 1.62 | 1.74 | 2.02 | 0 | 28 | 19 | 11 | 0 | 0 | 0 | 0.444 | 0.342 | 0.84 | 0.179 | 0.229 | 0.165 | 6.7 | 14.1 | 13.5 | 14.1 | 21.3 | 14 | 29.9 | 28 | 29.8 | 41.3 | 3.16 | 3.38 | 3 | 5.9 | 0.012 | 23.4 | 20.4 | 1.9264 | 67.7 | 90.3 | 0.1692 | 0.0434 | 17 | 15.93 | 16.86 | 0.93 | 0 | 0 | 0 | 3.0164 | 21.12 | 2.4 | 4.5 | 2022-08-06
2022-08-07 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.70258 | 0 | 0 | 0 | 0 | 18.84 | 17.9 | 18.79 | 0.89 | 1.652 | 2.756 | 14.334 | 2.5726 | 0 | 0 | 0 | 2022-08-07
2022-08-08 | Click Here |  | 6.56 | 5.41 | 5.45 | 5.47 | 5.49 | 7.24 | 7.45 | 1.53 | 1.77 | 2.06 | 2.02 | 28 | 22 | 18 | 2 | 1 | 0 | 0.53 | 0.413 | 1.47 | 0.131 | 0.214 | 0.199 | 6.9 | 15.7 | 13.8 | 13.6 | 21.2 | 14.4 | 33.5 | 29.9 | 29 | 41.3 | 3.19 | 3.35 | 2.9 | 5.9 | 0.087 | 23.5 | 20.6 | 1.4852 | 67.9 | 90.6 | 0.169 | 0.0436 | 20.25 | 18.5 | 20.43 | 1.93 | 1.668 | 2.929 | 13.641 | 3.4852 | 19.59 | 2.4 | 4.5 | 2022-08-08
2022-08-09 | Click Here |  | 6.64 | 5.32 | 5.13 | 5.4 | 5.46 | 6.84 | 7.58 | 1.69 | 1.76 | 2.15 | 2.1 | 29 | 23 | 11 | 1 | 0 | 0 | 0.524 | 0.347 | 1.07 | 0.126 | 0.197 | 0.214 | 6.9 | 14.4 | 13.2 | 13.7 | 21.3 | 14.1 | 29.9 | 27.1 | 28.5 | 41.4 | 3.23 | 3.29 | 2.9 | 5.9 | 0.068 | 20.9 | 20.5 | 1.3074 | 67.9 | 90.9 | 0.1692 | 0.0134 | 15.83 | 14.82 | 15.77 | 0.95 | 1.28 | 2.941 | 9.556 | 3.3774 | 21.54 | 2.4 | 4.5 | 2022-08-09
2022-08-10 | Click Here |  | 6.51 | 5.8 | 5.22 | 5.41 | 5.29 | 7.91 | 7.26 | 1.64 | 1.7 | 2.16 | 2.07 | 28 | 19 | 10 | 0 | 0 | 0 | 0.513 | 0.373 | 1.23 | 0.277 | 0.2 | 0.139 | 7.1 | 14.7 | 14.1 | 14.3 | 23.3 | 14 | 29.5 | 20.9 | 28.6 | 44.3 | 3.25 | 3.33 | 2.9 | 6 | 0.123 | 21 | 20.2 | 0.6296 | 68.2 | 90.6 | 0.1662 | 0.0427 | 16.31 | 15.46 | 16.24 | 0.78 | 1.292 | 2.807 | 10.244 | 2.7196 | 21.02 | 2.4 | 4.7 | 2022-08-10
2022-08-11 | Click Here |  | 6.47 | 5.62 | 5.38 | 5.37 | 5.46 | 7.23 | 7.73 | 1.55 | 1.75 | 2.06 | 2.03 | 28 | 22 | 3 | 0 | 0 | 0 | 0.503 | 0.284 | 0.991 | 0.121 | 0.146 | 0.121 | 6.8 | 14.3 | 13.2 | 13.6 | 22.6 | 13.6 | 29.1 | 26.2 | 27.4 | 43.4 | 3.21 | 3.32 | 2.9 | 6 | 0.108 | 21 | 20.1 | 1.2511 | 68 | 90.9 | 0.1664 | 0.0423 | 14.56 | 13.5 | 14.47 | 0.97 | 1.306 | 2.557 | 9.689 | 3.4111 | 21.39 | 2.2 | 4.5 | 2022-08-11
2022-08-12 | Click Here |  | 6.59 | 5.89 | 5.29 | 6.41 | 7.01 | 7.89 | 7.6 | 1.65 | 1.77 | 2.11 | 2.09 | 31 | 23 | 9 | 0 | 0 | 0 | 0.514 | 0.342 | 0.914 | 0.165 | 0.211 | 0.124 | 7.5 | 14.2 | 14.4 | 13.8 | 22.4 | 14.5 | 28.2 | 28 | 27.1 | 42.8 | 3.22 | 3.32 | 3 | 5.9 | 0.056 | 20.1 | 19.7 | 1.2179 | 76.8 | 100.9 | 0.1144 | -0.003 | 14.56 | 13.53 | 14.47 | 0.94 | 1.237 | 2.443 | 9.2 | 3.3679 | 21.56 | 2 | 4.5 | 2022-08-12
2022-08-13 | Click Here |  | 6.89 | 5.61 | 5.41 | 6.32 | 6.39 | 7.49 | 7.53 | 1.62 | 1.81 | 2.09 | 2.15 | 29 | 20 | 5 | 0 | 0 | 0 | 0.493 | 0.301 | 0.714 | 0.133 | 0.201 | 0.11 | 7.1 | 14.5 | 14.2 | 14.1 | 21.3 | 13.9 | 28.6 | 28.1 | 27.8 | 40.6 | 3.14 | 3.26 | 2.7 | 5.8 | 0.062 | 20.9 | 19.6 | 1.1861 | 72.3 | 93.5 | 0.1353 | 0.0291 | 15.01 | 14.02 | 15 | 0.98 | 0 | 0 | 0 | 3.3561 | 21.28 | 2 | 4.5 | 2022-08-13
2022-08-14 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-08-14
2022-08-15 | Click Here |  | 6.69 | 5.3 | 5.03 | 5.17 | 5.3 | 7.68 | 7.85 | 1.63 | 1.77 | 2.25 | 2.1 | 27 | 18 | 18 | 1 | 0 | 0 | 0.506 | 0.314 | 1.06 | 0.154 | 0.465 | 0.366 | 7.6 | 15.9 | 14.3 | 14.7 | 22.3 | 14.9 | 31.8 | 20.6 | 29.3 | 42.5 | 3.21 | 3.36 | 3 | 6 | 0.126 | 20.9 | 19.6 | 0.90271 | 70.1 | 89 | 0.1542 | 0.0503 | 14.49 | 13.49 | 14.46 | 0.97 | 1.183 | 2.324 | 9.382 | 3.0427 | 20.99 | 2.2 | 4.5 | 2022-08-15
2022-08-16 | Click Here |  | 6.4 | 5.33 | 5.43 | 5.32 | 5.3 | 7.3 | 7.2 | 1.64 | 1.71 | 2.3 | 2.14 | 26 | 16 | 28 | 3 | 0 | 0 | 0 | 0.53 | 1.31 | 0.166 | 0.236 | 0.164 | 6.7 | 14 | 14.5 | 14.2 | 22.9 | 13.3 | 28.3 | 28.8 | 28 | 43.9 | 3.13 | 3.23 | 2.9 | 5.8 | 0.064 | 0 | 0 | 1.236 | 68.5 | 89.8 | 0.1643 | 0.0463 | 14.65 | 13.6 | 14.53 | 0.93 | 1.256 | 2.189 | 10.536 | 3.386 | 20.76 | 2.2 | 4.3 | 2022-08-16
2022-08-17 | Click Here |  | 6.44 | 5.86 | 5.24 | 5.91 | 5.94 | 7.22 | 7.11 | 1.69 | 1.75 | 2.26 | 2.2 | 33 | 27 | 15 | 1 | 0 | 0 | 0.492 | 0 | 1.22 | 0.148 | 0.178 | 0.107 | 6.9 | 13.5 | 13.9 | 13.8 | 20.6 | 13.8 | 27.5 | 27.7 | 28.1 | 39.4 | 2.95 | 3.13 | 2.9 | 5.9 | 0.056 | 21.4 | 19.9 | 1.3161 | 69.3 | 90.7 | 0.1591 | 0.0421 | 15.42 | 14.37 | 15.36 | 0.99 | 1.298 | 2.141 | 9.868 | 3.4661 | 21.74 | 2.2 | 4.3 | 2022-08-17
2022-08-18 | Click Here |  | 6.94 | 5.39 | 5.68 | 6.48 | 6.49 | 7.96 | 7.24 | 1.57 | 1.61 | 2.16 | 2.23 | 30 | 22 | 19 | 0 | 0 | 0 | 0.492 | 0.206 | 0.809 | 0.175 | 0.227 | 0.133 | 6.8 | 13 | 13.8 | 13.4 | 19.9 | 13.7 | 26.6 | 27.6 | 27.4 | 38.8 | 3.01 | 3.26 | 2.9 | 6 | 0.021 | 21.4 | 20.6 | 0.99014 | 71.5 | 90.4 | 0.1453 | 0.0438 | 14.1 | 13.07 | 14.04 | 0.97 | 1.381 | 2.113 | 9.187 | 3.1401 | 22.04 | 2.2 | 4.3 | 2022-08-18
2022-08-19 | Click Here |  | 6.63 | 5.46 | 5.4 | 5.42 | 5.52 | 6.99 | 7.8 | 1.8 | 1.89 | 2.14 | 2.21 | 31 | 25 | 13 | 1 | 0 | 0 | 0.515 | 0.189 | 0.888 | 0.141 | 0.156 | 0.113 | 6.9 | 13.5 | 12.8 | 12.9 | 20.1 | 13.8 | 27.6 | 25.8 | 25.9 | 38.7 | 3.03 | 3.21 | 2.9 | 6 | 0.062 | 21.3 | 20.3 | 1.1849 | 71.7 | 89.5 | 0.1452 | 0.0481 | 14.68 | 13.75 | 14.7 | 0.95 | 1.565 | 2.073 | 8.817 | 3.3249 | 22.05 | 2.2 | 4.3 | 2022-08-19
2022-08-20 | Click Here |  | 6.74 | 5.39 | 5.18 | 5.41 | 5.43 | 6.93 | 6.84 | 1.56 | 1.7 | 2.2 | 2.2 | 28 | 23 | 12 | 1 | 0 | 0 | 0.497 | 0.136 | 0.903 | 0.147 | 0.216 | 0.199 | 6.7 | 13.7 | 12.9 | 12.9 | 20.3 | 13.6 | 27.8 | 25.7 | 25.8 | 30.8 | 3.06 | 3.26 | 2.9 | 5.9 | 0.057 | 21.2 | 20.3 | 1.3157 | 71.5 | 90.8 | 0.1454 | 0.042 | 13.73 | 12.63 | 13.6 | 0.97 | 0 | 0 | 0 | 3.4257 | 20.45 | 2.1 | 4.4 | 2022-08-20
2022-08-21 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 1.2692 | 0 | 0 | 0 | 0 | 14.27 | 13.33 | 14.28 | 0.95 | 1.509 | 2.068 | 9.19 | 3.3892 | 0 | 2.1 | 4.4 | 2022-08-21
2022-08-22 | Click Here |  | 6.69 | 5.39 | 5.46 | 5.34 | 5.45 | 7.22 | 7.01 | 1.58 | 1.67 | 2.12 | 2.06 | 29 | 22 | 11 | 1 | 0 | 0 | 0.476 | 0.107 | 1.21 | 0.236 | 0.228 | 0.158 | 7 | 12.8 | 13.2 | 13.4 | 20.5 | 14.1 | 26.1 | 26.5 | 27.5 | 39.4 | 3.1 | 3.21 | 3 | 5.9 | 0.031 | 21.6 | 20.1 | 1.274 | 71.1 | 91.2 | 0.1479 | 0.0399 | 15.94 | 14.99 | 15.98 | 0.99 | 1.744 | 2.107 | 10.131 | 3.354 | 20.57 | 2.1 | 4.4 | 2022-08-22
2022-08-23 | Click Here |  | 6.54 | 5.36 | 5.39 | 5.49 | 5.67 | 7.41 | 7.21 | 1.56 | 1.63 | 2.09 | 2.14 | 31 | 26 | 14 | 1 | 0 | 0 | 0.508 | 0.08 | 0.915 | 0.168 | 0.246 | 0.222 | 6.8 | 12.6 | 12.8 | 13.2 | 20.1 | 13.6 | 25.8 | 25.5 | 26.9 | 39.1 | 3.03 | 3.26 | 2.9 | 5.7 | 0.043 | 21.6 | 20.5 | 1.34 | 71.5 | 91.7 | 0.1456 | 0.0377 | 15.03 | 14.05 | 14.99 | 0.94 | 1.812 | 2.11 | 9.904 | 3.42 | 20.47 | 2.1 | 4.4 | 2022-08-23
2022-08-24 | Click Here |  | 6.58 | 5.75 | 5.55 | 5.64 | 5.73 | 7.08 | 7.3 | 1.52 | 1.57 | 2.15 | 2.03 | 27 | 16 | 28 | 0 | 1 | 0 | 0.495 | 0.946 | 1.25 | 0.28 | 0.292 | 0.205 | 6.9 | 13.8 | 12.9 | 13.2 | 20.7 | 13.8 | 28.3 | 25.7 | 26.5 | 39.7 | 3.15 | 3.24 | 2.9 | 5.9 | 0.109 | 21.8 | 20.1 | 1.4484 | 69.2 | 89.3 | 0.1599 | 0.0489 | 14.67 | 13.58 | 14.54 | 0.96 | 1.745 | 2.1 | 8.683 | 3.5384 | 20.01 | 2.1 | 4.4 | 2022-08-24
2022-08-25 | Click Here |  | 6.26 | 5.54 | 5.56 | 5.55 | 5.57 | 7.7 | 7.03 | 1.7 | 1.76 | 2.14 | 1.95 | 26 | 16 | 24 | 0 | 1 | 0 | 0.591 | 0.971 | 1.66 | 0.233 | 0.265 | 0.192 | 6.9 | 13.8 | 13.4 | 13.3 | 20.3 | 13.9 | 28.6 | 26.9 | 27.4 | 39.2 | 3.09 | 3.22 | 3 | 6 | 0.101 | 22 | 20.3 | 0.8056 | 71 | 90.7 | 0.1485 | 0.042 | 15 | 14.03 | 14.98 | 0.95 | 1.737 | 2.098 | 9.246 | 2.9256 | 20.07 | 1.9 | 4.4 | 2022-08-25
2022-08-26 | Click Here |  | 6.31 | 5.41 | 5.33 | 5.44 | 5.48 | 7.1 | 7.07 | 1.61 | 1.69 | 2.11 | 1.94 | 26 | 16 | 23 | 0 | 0 | 0 | 0.621 | 0.519 | 1.57 | 0.198 | 0.234 | 0.197 | 6.8 | 13.8 | 13.6 | 13.4 | 21.1 | 13.7 | 28.6 | 26.8 | 27.2 | 42 | 3.02 | 3.19 | 3.1 | 6 | 0.088 | 22 | 20.2 | 0.7531 | 69.8 | 91 | 0.151 | 0.0406 | 14.58 | 13.38 | 14.43 | 1.05 | 1.767 | 2.082 | 8.883 | 2.8431 | 20.69 | 1.8 | 4.4 | 2022-08-26
2022-08-27 | Click Here |  | 6.28 | 5.34 | 5.32 | 5.36 | 5.41 | 7.11 | 7.01 | 1.6 | 1.66 | 2.1 | 1.98 | 26 | 16 | 24 | 0 | 1 | 0 | 0.585 | 0.521 | 1.48 | 0.189 | 0.216 | 0.202 | 6.8 | 13.7 | 13.8 | 13.3 | 22.1 | 13.6 | 28.5 | 26.9 | 27 | 43.8 | 3.09 | 3.2 | 3 | 5.9 | 0.081 | 21.9 | 20.1 | 1.3242 | 70.1 | 91.1 | 0.1491 | 0.04 | 14.26 | 13.22 | 14.17 | 0.95 | 0 | 0 | 0 | 3.5142 | 20.63 | 1.8 | 4.4 | 2022-08-27
2022-08-28 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 1.3976 | 0 | 0 | 0 | 0 | 14.4 | 13.29 | 14.28 | 0.99 | 1.58 | 2.082 | 8.997 | 3.5876 | 0 | 1.8 | 4.4 | 2022-08-28
2022-08-29 | Click Here |  | 6.39 | 5.42 | 5.33 | 5.49 | 5.57 | 7.88 | 7.6 | 1.64 | 1.7 | 2.09 | 2.15 | 30 | 24 | 27 | 0 | 0 | 0 | 0.516 | 0.528 | 1.62 | 0.177 | 0.258 | 0.204 | 6.8 | 12.8 | 12.4 | 12.5 | 21.3 | 13.7 | 26.8 | 24.8 | 25.3 | 41.1 | 3.08 | 3.26 | 3 | 6.1 | 0.137 | 22 | 20.3 | 1.2563 | 71.3 | 90.5 | 0.1466 | 0.0432 | 15.49 | 14.48 | 15.44 | 0.96 | 1.684 | 2.082 | 9.514 | 3.4063 | 20.17 | 1.8 | 4.4 | 2022-08-29
2022-08-30 | Click Here |  | 6.74 | 5.89 | 5.51 | 6.36 | 6.32 | 7.81 | 8.45 | 1.53 | 1.7 | 2.01 | 2.09 | 30 | 22 | 24 | 2 | 0 | 0 | 0.547 | 0.531 | 1.87 | 0.294 | 0.541 | 0.652 | 6.9 | 13.1 | 13.4 | 13.5 | 22.6 | 13.9 | 26.5 | 26.8 | 27.6 | 43.3 | 3.14 | 3.33 | 2.8 | 5.9 | 0.046 | 21.8 | 20 | 1.2935 | 75.1 | 94.3 | 0.1229 | 0.0252 | 15.77 | 14.75 | 15.74 | 0.99 | 1.768 | 2.082 | 10.368 | 3.3935 | 19.42 | 1.8 | 4.4 | 2022-08-30
2022-08-31 | Click Here |  | 6.41 | 5.85 | 5.94 | 5.68 | 5.62 | 7.71 | 7.79 | 1.51 | 1.71 | 2.32 | 2.09 | 27 | 19 | 22 | 4 | 0 | 0 | 0.564 | 0.519 | 1.55 | 0.2 | 0.223 | 0.18 | 6.9 | 13.5 | 13.6 | 13.4 | 21.9 | 13.8 | 27.5 | 27.2 | 27.4 | 42.2 | 3.03 | 3.36 | 2.9 | 5.9 | 0.122 | 21.6 | 20.1 | 1.4043 | 70.1 | 90.2 | 0.1542 | 0.0446 | 15.47 | 14.49 | 15.44 | 0.95 | 1.915 | 2.082 | 10.572 | 3.4543 | 21.08 | 1.8 | 4.4 | 2022-08-31
2022-09-01 | Click Here |  | 6.77 | 5.89 | 5.79 | 5.66 | 5.31 | 7.45 | 7.13 | 1.56 | 1.61 | 2.27 | 1.91 | 27 | 18 | 21 | 1 | 0 | 0 | 0.561 | 0.547 | 1.49 | 0.189 | 0.243 | 0.222 | 6.9 | 13.3 | 13.5 | 13.6 | 22.1 | 13.7 | 27.4 | 27.3 | 27.5 | 42.4 | 3.11 | 3.18 | 3 | 5.9 | 0.075 | 21.5 | 20.1 | 1.3571 | 70.2 | 90.4 | 0.1544 | 0.0419 | 15.32 | 14.3 | 15.27 | 0.97 | 1.862 | 2.082 | 9.172 | 3.3371 | 19.9 | 1.6 | 4.2 | 2022-09-01
2022-09-02 | Click Here |  | 6.74 | 5.39 | 5.51 | 5.17 | 5.19 | 5.26 | 5.59 | 1.65 | 1.79 | 2.14 | 2.07 | 31 | 27 | 29 | 1 | 0 | 0 | 0.599 | 0.574 | 0.808 | 0.19 | 0.233 | 0.136 | 7.2 | 13.1 | 13.6 | 13.7 | 15.2 | 14.6 | 27.1 | 27.6 | 28.1 | 29.6 | 3.11 | 3.23 | 2.9 | 6 | 0.021 | 22.3 | 20.7 | 1.3402 | 72.3 | 92 | 0.1404 | 0.0362 | 15.21 | 14.2 | 15.16 | 0.96 | 1.739 | 2.082 | 9.273 | 3.4002 | 20.99 | 1.6 | 4.2 | 2022-09-02
2022-09-03 | Click Here |  | 6.49 | 5.48 | 5.57 | 5.29 | 5.48 | 6.89 | 6.64 | 1.62 | 1.74 | 2.09 | 2.04 | 30 | 22 | 31 | 0 | 0 | 0 | 0.601 | 0.567 | 0.786 | 0.174 | 0.206 | 0.154 | 7.4 | 13.3 | 14.1 | 14.5 | 15.7 | 14.9 | 27.9 | 27.7 | 29.8 | 30.9 | 3.18 | 3.29 | 3 | 6.1 | 0.037 | 22.1 | 20.4 | 1.4793 | 72.5 | 92.6 | 0.1389 | 0.0337 | 14.44 | 13.37 | 14.35 | 0.98 | 0 | 0 | 0 | 3.5193 | 20.13 | 1.6 | 4.2 | 2022-09-03
2022-09-04 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-09-04
2022-09-05 | Click Here |  | 6.43 | 5.92 | 5.5 | 5.52 | 5.53 | 5.42 | 5.17 | 1.78 | 1.87 | 2.23 | 2.01 | 28 | 18 | 30 | 3 | 0 | 0 | 0.606 | 0.649 | 2.02 | 0.384 | 0.23 | 0.108 | 7.1 | 14.4 | 13.2 | 13 | 14.6 | 14.4 | 29.6 | 27.2 | 27.1 | 28.4 | 3.13 | 3.17 | 3 | 6 | 0.051 | 22.2 | 20.6 | 1.0947 | 73.5 | 91.7 | 0.1334 | 0.0374 | 14.09 | 12.97 | 13.97 | 1 | 1.527 | 2.082 | 8.569 | 3.1647 | 21.15 | 1.6 | 4.3 | 2022-09-05
2022-09-06 | Click Here |  | 6.05 | 5.61 | 5.65 | 5.79 | 5.55 | 5.65 | 5.07 | 1.78 | 1.88 | 2.25 | 1.98 | 23 | 16 | 32 | 0 | 0 | 0 | 0.553 | 0.588 | 3.12 | 0.393 | 0.276 | 0.218 | 7.2 | 13 | 12.7 | 13.6 | 14.8 | 14.2 | 25.9 | 24.8 | 27.6 | 28.7 | 2.99 | 3.14 | 3 | 5.9 | 0.123 | 20.6 | 20.2 | 1.605 | 70.6 | 91.8 | 0.1509 | 0.037 | 15.92 | 12.99 | 13.98 | 0.99 | 1.643 | 2.082 | 8.366 | 3.545 | 20.48 | 1.5 | 4.3 | 2022-09-06
2022-09-07 | Click Here |  | 6.11 | 5.68 | 5.74 | 5.93 | 5.88 | 7.7 | 7.56 | 1.49 | 1.72 | 1.94 | 1.91 | 27 | 20 | 44 | 2 | 0 | 0 | 0.602 | 0.612 | 1.38 | 0.252 | 0.202 | 0.134 | 7 | 13.7 | 13.3 | 13.5 | 20.2 | 13.6 | 26.9 | 25.1 | 27 | 38.6 | 2.99 | 3.21 | 2.8 | 5.9 | 0.013 | 19.8 | 19.9 | 1.4238 | 72.2 | 91 | 0.1409 | 0.0406 | 15.76 | 13.66 | 14.64 | 0.98 | 1.594 | 2.082 | 8.82 | 3.3638 | 20.87 | 1.5 | 4.3 | 2022-09-07
2022-09-08 | Click Here |  | 6.09 | 5.54 | 5.7 | 5.8 | 5.74 | 7.84 | 7.99 | 1.55 | 1.74 | 1.99 | 2 | 27 | 19 | 5 | 0 | 0 | 0 | 0.517 | 0.567 | 0.425 | 0.116 | 0.137 | 0.104 | 6.8 | 13.4 | 13.7 | 13.9 | 19.8 | 13.7 | 27.5 | 28.1 | 28.4 | 38.7 | 2.93 | 3.18 | 3 | 5.8 | 0.041 | 19.6 | 19.7 | 1.7755 | 72 | 91.9 | 0.142 | 0.0361 | 14.15 | 13.05 | 14.03 | 0.98 | 1.601 | 2.082 | 8.165 | 3.8355 | 20.22 | 1.5 | 4.1 | 2022-09-08
2022-09-09 | Click Here |  | 6.58 | 5.36 | 5.48 | 5.47 | 5.46 | 7.4 | 7.95 | 1.58 | 1.78 | 2.1 | 2.12 | 28 | 21 | 7 | 0 | 0 | 0 | 0.526 | 0.513 | 0.583 | 0.104 | 0.126 | 0.097 | 6.6 | 13.2 | 13.8 | 13.9 | 19.9 | 13.5 | 27.5 | 28.3 | 28.7 | 38.5 | 2.97 | 3.12 | 2.9 | 5.9 | 0.046 | 19.5 | 19.8 | 1.0954 | 72.2 | 91.7 | 0.1418 | 0.0363 | 13.64 | 12.65 | 13.63 | 0.98 | 1.509 | 2.082 | 8.463 | 3.1654 | 20.89 | 1.5 | 4.1 | 2022-09-09
2022-09-10 | Click Here |  | 6.69 | 5.61 | 5.3 | 5.84 | 5.69 | 6.97 | 7.63 | 1.82 | 1.89 | 2.15 | 2.13 | 25 | 19 | 9 | 0 | 0 | 0 | 0.543 | 0.517 | 0.63 | 0.112 | 0.128 | 0.09 | 7.1 | 12.6 | 12.5 | 12.3 | 19.1 | 13.4 | 24.7 | 23.3 | 24.1 | 36.3 | 3.01 | 3.19 | 2.9 | 5.9 | 0.038 | 18.7 | 19.3 | 1.7409 | 70.8 | 91.5 | 0.1496 | 0.0384 | 13.36 | 12.74 | 13.7 | 0.96 | 0 | 0 | 0 | 3.3309 | 21.22 | 1.5 | 4.1 | 2022-09-10
2022-09-11 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 1.2812 | 0 | 0 | 0 | 0 | 14.02 | 12.91 | 13.9 | 0.99 | 1.542 | 2.082 | 8.203 | 3.3412 | 0 | 1.5 | 4.1 | 2022-09-11
2022-09-12 | Click Here |  | 6.47 | 5.47 | 5.66 | 5.71 | 5.54 | 7.26 | 7.59 | 1.69 | 1.9 | 2.11 | 2.04 | 29 | 21 | 10 | 0 | 0 | 0 | 0.627 | 0.814 | 0.617 | 0.139 | 0.134 | 0.156 | 6.9 | 12.2 | 12.9 | 12.7 | 20.4 | 13 | 24.4 | 25.7 | 24.9 | 37.9 | 3.06 | 3.32 | 2.8 | 6 | 0.042 | 18.5 | 19.1 | 1.3141 | 71.1 | 91.9 | 0.1472 | 0.0361 | 13.91 | 12.84 | 13.83 | 0.99 | 1.552 | 2.082 | 7.693 | 3.3541 | 21.83 | 1.5 | 4.1 | 2022-09-12
2022-09-13 | Click Here |  | 6.59 | 5.41 | 5.57 | 5.6 | 5.52 | 7.68 | 7.54 | 1.74 | 1.96 | 2.11 | 2.04 | 33 | 25 | 5 | 0 | 0 | 0 | 0.698 | 0.774 | 0.541 | 0.167 | 0.192 | 0.144 | 7 | 12.7 | 13.3 | 13 | 21.7 | 13.3 | 24.8 | 27.7 | 26.4 | 38.9 | 2.94 | 3.21 | 2.8 | 5.9 | 0.056 | 18.6 | 19 | 1.8292 | 70.8 | 92.4 | 0.1491 | 0.0346 | 14.26 | 13.14 | 14.12 | 0.73 | 1.548 | 2.082 | 8.453 | 3.8092 | 21.83 | 1.5 | 4.1 | 2022-09-13
2022-09-14 | Click Here |  | 6.52 | 5.59 | 5.56 | 5.37 | 5.4 | 7.81 | 7.25 | 1.93 | 1.96 | 2.03 | 1.96 | 27 | 22 | 16 | 2 | 0 | 0 | 0.727 | 0.688 | 0.963 | 0.124 | 0.147 | 0.121 | 6.9 | 13.8 | 12.5 | 12.9 | 22.2 | 12.7 | 27.1 | 22.6 | 24.7 | 40.8 | 2.98 | 3.14 | 2.9 | 5.9 | 0.087 | 17.5 | 18.7 | 1.6113 | 70.5 | 89.7 | 0.1489 | 0.0472 | 13.46 | 12.44 | 13.39 | 0.95 | 1.547 | 2.082 | 7.863 | 3.5513 | 20.33 | 1.5 | 4.1 | 2022-09-14
2022-09-15 | Click Here |  | 6.52 | 5.59 | 5.37 | 5.62 | 5.73 | 7.01 | 6.99 | 1.61 | 1.7 | 1.87 | 1.83 | 28 | 22 | 7 | 0 | 0 | 0 | 0.552 | 0.622 | 0.895 | 0.142 | 0.147 | 0.132 | 7.1 | 12.9 | 13.1 | 12.8 | 19.9 | 13.2 | 24.7 | 23.7 | 24.9 | 36.7 | 2.97 | 3.1 | 2.9 | 5.9 | 0.074 | 18.2 | 18.2 | 1.2692 | 70.2 | 91.3 | 0.1535 | 0.0392 | 13.77 | 12.68 | 13.66 | 0.98 | 1.559 | 2.082 | 7.844 | 3.0792 | 20.85 | 1.5 | 4.1 | 2022-09-15
2022-09-16 | Click Here |  | 6.52 | 5.44 | 5.94 | 5.93 | 5.87 | 7.91 | 7.5 | 1.72 | 1.76 | 2.26 | 1.88 | 25 | 18 | 22 | 1 | 0 | 0 | 0.612 | 0.664 | 1.52 | 0.212 | 0.214 | 0.138 | 6.8 | 13.1 | 13.2 | 13.6 | 21.1 | 12.8 | 20.5 | 24 | 26.2 | 39 | 3.14 | 3.26 | 3.1 | 5.9 | 0.063 | 18.9 | 18.2 | 1.1959 | 72.3 | 92.6 | 0.1403 | 0.033 | 13.87 | 12.81 | 13.76 | 0.95 | 1.551 | 2.082 | 8.344 | 3.1259 | 20.65 | 1.5 | 4.1 | 2022-09-16
2022-09-17 | Click Here |  | 6.62 | 5.62 | 5.39 | 5.75 | 5.62 | 8.34 | 7.36 | 1.72 | 1.79 | 2.25 | 2.11 | 28 | 19 | 18 | 1 | 0 | 0 | 0.547 | 0.607 | 0.799 | 0.18 | 0.237 | 0.139 | 6.8 | 12.6 | 12.9 | 12.7 | 20.2 | 12.5 | 24.2 | 23.1 | 23.2 | 37.1 | 2.9 | 3.09 | 3 | 6 | 0.132 | 17.7 | 18 | 1.4151 | 71.1 | 95.2 | 0.1477 | 0.021 | 13.52 | 12.46 | 13.43 | 0.97 | 1.558 | 1.4 | 7.542 | 3.5351 | 20.8 | 1.4 | 3.8 | 2022-09-17
2022-09-18 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 1.1824 | 0 | 0 | 0 | 0 | 13.19 | 12.17 | 13.11 | 0.97 | 1.501 | 2.082 | 7.495 | 3.3724 | 0 | 0 | 0 | 2022-09-18
2022-09-19 | Click Here |  | 6.4 | 5.71 | 5.28 | 5.76 | 5.77 | 6.93 | 6.91 | 1.65 | 1.93 | 2.15 | 2.23 | 30 | 23 | 11 | 1 | 0 | 0 | 0.738 | 0.673 | 0.841 | 0.101 | 0.146 | 0.14 | 7 | 14.6 | 12.9 | 12.6 | 19.5 | 12.5 | 27.7 | 22.1 | 22.1 | 35 | 2.94 | 3.06 | 2.9 | 5.8 | 0.08 | 15.9 | 17 | 1.4752 | 63.5 | 90.8 | 0.1971 | 0.0417 | 13.69 | 12.64 | 13.62 | 0.98 | 1.459 | 2.082 | 8.66 | 3.6852 | 22.14 | 1.4 | 3.8 | 2022-09-19
2022-09-20 | Click Here |  | 6.69 | 5.8 | 5.41 | 5.68 | 5.61 | 6.97 | 7.52 | 1.52 | 1.66 | 2.08 | 2.14 | 29 | 24 | 12 | 1 | 0 | 0 | 0.653 | 0.597 | 0.981 | 0.114 | 0.136 | 0.113 | 7 | 13.5 | 13 | 12.6 | 20.9 | 12.2 | 24.6 | 21.9 | 21.7 | 37.4 | 2.98 | 3.04 | 2.9 | 5.8 | 0.116 | 15.4 | 16.9 | 1.2997 | 63.9 | 91.2 | 0.1967 | 0.0396 | 13.93 | 12.89 | 13.87 | 0.98 | 1.406 | 2.082 | 8.115 | 3.3397 | 21.72 | 1.4 | 4 | 2022-09-20
2022-09-21 | Click Here |  | 6.72 | 5.78 | 4.63 | 5.7 | 5.98 | 8.2 | 7.19 | 1.95 | 2.05 | 2.5 | 2.14 | 22 | 14 | 18 | 3 | 0 | 0 | 0.521 | 0.569 | 1.02 | 0.195 | 0.248 | 0.151 | 6.9 | 12.7 | 13.1 | 13.1 | 22.8 | 12.1 | 23.2 | 22.2 | 22.8 | 40.8 | 3.03 | 3.15 | 3.1 | 5.9 | 0.265 | 15.5 | 16.8 | 0.87664 | 72.2 | 92.7 | 0.1413 | 0.033 | 13.5 | 12.32 | 13.3 | 0.98 | 1.449 | 2.082 | 7.58 | 3.0066 | 21.14 | 1 | 3 | 2022-09-21
2022-09-22 | Click Here |  | 6.84 | 5.69 | 5.61 | 5.52 | 5.74 | 7.76 | 6.84 | 1.87 | 1.94 | 2.3 | 2.04 | 26 | 17 | 14 | 1 | 0 | 0 | 0.535 | 0.568 | 1.04 | 0.164 | 0.303 | 0.252 | 6.8 | 12.8 | 12.7 | 12 | 20 | 12.2 | 23.9 | 21.7 | 21.1 | 35.6 | 3.01 | 3.18 | 3 | 5.9 | 0.159 | 16.3 | 16.8 | 0.98271 | 71.1 | 92.1 | 0.1479 | 0.0354 | 13.28 | 12.34 | 13.31 | 0.97 | 1.449 | 2.082 | 7.932 | 3.0827 | 20.81 | 1 | 2.9 | 2022-09-22
2022-09-23 | Click Here |  | 6.74 | 5.6 | 5.37 | 5.62 | 5.57 | 6.78 | 7.22 | 1.86 | 1.94 | 2.24 | 2.12 | 27 | 20 | 7 | 0 | 0 | 0 | 0.51 | 0.437 | 0.681 | 0.103 | 0.147 | 0.126 | 7.1 | 12.8 | 12.7 | 11.6 | 18.8 | 12.6 | 23.5 | 21.9 | 20.5 | 33.7 | 2.98 | 3.12 | 2.9 | 5.9 | 0.085 | 16.2 | 16.8 | 1.2365 | 69.8 | 91.8 | 0.1481 | 0.0357 | 13.01 | 11.93 | 12.88 | 0.95 | 1.48 | 2.082 | 8.322 | 3.3565 | 20.83 | 0.8 | 2.7 | 2022-09-23
2022-09-24 | Click Here |  | 6.77 | 5.57 | 5.3 | 5.56 | 5.61 | 7.47 | 6.81 | 1.84 | 1.92 | 2.16 | 2.1 | 29 | 23 | 9 | 1 | 0 | 0 | 0.596 | 0.567 | 0.596 | 0.116 | 0.157 | 0.129 | 7.1 | 12.5 | 13.3 | 11.6 | 18 | 12.9 | 23.7 | 16.1 | 20.9 | 32.4 | 3.01 | 3.19 | 2.9 | 5.9 | 0.07 | 17 | 16.9 | 1.2948 | 69.5 | 91.3 | 0.1454 | 0.036 | 13.18 | 12.08 | 13.06 | 0.98 | 1.536 | 2.082 | 7.772 | 3.3148 | 20.08 | 0.7 | 2.9 | 2022-09-24
2022-09-25 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-09-25
2022-09-26 | Click Here |  | 6.79 | 5.38 | 5.26 | 5.15 | 5.25 | 7.25 | 7.08 | 1.75 | 1.85 | 2.32 | 1.95 | 58 | 41 | 44 | 6 | 5 | 0 | 1.77 | 2.172 | 1.99 | 0.373 | 0.677 | 0.534 | 6.5 | 13.6 | 13.4 | 12.7 | 18.9 | 11.4 | 25.7 | 22.9 | 22.4 | 33.8 | 3.05 | 3.13 | 3 | 5.8 | 0.123 | 15.9 | 16.8 | 0.90781 | 70.7 | 90.4 | 0.1502 | 0.0436 | 12.52 | 11.43 | 12.41 | 0.98 | 1.483 | 2.082 | 8.048 | 2.9778 | 20.91 | 0.6 | 2.9 | 2022-09-26
2022-09-27 | Click Here |  | 6.51 | 5.45 | 5.31 | 5.19 | 5.37 | 7.51 | 6.8 | 1.63 | 1.7 | 2.13 | 1.95 | 50 | 38 | 41 | 8 | 4 | 0 | 1.93 | 2.028 | 2.45 | 0.424 | 0.659 | 0.534 | 6.4 | 12.8 | 12.9 | 12.4 | 17.3 | 11.5 | 24.6 | 22.5 | 22.1 | 30.8 | 2.96 | 3.13 | 2.9 | 6 | 0.092 | 17 | 16.7 | 1.1424 | 70 | 89.6 | 0.1549 | 0.0477 | 14.38 | 13.38 | 14.34 | 0.96 | 1.706 | 2.082 | 8.858 | 3.1424 | 20.94 | 0.6 | 2.9 | 2022-09-27
2022-09-28 | Click Here |  | 6.42 | 5.3 | 5.38 | 5.21 | 5.39 | 7.4 | 7.48 | 1.68 | 1.82 | 2.01 | 1.91 | 54 | 44 | 33 | 4 | 2 | 0 | 1.84 | 1.6 | 1.46 | 0.391 | 1.51 | 1.85 | 6.5 | 13.3 | 13.9 | 12.98 | 15.1 | 12 | 26.1 | 24.8 | 23.3 | 32.2 | 3.03 | 3.13 | 2.8 | 5.9 | 0.012 | 17.6 | 16.9 | 1.2725 | 68.8 | 89.2 | 0.1591 | 0.495 | 14.5 | 13.49 | 14.48 | 0.99 | 1.702 | 2.082 | 7.818 | 3.1925 | 22.59 | 0.5 | 2.9 | 2022-09-28
2022-09-29 | Click Here |  | 6.47 | 5.29 | 5.35 | 5.32 | 5.44 | 7.28 | 7.48 | 1.7 | 1.93 | 2.04 | 1.91 | 61 | 52 | 39 | 6 | 4 | 0 | 1.48 | 1.54 | 1.21 | 0.314 | 0.569 | 0.446 | 6.5 | 13.9 | 14.1 | 13 | 18.7 | 12.1 | 28.8 | 25.2 | 23.7 | 34.9 | 2.96 | 3.09 | 2.9 | 5.8 | 0.041 | 17.4 | 16.8 | 1.4439 | 68.1 | 90.9 | 0.1682 | 0.0414 | 13.77 | 12.72 | 13.71 | 0.99 | 1.702 | 2.082 | 7.818 | 3.3839 | 22.87 | 0.5 | 2.8 | 2022-09-29
2022-09-30 | Click Here |  | 6.44 | 5.19 | 5.34 | 5.05 | 5.04 | 6.71 | 7.6 | 1.64 | 1.81 | 1.97 | 1.89 | 60 | 51 | 36 | 4 | 2 | 0 | 1.42 | 1.34 | 1.18 | 0.326 | 0.742 | 0.613 | 6.6 | 18.2 | 14 | 12.4 | 17.7 | 12 | 34.4 | 24.8 | 24.5 | 31.9 | 3.01 | 3.07 | 2.9 | 5.9 | 0.058 | 16.6 | 17 | 1.4109 | 66.2 | 88.6 | 0.1939 | 0.0525 | 13.39 | 12.29 | 13.24 | 0.95 | 1.491 | 2.082 | 7.655 | 3.3409 | 24.91 | 0.5 | 2.8 | 2022-09-30
2022-10-01 | Click Here |  | 6.38 | 5.18 | 5.37 | 5.08 | 5.06 | 6.79 | 7.08 | 1.61 | 1.78 | 1.95 | 1.89 | 27 | 22 | 20 | 4 | 3 | 0 | 1.04 | 1.17 | 1.86 | 0.397 | 0.817 | 0.713 | 6.5 | 14.9 | 14.8 | 14.4 | 18.7 | 11.7 | 27.6 | 26 | 26.2 | 39.5 | 3.03 | 3.11 | 2.9 | 5.8 | 0.081 | 16.2 | 16.9 | 1.43 | 66 | 88.9 | 0.1937 | 0.0522 | 12.96 | 11.91 | 12.89 | 0.98 | 0 | 0 | 0 | 3.34 | 26.65 | 0.5 | 3.3 | 2022-10-01
2022-10-02 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 1.4512 | 0 | 0 | 0 | 0 | 13.91 | 12.9 | 13.87 | 0.97 | 0 | 0 | 0 | 3.3212 | 0 | 0.5 | 3.6 | 2022-10-02
2022-10-03 | Click Here |  | 6.19 | 5.31 | 5.44 | 5.14 | 5.2 | 7.24 | 7.39 | 1.59 | 1.74 | 1.98 | 1.92 | 31 | 24 | 25 | 6 | 2 | 0 | 0.992 | 1.06 | 1.74 | 0.59 | 0.82 | 0.845 | 6.5 | 12.9 | 12.2 | 12.3 | 17 | 11.2 | 23.7 | 20.3 | 21.5 | 30.1 | 2.96 | 3.19 | 2.8 | 5.9 | 0.057 | 14.3 | 16.3 | 1.6603 | 72.8 | 90.5 | 0.1376 | 0.0432 | 14.26 | 12.37 | 14.25 | 1.88 | 1.596 | 2.082 | 7.498 | 3.5703 | 20.88 | 0.5 | 3.6 | 2022-10-03
2022-10-04 | Click Here |  | 6.64 | 6.15 | 5.63 | 6.25 | 6.14 | 7.71 | 6.74 | 1.73 | 1.94 | 2.01 | 1.96 | 29 | 21 | 20 | 1 | 3 | 0 | 0.907 | 0.918 | 0.925 | 0.278 | 0.773 | 0.474 | 6.7 | 15.3 | 12.6 | 13.7 | 17.9 | 11.1 | 27.7 | 20.6 | 23.6 | 31.3 | 3 | 3.21 | 3.1 | 6 | 0.173 | 13.4 | 15.7 | 1.0568 | 73.1 | 89.8 | 0.1361 | 0.0465 | 12.82 | 12.69 | 12.69 | 0 | 1.483 | 2.082 | 7.62 | 3.0768 | 20.44 | 2.5 | 3.6 | 2022-10-04
2022-10-05 | Click Here |  | 6.51 | 5.44 | 6.52 | 5.17 | 5.42 | 6.78 | 6.85 | 1.92 | 2.04 | 2.28 | 2.04 | 33 | 24 | 33 | 3 | 1 | 0 | 0.842 | 0.929 | 2.48 | 0.229 | 0.343 | 0.224 | 6.5 | 13.4 | 12.8 | 12.5 | 15.5 | 10.9 | 24.5 | 20.9 | 21.6 | 26.8 | 2.99 | 3.2 | 3 | 6 | 0.09 | 13.6 | 15.4 | 1.0882 | 73.3 | 92.9 | 0.1349 | 0.0319 | 12.69 | 11.62 | 12.63 | 1.01 | 1.483 | 2.082 | 7.62 | 3.1882 | 21.74 | 2 | 3.2 | 2022-10-05
2022-10-06 | Click Here |  | 6.76 | 5.31 | 5.1 | 5.33 | 5.29 | 6.76 | 6.37 | 1.71 | 1.91 | 2.08 | 1.9 | 31 | 22 | 25 | 1 | 1 | 0 | 0.819 | 0.849 | 1.55 | 0.391 | 0.512 | 0.44 | 6.5 | 13.8 | 13.5 | 13.3 | 15.9 | 11.3 | 26.2 | 22.3 | 23 | 27.7 | 2.94 | 3.13 | 3.1 | 5.9 | 0.082 | 15.6 | 15.4 | 1.1303 | 73 | 91.8 | 0.1366 | 0.0372 | 13.33 | 12.27 | 13.25 | 0.98 | 1.483 | 2.082 | 7.62 | 3.1003 | 21.87 | 1.8 | 3.8 | 2022-10-06
2022-10-07 | Click Here |  | 6.73 | 5.27 | 5.28 | 5.19 | 5.06 | 6.78 | 6.54 | 1.79 | 1.82 | 2.14 | 1.89 | 31 | 20 | 19 | 1 | 0 | 0 | 0.749 | 0.771 | 1.73 | 0.555 | 0.692 | 0.542 | 6.4 | 13.7 | 14.4 | 13.9 | 16.3 | 11.4 | 26.6 | 24 | 24.5 | 28.5 | 2.97 | 3.11 | 2.9 | 6 | 0.148 | 16 | 15.6 | -9.0218 | 56.6 | 90.4 | 0.247 | 0.0436 | 13.1 | 12.02 | 13.02 | 1 | 1.483 | 2.082 | 7.62 | 2.9982 | 24.96 | 1.7 | 4.5 | 2022-10-07
2022-10-08 | Click Here |  | 6.71 | 5.05 | 5.27 | 5.24 | 5.2 | 7.18 | 7.34 | 1.72 | 1.88 | 2.1 | 1.98 | 31 | 22 | 20 | 1 | 1 | 0 | 0.749 | 0.737 | 1.46 | 0.312 | 0.344 | 0.363 | 6.5 | 13.4 | 13.8 | 13.6 | 17.2 | 11.6 | 26.5 | 25.9 | 24.2 | 33.4 | 3.03 | 3.21 | 3 | 5.8 | 0.091 | 15.9 | 15.6 | 1.2228 | 57.2 | 90.1 | 0.2414 | 0.0443 | 12.39 | 11.35 | 12.29 | 0.94 | 0 | 0 | 0 | 3.0428 | 21.1 | 1.7 | 4.5 | 2022-10-08
2022-10-09 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 1.1409 | 0 | 0 | 0 | 0 | 12.63 | 11.53 | 12.5 | 0.97 | 1.483 | 2.082 | 7.62 | 2.9209 | 0 | 0 | 0 | 2022-10-09
2022-10-10 | Click Here |  | 6.61 | 5.09 | 5.12 | 5.31 | 5.33 | 6.7 | 7.47 | 1.52 | 1.74 | 1.97 | 1.95 | 27 | 22 | 24 | 5 | 2 | 0 | 0.662 | 0.611 | 1.52 | 0.316 | 0.663 | 0.448 | 7.2 | 15.2 | 13.6 | 13.8 | 17.1 | 12.5 | 29.3 | 22.7 | 24.3 | 29.7 | 3.07 | 3.26 | 2.9 | 5.7 | 0.167 | 15.3 | 15.2 | 1.2161 | 57.4 | 88.9 | 0.2412 | 0.0507 | 13.77 | 12.78 | 13.75 | 0.97 | 1.483 | 2.082 | 7.62 | 2.9961 | 23.78 | 1.8 | 4.5 | 2022-10-10
2022-10-11 | Click Here |  | 6.72 | 5.4 | 5.23 | 5.32 | 5.4 | 6.78 | 7.48 | 1.45 | 1.63 | 1.76 | 1.73 | 28 | 23 | 48 | 7 | 4 | 1 | 0.743 | 0.698 | 1.72 | 0.648 | 0.593 | 0.486 | 7.1 | 14.1 | 12.6 | 13.3 | 17 | 12.1 | 26.5 | 20.7 | 23.2 | 29.2 | 3.02 | 3.23 | 3 | 5.8 | 0.148 | 14 | 14.9 | 1.2735 | 71.3 | 89.6 | 0.1467 | 0.0475 | 15.46 | 12.54 | 13.52 | 0.98 | 1.483 | 2.082 | 7.62 | 3.0335 | 22.57 | 1.8 | 4.8 | 2022-10-11
2022-10-12 | Click Here |  | 6.98 | 5.19 | 5.27 | 5.2 | 5.47 | 7.55 | 7.65 | 1.6 | 1.77 | 1.64 | 1.59 | 24 | 16 | 39 | 7 | 3 | 0 | 0.789 | 0.734 | 0.964 | 0.563 | 0.841 | 0.539 | 7 | 12.3 | 11.9 | 12.5 | 17.1 | 12.1 | 12.2 | 18.7 | 21.5 | 29 | 2.97 | 3.18 | 3 | 6.1 | 0.066 | 15 | 14.5 | 0.72984 | 73 | 92.9 | 0.1365 | 0.032 | 16.4 | 13.72 | 14.66 | 0.94 | 1.483 | 2.082 | 7.62 | 2.6998 | 20.99 | 1.4 | 5 | 2022-10-12
2022-10-13 | Click Here |  | 6.54 | 5.36 | 5.2 | 5.21 | 5.36 | 7.69 | 7.68 | 1.7 | 1.75 | 2.12 | 1.82 | 22 | 16 | 26 | 6 | 0 | 0 | 0.656 | 0.675 | 1.86 | 0.507 | 0.53 | 0.515 | 6.9 | 12.5 | 11.7 | 12.5 | 16.2 | 11.8 | 23.2 | 18.5 | 21.5 | 27.6 | 2.91 | 3.14 | 2.9 | 5.9 | 0.038 | 14.6 | 14.8 | 1.0543 | 72.5 | 90.7 | 0.1395 | 0.0422 | 13.98 | 12.92 | 13.87 | 0.95 | 1.483 | 2.082 | 7.62 | 2.9443 | 21.63 | 1.4 | 5 | 2022-10-13
2022-10-14 | Click Here |  | 6.47 | 5.37 | 5.46 | 5.19 | 5.27 | 6.91 | 6.7 | 1.84 | 1.92 | 2.01 | 1.84 | 27 | 18 | 22 | 2 | 0 | 0 | 0.617 | 0.606 | 0.895 | 0.197 | 0.392 | 0.486 | 7.6 | 13.7 | 13.1 | 13.5 | 17.8 | 12.8 | 24.3 | 20.8 | 23.3 | 30.2 | 2.98 | 3.22 | 2.9 | 5.8 | 0.046 | 14.2 | 14.3 | 1.1883 | 73.1 | 91.9 | 0.1359 | 0.0378 | 14.45 | 13.37 | 14.36 | 0.99 | 1.483 | 2.082 | 7.62 | 3.0683 | 20.47 | 1.3 | 4.9 | 2022-10-14
2022-10-15 | Click Here |  | 6.37 | 5.41 | 5.39 | 5.37 | 5.41 | 7.1 | 7 | 1.79 | 1.94 | 2.01 | 1.96 | 27 | 19 | 15 | 0 | 0 | 0 | 0.541 | 0.574 | 0.744 | 0.126 | 0.299 | 0.347 | 7.7 | 13.9 | 13.2 | 13.9 | 18.6 | 13 | 24.8 | 21.1 | 23.9 | 32.4 | 2.89 | 3.15 | 2.7 | 5.9 | 0.031 | 14.2 | 14.4 | 1.2485 | 72.8 | 92.4 | 0.1399 | 0.0351 | 13.61 | 12.48 | 13.46 | 0.98 | 0 | 0 | 0 | 3.1285 | 21.24 | 1.3 | 4.9 | 2022-10-15
2022-10-16 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-10-16
2022-10-17 | Click Here |  | 6.55 | 5.38 | 5.4 | 5.26 | 5.43 | 7.43 | 6.93 | 1.71 | 1.8 | 2.3 | 1.92 | 24 | 16 | 30 | 23 | 5 | 0 | 0.676 | 0.562 | 1.19 | 1.02 | 0.547 | 0.273 | 7.4 | 13.4 | 13.3 | 13.2 | 17.7 | 12.6 | 24.6 | 21.1 | 21.3 | 30 | 2.91 | 3.14 | 3.1 | 6 | 0.05 | 14.2 | 14.5 | 1.1245 | 73.2 | 91.6 | 0.1354 | 0.0378 | 13.92 | 12.94 | 13.89 | 0.95 | 1.483 | 2.082 | 7.62 | 3.0945 | 19.96 | 1.3 | 3.9 | 2022-10-17
2022-10-18 | Click Here |  | 6.77 | 5.31 | 5.27 | 5.28 | 5.32 | 7.27 | 7.38 | 1.73 | 1.87 | 2.03 | 1.95 | 26 | 17 | 27 | 8 | 0 | 0 | 0.59 | 0.586 | 1.67 | 0.485 | 0.346 | 0.282 | 7.2 | 12.9 | 12.7 | 12.8 | 17.1 | 12.6 | 24.2 | 20.4 | 20.9 | 28.7 | 2.98 | 3.45 | 3 | 5.9 | 0.028 | 15.3 | 14.1 | 1.0844 | 72.9 | 90.9 | 0.1372 | 0.0413 | 13.07 | 12.05 | 13.01 | 0.96 | 1.483 | 2.082 | 7.62 | 3.0744 | 18.53 | 1.2 | 4.9 | 2022-10-18
2022-10-19 | Click Here |  | 6.27 | 5.3 | 5.13 | 5.23 | 5.39 | 7.41 | 7.32 | 1.53 | 1.63 | 1.91 | 1.7 | 29 | 21 | 24 | 6 | 0 | 0 | 0.694 | 0.694 | 2.33 | 0.518 | 0.81 | 0.659 | 7.9 | 16.3 | 14.4 | 13.9 | 18.1 | 13.6 | 29.9 | 23.4 | 22.9 | 30.6 | 3.11 | 3.32 | 3 | 6.1 | 0.06 | 14.5 | 14.4 | 1.4005 | 54.3 | 84 | 0.2651 | 0.0757 | 13.77 | 12.63 | 13.59 | 0.96 | 1.483 | 2.082 | 7.62 | 3.1705 | 19.66 | 1.2 | 4.9 | 2022-10-19
2022-10-20 | Click Here |  | 6.01 | 5.14 | 5.01 | 4.87 | 5.09 | 7.34 | 7.05 | 1.46 | 1.58 | 1.7 | 1.63 | 55 | 40 | 68 | 10 | 3 | 0 | 0.743 | 0.729 | 2.78 | 0.619 | 1.19 | 0.828 | 8.5 | 17.5 | 17.5 | 16.2 | 19.5 | 14.6 | 32.4 | 28.8 | 26.9 | 32.8 | 2.87 | 3.36 | 2.9 | 5.8 | 0.114 | 15 | 14.2 | 1.5106 | 48.4 | 79.1 | 0.3151 | 0.1016 | 13.88 | 12.75 | 13.73 | 0.98 | 1.483 | 2.082 | 7.62 | 3.1406 | 27.84 | 1.2 | 4.9 | 2022-10-20
2022-10-21 | Click Here |  | 6.72 | 4.89 | 5.17 | 5.07 | 5.07 | 6.14 | 7.11 | 1.33 | 1.55 | 1.68 | 1.61 | 54 | 46 | 36 | 9 | 9 | 4 | 0.703 | 0.698 | 1.94 | 0.32 | 0.982 | 0.812 | 7.9 | 14.3 | 17.2 | 16.4 | 19.1 | 13.6 | 26.4 | 28.5 | 27.5 | 32.3 | 2.91 | 3.32 | 3 | 5.7 | 0.179 | 14.7 | 14.2 | 1.9352 | 53.1 | 78.8 | 0.2743 | 0.1034 | 13.38 | 12.29 | 13.25 | 0.96 | 1.483 | 2.082 | 7.62 | 3.6652 | 26.53 | 1.2 | 4.9 | 2022-10-21
2022-10-22 | Click Here |  | 6.38 | 5.13 | 5.29 | 5.14 | 4.75 | 6.33 | 7.32 | 1.89 | 1.93 | 1.99 | 1.96 | 31 | 26 | 19 | 3 | 1 | 0 | 0.63 | 0.631 | 0.783 | 0.148 | 0.418 | 0.399 | 7.6 | 19 | 17.9 | 17.4 | 17.6 | 12.7 | 34.1 | 28.9 | 28.8 | 29 | 2.95 | 3.36 | 2.9 | 5.7 | 0.083 | 13.4 | 13.5 | 1.5341 | 53.4 | 86.6 | 0.2746 | 0.0625 | 13.44 | 12.57 | 13.48 | 0.91 | 1.483 | 2.082 | 7.62 | 3.5041 | 28.3 | 2.4 | 5.8 | 2022-10-22
2022-10-23 | Click Here |  | 0 | 5.32 | 0 | 0 | 0 | 6.56 | 0 | 1.8 | 1.91 | 2.09 | 2.06 | 0 | 0 | 10 | 0 | 2 | 0 | 0 | 0 | 0.817 | 0.101 | 0.0573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0.01 | 0 | 0 | 1.4544 | 0 | 89.4 | 0 | 0.0485 | 13.49 | 12.47 | 13.45 | 0.98 | 1.393 | 2.082 | 7.498 | 3.4744 | 0 | 3.6 | 7.5 | 2022-10-23
2022-10-24 | Click Here |  | 6.24 | 5.51 | 5.33 | 5.29 | 5.71 | 7.73 | 7.26 | 1.65 | 1.84 | 1.89 | 1.93 | 48 | 39 | 24 | 5 | 3 | 0 | 0.725 | 0.629 | 1.22 | 0.179 | 0.844 | 0.619 | 7.7 | 21.5 | 18.1 | 17.9 | 23.9 | 12.7 | 37.1 | 28.8 | 29.4 | 39.7 | 3.01 | 3.31 | 2.9 | 5.9 | 0.025 | 13.2 | 13.8 | 1.5623 | 58.1 | 88.7 | 0.2356 | 0.0517 | 16.39 | 15.56 | 16.55 | 0.99 | 1.407 | 2.082 | 8.492 | 3.4523 | 28.1 | 3.6 | 7.5 | 2022-10-24
2022-10-25 | Click Here |  | 5.91 | 5.03 | 5.27 | 4.94 | 4.92 | 6.94 | 7.72 | 1.59 | 1.61 | 1.84 | 1.79 | 51 | 44 | 29 | 8 | 2 | 0 | 0.819 | 0.672 | 2.23 | 0.394 | 0.914 | 0.51 | 8.1 | 18.8 | 18.6 | 18.4 | 26.7 | 13.3 | 33.7 | 29.5 | 30.1 | 44.2 | 2.96 | 3.25 | 2.8 | 5.8 | 0.095 | 13 | 13.6 | 1.6373 | 54.6 | 85.7 | 0.2624 | 0.0641 | 18.33 | 17.68 | 18.63 | 0.95 | 1.433 | 2.082 | 8.581 | 3.3973 | 28.64 | 3.5 | 7.5 | 2022-10-25
2022-10-26 | Click Here |  | 6.47 | 5.15 | 5.33 | 4.86 | 4.88 | 6.73 | 7.59 | 1.57 | 1.6 | 1.83 | 1.8 | 46 | 40 | 27 | 9 | 7 | 2 | 0.728 | 0.615 | 1.73 | 0.59 | 0.903 | 0.407 | 7.5 | 18.7 | 19 | 18.9 | 21.3 | 12.7 | 34.1 | 30.7 | 30.9 | 39.4 | 2.93 | 3.22 | 2.9 | 5.7 | 0.127 | 13.9 | 13.6 | 1.8451 | 54.9 | 86.4 | 0.2621 | 0.0633 | 17.98 | 16.55 | 18.46 | 1.91 | 1.433 | 2.082 | 8.581 | 3.7351 | 27.14 | 3.7 | 7.5 | 2022-10-26
2022-10-27 | Click Here |  | 7.1 | 5.35 | 5.39 | 5.32 | 5.34 | 6.84 | 7.69 | 1.63 | 1.74 | 1.87 | 1.83 | 33 | 25 | 19 | 3 | 0 | 0 | 0.717 | 0.613 | 1.17 | 0.264 | 0.399 | 0.358 | 8 | 18.9 | 18.8 | 18.8 | 19.9 | 13.6 | 33.7 | 30.8 | 31.6 | 34.3 | 2.97 | 3.18 | 2.9 | 5.8 | 0.084 | 14.5 | 14.6 | 1.6794 | 54.7 | 86.3 | 0.2623 | 0.064 | 18.5 | 17.8 | 18.78 | 0.98 | 1.396 | 2.082 | 7.701 | 3.5994 | 29.26 | 4.2 | 7.5 | 2022-10-27
2022-10-28 | Click Here |  | 6.54 | 5.37 | 5.29 | 5.36 | 5.37 | 6.99 | 7.6 | 2.2 | 2.43 | 2.53 | 2.08 | 41 | 32 | 36 | 9 | 1 | 0 | 0.787 | 0.636 | 2.62 | 0.405 | 0.442 | 0.311 | 7.5 | 18.1 | 17.9 | 18.1 | 23.9 | 12.8 | 33.1 | 29.5 | 30.7 | 40.6 | 2.99 | 3.39 | 3.1 | 6 | 0.082 | 14.7 | 14.6 | 0.85309 | 58.7 | 88.8 | 0.231 | 0.0514 | 16.05 | 15.15 | 16.11 | 0.96 | 1.423 | 2.082 | 8.013 | 2.6431 | 29.01 | 4.2 | 7.5 | 2022-10-28
2022-10-29 | Click Here |  | 6.6 | 5.27 | 5.34 | 5.14 | 5.3 | 6.69 | 7.6 | 1.88 | 2 | 2.38 | 2.34 | 44 | 35 | 35 | 8 | 8 | 0 | 0.613 | 0.599 | 1.67 | 0.27 | 1.02 | 0.509 | 7.7 | 18.9 | 19.2 | 18.6 | 24.3 | 12.9 | 34.7 | 30.2 | 30.7 | 40.6 | 2.95 | 3.52 | 2.9 | 5.9 | 0.065 | 13.6 | 14 | 1.518 | 59.6 | 89.1 | 0.2247 | 0.0498 | 14.66 | 13.71 | 14.71 | 1 | 1.366 | 2.082 | 7.13 | 3.578 | 29.47 | 4.2 | 7.7 | 2022-10-29
2022-10-30 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-10-30
2022-10-31 | Click Here |  | 7.68 | 5.28 | 5.3 | 5.31 | 5.38 | 6.13 | 6.24 | 1.87 | 2.09 | 2.2 | 2.26 | 40 | 38 | 20 | 0 | 0 | 0 | 0.685 | 0.655 | 1.48 | 0.161 | 0.747 | 0.654 | 7.9 | 18.9 | 19 | 18.2 | 22.4 | 12.7 | 34.3 | 29.1 | 29.2 | 36.4 | 2.93 | 3.47 | 2.9 | 5.7 | 0.072 | 12 | 13 | 1.4314 | 59.8 | 86.4 | 0.2246 | 0.0631 | 14.78 | 13.86 | 14.84 | 0.98 | 1.422 | 2.566 | 0.98 | 3.6114 | 29.33 | 4.3 | 7.9 | 2022-10-31
2022-11-01 | Click Here |  | 7.14 | 5.3 | 5.26 | 5.28 | 5.32 | 6.19 | 6.5 | 1.85 | 1.92 | 2.14 | 2.11 | 43 | 37 | 21 | 0 | 0 | 0 | 0.937 | 0.733 | 0.986 | 0.162 | 0.794 | 0.781 | 8 | 18.9 | 18.9 | 18.3 | 22.7 | 12.7 | 33.1 | 28.6 | 29.4 | 36.8 | 2.97 | 3.26 | 2.9 | 5.7 | 0.059 | 11.7 | 12.8 | 1.5365 | 59.5 | 88.6 | 0.2248 | 0.0516 | 15.45 | 14.56 | 15.52 | 0.96 | 1.281 | 2.207 | 7.804 | 3.5765 | 29.06 | 3.5 | 8.1 | 2022-11-01
2022-11-02 | Click Here |  | 6.49 | 5.21 | 5.29 | 5.26 | 5.3 | 6.81 | 7.18 | 1.68 | 1.81 | 2.38 | 2.05 | 45 | 36 | 39 | 13 | 11 | 0 | 0.683 | 0.718 | 2.08 | 0.603 | 1.2 | 1.055 | 7.8 | 18.8 | 18.9 | 18.7 | 24.1 | 12.5 | 33.7 | 28.3 | 29.8 | 39.3 | 3 | 3.23 | 2.9 | 5.9 | 0.046 | 12.2 | 13.1 | 1.4407 | 58.2 | 87 | 0.2346 | 0.0602 | 12.18 | 11.12 | 12.07 | 0.95 | 1.281 | 2.207 | 7.804 | 3.5107 | 29.55 | 3.4 | 9.2 | 2022-11-02
2022-11-03 | Click Here |  | 6.19 | 5.08 | 5.27 | 5.07 | 5.1 | 6.87 | 6.59 | 1.74 | 1.88 | 2.32 | 2.04 | 45 | 36 | 49 | 9 | 10 | 0 | 0.667 | 0.722 | 2.26 | 0.672 | 0.683 | 0.648 | 7.8 | 18.3 | 18.3 | 18.3 | 23.4 | 12.4 | 32.2 | 26.9 | 29 | 37.9 | 2.96 | 2.99 | 3 | 6 | 0.033 | 11.8 | 12.7 | 1.5403 | 59 | 88.4 | 0.2285 | 0.0533 | 13.13 | 12.1 | 13.04 | 0.94 | 1.281 | 2.207 | 7.804 | 3.6403 | 27.52 | 3.4 | 9.4 | 2022-11-03
2022-11-04 | Click Here |  | 6.14 | 6.07 | 6.07 | 6 | 5.34 | 5.16 | 6.03 | 2.11 | 2.24 | 2.2 | 2.1 | 44 | 34 | 41 | 5 | 8 | 0 | 0.747 | 0.606 | 3.71 | 0.602 | 0.584 | 0.734 | 7.6 | 20.2 | 18.3 | 18.6 | 17.3 | 11.7 | 34.1 | 26.6 | 29.1 | 27.7 | 2.97 | 3.09 | 3 | 5.7 | 0.187 | 10.4 | 12.1 | 1.7419 | 62.7 | 86.5 | 0.2021 | 0.0629 | 14.1 | 12.31 | 14.2 | 1.89 | 1.281 | 2.207 | 7.804 | 3.8319 | 26.87 | 3.5 | 9.4 | 2022-11-04
2022-11-05 | Click Here |  | 6.49 | 5.26 | 5.27 | 5.37 | 5.45 | 7.15 | 7.24 | 1.98 | 2.04 | 2.16 | 2.08 | 45 | 37 | 37 | 1 | 4 | 0 | 0.647 | 0.596 | 1.96 | 0.214 | 0.541 | 0.594 | 7.8 | 18 | 17.4 | 17.5 | 23.3 | 12.1 | 31.2 | 25.6 | 27.4 | 37.2 | 2.92 | 3.13 | 3 | 5.9 | 0.009 | 10.9 | 12 | 1.2386 | 64.9 | 88.5 | 0.1877 | 0.0529 | 12.2 | 12.03 | 12.03 | 0 | 0 | 0 | 0 | 3.3286 | 28.67 | 3.3 | 9.4 | 2022-11-05
2022-11-06 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-11-06
2022-11-07 | Click Here |  | 6.35 | 5.28 | 5.22 | 5.33 | 5.35 | 6.91 | 7.22 | 1.97 | 2.05 | 2.52 | 2.07 | 41 | 32 | 40 | 10 | 9 | 0 | 0.597 | 0.635 | 1.76 | 0.976 | 1.14 | 0.934 | 7.6 | 17.2 | 17.2 | 17.5 | 22.6 | 12.1 | 31.1 | 26 | 28 | 35.9 | 2.87 | 3.11 | 3.1 | 6 | 0.047 | 11.8 | 11.9 | 1.4527 | 58.9 | 86.1 | 0.2297 | 0.0646 | 13.17 | 12.26 | 13.19 | 0.93 | 1.281 | 2.207 | 7.804 | 3.5927 | 26.41 | 3.3 | 9 | 2022-11-07
2022-11-08 | Click Here |  | 6.57 | 5.52 | 5.42 | 5.64 | 5.62 | 7.11 | 7.01 | 1.93 | 2.03 | 2.38 | 2.05 | 44 | 35 | 62 | 14 | 14 | 2 | 0.742 | 0.724 | 3.65 | 0.834 | 0.592 | 0.682 | 7.8 | 16.8 | 17 | 17.1 | 23 | 12.5 | 30.3 | 25.9 | 27.7 | 36.8 | 2.9 | 3.25 | 2.9 | 6 | 0.05 | 11.7 | 12.2 | 1.5773 | 60.3 | 88.2 | 0.2197 | 0.0544 | 15.15 | 12.03 | 12.97 | 0.94 | 1.284 | 2.207 | 7.804 | 3.6573 | 26.28 | 3.3 | 9.2 | 2022-11-08
2022-11-09 | Click Here |  | 6.65 | 5.54 | 5.42 | 5.66 | 5.71 | 7.01 | 6.98 | 1.71 | 1.82 | 2.04 | 2.09 | 42 | 33 | 49 | 5 | 3 | 0 | 0.958 | 0.897 | 1.39 | 0.442 | 0.823 | 0.814 | 7.7 | 18.6 | 18.7 | 18.1 | 23 | 12.6 | 34.1 | 37.5 | 27 | 36.8 | 2.95 | 3.19 | 2.9 | 6 | 0.199 | 12.8 | 12.2 | 1.5396 | 60.9 | 86.9 | 0.2151 | 0.0609 | 17.12 | 13.6 | 14.57 | 0.97 | 1.281 | 2.207 | 7.804 | 3.6096 | 30.72 | 3 | 9.2 | 2022-11-09
2022-11-10 | Click Here |  | 6.74 | 5.49 | 5.42 | 5.46 | 5.54 | 6.59 | 6.56 | 1.71 | 1.9 | 2.12 | 2.16 | 47 | 39 | 11 | 1 | 7 | 0 | 0.789 | 0.668 | 0.646 | 0.174 | 1.14 | 1.287 | 7.6 | 18.1 | 18.4 | 17.4 | 23.9 | 11.8 | 32.5 | 26 | 26.1 | 37.8 | 2.97 | 3.24 | 2.8 | 6.1 | 0.189 | 10.8 | 11.7 | 1.3873 | 63.7 | 88.2 | 0.1957 | 0.0542 | 12.92 | 11.92 | 12.89 | 0.97 | 1.281 | 2.207 | 7.804 | 3.5273 | 29.81 | 2.8 | 9.4 | 2022-11-10
2022-11-11 | Click Here |  | 6.46 | 5.55 | 5.26 | 5.72 | 5.75 | 6.54 | 6.53 | 2.05 | 2.18 | 2.17 | 2.19 | 52 | 46 | 10 | 1 | 2 | 0 | 0.763 | 0.607 | 0.67 | 0.11 | 0.71 | 0.664 | 7.6 | 20.8 | 17.8 | 17.7 | 23.3 | 11.9 | 34.4 | 25.4 | 25.2 | 36.4 | 3 | 3.27 | 2.9 | 5.7 | 0.018 | 10.8 | 11.2 | 1.3336 | 63.9 | 86.8 | 0.1955 | 0.0612 | 11.97 | 10.92 | 11.87 | 0.95 | 1.281 | 2.207 | 7.804 | 3.4836 | 27.47 | 2.8 | 8.5 | 2022-11-11
2022-11-12 | Click Here |  | 7.04 | 5.19 | 5.4 | 5.31 | 5.37 | 6.47 | 6.56 | 2.07 | 2.18 | 2.19 | 2.11 | 39 | 33 | 15 | 1 | 3 | 0 | 0.698 | 0.624 | 0.874 | 0.144 | 0.619 | 0.574 | 7.8 | 19.4 | 18.1 | 18 | 23.9 | 12 | 33.3 | 25.8 | 25.7 | 36.4 | 3.03 | 3.24 | 2.8 | 5.7 | 0.026 | 10.2 | 10.2 | 1.4318 | 63.6 | 86.6 | 0.1958 | 0.0621 | 12.35 | 11.37 | 12.32 | 0.95 | 0 | 0 | 0 | 3.5218 | 29.31 | 3.2 | 8.8 | 2022-11-12
2022-11-13 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-11-13
2022-11-14 | Click Here |  | 6.55 | 5.15 | 5.11 | 5.29 | 5.34 | 6.88 | 6.8 | 2.02 | 2.17 | 2.97 | 2.23 | 41 | 32 | 13 | 2 | 0 | 0 | 0.74 | 0.688 | 1.05 | 0.321 | 1.12 | 0.94 | 7.6 | 18.7 | 18.2 | 18 | 23.8 | 11.3 | 32.1 | 24.6 | 24.4 | 36.2 | 2.94 | 3.12 | 3.1 | 6 | 0.042 | 9 | 10.2 | 1.4286 | 76.7 | 86 | 0.1155 | 0.0653 | 13.56 | 12.59 | 13.53 | 0.94 | 1.528 | 2.019 | 7.707 | 3.4986 | 27.51 | 3.4 | 9.1 | 2022-11-14
2022-11-15 | Click Here |  | 6.52 | 5.19 | 5.14 | 5.35 | 5.38 | 6.81 | 6.84 | 1.77 | 2.12 | 2.16 | 2 | 42 | 33 | 33 | 8 | 11 | 0 | 0.851 | 0.652 | 1.55 | 0.531 | 1.46 | 1.137 | 7.6 | 18.3 | 18.2 | 18.2 | 23.7 | 11.1 | 31.9 | 24.5 | 24.5 | 36 | 3.05 | 3.1 | 3 | 6.1 | 0.189 | 8.4 | 10.2 | 1.0498 | 60 | 86.7 | 0.2218 | 0.0618 | 14.62 | 13.52 | 14.52 | 1 | 1.528 | 2.019 | 7.707 | 3.1098 | 29.62 | 3.5 | 9.3 | 2022-11-15
2022-11-16 | Click Here |  | 6.97 | 5.31 | 5.33 | 5.42 | 5.45 | 6.8 | 7.11 | 1.81 | 2.09 | 2.16 | 2.09 | 39 | 33 | 15 | 2 | 3 | 0 | 0.723 | 0.66 | 1.22 | 0.196 | 0.817 | 0.782 | 7.6 | 19 | 17.6 | 17.9 | 25.1 | 11.2 | 33.5 | 23.9 | 24.2 | 37.3 | 3.02 | 3.09 | 2.9 | 5.9 | 0.032 | 8.3 | 9.3 | 1.3344 | 59.8 | 86.5 | 0.222 | 0.063 | 14.24 | 13.31 | 14.23 | 0.92 | 1.528 | 2.019 | 7.707 | 3.3844 | 28.86 | 4.2 | 9.3 | 2022-11-16
2022-11-17 | Click Here |  | 7.12 | 5.25 | 5.36 | 5.42 | 5.53 | 6.63 | 6.7 | 1.61 | 1.94 | 2.09 | 2 | 42 | 34 | 19 | 3 | 4 | 0 | 0.825 | 0.698 | 1.42 | 0.206 | 0.603 | 0.551 | 7.7 | 18.2 | 17.8 | 17.7 | 24.3 | 11.3 | 30.6 | 23 | 23.3 | 35.9 | 3.06 | 3.12 | 2.9 | 5.8 | 0.026 | 8.2 | 9.1 | 1.3445 | 60.1 | 85.7 | 0.2219 | 0.067 | 14.25 | 13.37 | 14.28 | 0.91 | 1.528 | 2.019 | 7.707 | 3.2945 | 29.59 | 3.8 | 9.3 | 2022-11-17
2022-11-18 | Click Here |  | 6.83 | 5.37 | 5.38 | 5.46 | 5.49 | 7.02 | 7.05 | 1.81 | 1.91 | 2.1 | 1.94 | 41 | 30 | 25 | 3 | 7 | 0 | 0.626 | 0.459 | 0.896 | 0.311 | 1.53 | 0.629 | 7.5 | 19.7 | 19.8 | 19.8 | 25.9 | 10.8 | 32.4 | 25.4 | 26 | 38.6 | 3.04 | 3.19 | 3 | 5.9 | 0.01 | 7.6 | 9.3 | 1.0936 | 59.4 | 90.3 | 0.2266 | 0.0448 | 13.45 | 12.42 | 13.37 | 0.95 | 1.528 | 2.019 | 7.707 | 3.1436 | 34.18 | 5.4 | 9.3 | 2022-11-18
2022-11-19 | Click Here |  | 6.4 | 5.29 | 5.34 | 5.43 | 5.46 | 6.94 | 6.47 | 1.86 | 2.08 | 2.03 | 2.15 | 44 | 34 | 26 | 7 | 11 | 0 | 0.92 | 0.538 | 1.28 | 0.154 | 1.59 | 0.582 | 7.4 | 20.5 | 20 | 19.8 | 24.6 | 10.7 | 33.8 | 25 | 24.6 | 36.5 | 2.97 | 3.35 | 3.1 | 6 | 0.02 | 7.9 | 9.2 | 1.0971 | 62.4 | 90.4 | 0.2048 | 0.0435 | 13.71 | 12.68 | 13.66 | 0.98 | 1.528 | 2.019 | 7.707 | 3.2371 | 33.3 | 5.5 | 9.3 | 2022-11-19
2022-11-20 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 14.32 | 13.52 | 14.39 | 0.87 | 1.528 | 2.019 | 7.707 |  | 0 | 0 | 0 | 2022-11-20
2022-11-21 | Click Here |  | 7.08 | 5.58 | 5.56 | 5.55 | 5.62 | 6.74 | 7.3 | 1.78 | 2.02 | 2.14 | 2.07 | 41 | 34 | 17 | 2 | 4 | 0 | 0.846 | 0.643 | 1.58 | 0.201 | 0.796 | 0.639 | 7.8 | 21.8 | 20.3 | 20.5 | 26.6 | 11.2 | 34 | 25.4 | 26.2 | 38.1 | 3 | 3.27 | 2.9 | 5.9 | 0.015 | 7.4 | 7.9 | 1.059 | 62.7 | 90.4 | 0.2045 | 0.0436 | 13.65 | 12.7 | 13.65 | 0.95 | 1.528 | 2.019 | 7.707 | 3.149 | 33.96 | 6.2 | 9.5 | 2022-11-21
2022-11-22 | Click Here |  | 7.18 | 5.42 | 5.41 | 5.51 | 5.56 | 6.84 | 7.15 | 1.78 | 2.07 | 2.11 | 2.04 | 41 | 36 | 12 | 0 | 0 | 0 | 0.696 | 0.44 | 1.21 | 0.163 | 0.582 | 0.714 | 7.5 | 21 | 20.3 | 20.3 | 27.7 | 10.8 | 33.7 | 25.4 | 26.2 | 39.2 | 3.03 | 3.31 | 3 | 5.9 | 0.017 | 7.8 | 7.6 | 1.6183 | 61.5 | 88.6 | 0.2108 | 0.0523 | 13.69 | 12.73 | 13.65 | 0.92 | 1.915 | 2.333 | 8.318 | 2.9883 | 33.78 | 6.2 | 9.8 | 2022-11-22
2022-11-23 | Click Here |  | 6.22 | 5.48 | 5.42 | 5.61 | 5.57 | 7.3 | 7.01 | 1.58 | 1.78 | 1.74 | 0 | 42 | 33 | 41 | 0 | 12 | 0 | 0.6 | 0.446 | 2.53 | 0.307 | 1.252 | 0.661 | 7.6 | 18.5 | 19.2 | 18.9 | 26.5 | 11.4 | 29.6 | 24.2 | 24.2 | 38.3 | 3.01 | 3.31 | 3.1 | 5.9 | 0.044 | 7.7 | 8.2 |  | 60.4 | 90.1 | 0.2186 | 0.0452 | 15.45 | 12.74 | 13.63 | 0.95 | 1.898 | 2.86 | 8.314 | 2.6716 | 33.62 | 6 | 10 | 2022-11-23
2022-11-24 | Click Here |  | 6.41 | 5.37 | 5.36 | 5.51 | 5.52 | 7.25 | 7.25 | 1.5 | 1.75 | 2.1 | 0 | 44 | 30 | 50 | 7 | 8 | 0 | 0.533 | 0.498 | 1.35 | 0.129 | 1.278 | 0.534 | 7.8 | 20.5 | 20.3 | 20.2 | 27.1 | 11.5 | 33.4 | 25.6 | 26.1 | 39.2 | 3.08 | 3.24 | 3 | 6 | 0.051 | 8 | 8.4 |  | 60.5 | 89.6 | 0.2182 | 0.0474 | 15.29 | 12.84 | 13.78 | 0.94 | 1.825 | 2.371 | 8.672 | 2.8845 | 34.11 | 6 | 10 | 2022-11-24
2022-11-25 | Click Here |  | 6.58 | 5.41 | 5.36 | 5.54 | 5.61 | 7.18 | 7.26 | 1.78 | 1.86 | 2.09 | 0 | 22 | 14 | 6 | 0 | 0 | 0 | 0.93 | 0.418 | 0.77 | 0.144 | 0.607 | 0.557 | 7.8 | 20.9 | 20.4 | 20.1 | 26.1 | 11 | 24.3 | 25.7 | 26.1 | 38.2 | 3.1 | 3.17 | 2.9 | 6 | 0.017 | 7 | 8.8 | 2.1257 | 62.34 | 89.4 | 0.2044 | 0.0484 | 13.46 | 12.46 | 13.4 | 0.94 | 1.793 | 2.362 | 7.801 | 2.7557 | 34.69 | 6.1 | 10 | 2022-11-25
2022-11-26 | Click Here |  | 6.49 | 5.36 | 5.32 | 5.49 | 5.56 | 7.41 | 7.225 | 1.91 | 2.14 | 2.12 | 2.17 | 24 | 16 | 9 | 0 | 0 | 0 | 0.799 | 0.409 | 0.779 | 0.121 | 0.547 | 0.61 | 8.1 | 21.69 | 20.6 | 20.3 | 27 | 11.3 | 34 | 26.3 | 26.5 | 39 | 3.16 | 3.3 | 3 | 6.1 | 0.008 | 6.8 | 8.3 | 0.47675 | 63.2 | 90.2 | 0.199 | 0.0446 | 13.47 | 13.34 | 13.34 | 0 | 0 | 0 | 0 | 2.7768 | 34.54 | 6.1 | 10 | 2022-11-26
2022-11-27 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-11-27
2022-11-28 | Click Here |  | 6.49 | 5.38 | 5.29 | 5.49 | 5.53 | 7.05 | 7.02 | 1.78 | 1.91 | 2.03 | 2.2 | 36 | 27 | 26 | 2 | 8 | 0 | 0.826 | 0.395 | 0.658 | 0.28 | 0.454 | 0.514 | 8.22 | 20 | 20.7 | 20.7 | 27.2 | 12 | 33.8 | 26.5 | 27 | 38.7 | 3.11 | 3.17 | 3.1 | 5.8 | 0.016 | 8.6 | 7.8 | 0.4424 | 61.2 | 90.1 | 0.213 | 0.045 | 14.11 | 13.11 | 14.08 | 0.97 | 2.039 | 2.442 | 8.95 | 2.6724 | 34.59 | 6.1 | 10 | 2022-11-28
2022-11-29 | Click Here |  | 6.44 | 5.44 | 5.41 | 5.55 | 5.57 | 7.04 | 7.11 | 1.73 | 1.89 | 2.08 | 2.1 | 45 | 33 | 31 | 4 | 7 | 0 | 0.914 | 0.39 | 1.21 | 0.25 | 0.709 | 0.553 | 8.1 | 20.1 | 20.3 | 20.1 | 26.5 | 11.6 | 34.4 | 26.1 | 26.3 | 38.5 | 3.03 | 3.12 | 3.1 | 6 | 0.047 | 7.6 | 8.4 | 0.71539 | 57.3 | 89.1 | 0.2415 | 0.0495 | 13.54 | 12.49 | 13.42 | 0.93 | 2.039 | 2.442 | 8.95 | 2.8854 | 32.96 | 6.1 | 10 | 2022-11-29
2022-11-30 | Click Here |  | 6.74 | 5.36 | 0 | 5.44 | 5.47 | 7.14 | 0 | 1.58 | 1.71 | 2.09 | 2.14 | 40 | 31 | 12 | 0 | 2 | 0 | 0.84 | 0.361 | 1.12 | 0.265 | 0.885 | 0.841 | 8.5 | 20.8 | 21 | 20.6 | 28.6 | 11.9 | 35.6 | 27 | 27.1 | 40.5 | 3.01 | 3.13 | 3 | 5.9 | 0.18 | 6.5 | 5.9 | 0.76599 | 58.7 | 89.8 | 0.2312 | 0.0467 | 13.59 | 12.64 | 13.61 | 0.97 | 1.448 | 2.436 | 8.831 | 2.886 | 33.68 | 6.1 | 10 | 2022-11-30
2022-12-01 | Click Here |  | 6.57 | 5.29 | 5.2 | 5.37 | 5.51 | 7.04 | 6.88 | 1.6 | 1.77 | 1.97 | 2 | 38 | 30 | 14 | 0 | 1 | 0 | 0.792 | 0.327 | 1.09 | 0.174 | 0.591 | 0.672 | 8.6 | 21.2 | 21.4 | 20.9 | 29.9 | 12.1 | 36.7 | 27.9 | 27.6 | 41.7 | 2.99 | 3.1 | 2.9 | 5.8 | 0.107 | 6.4 | 7.6 | 0.73018 | 59.9 | 90.1 | 0.2196 | 0.045 | 14.3 | 13.37 | 14.35 | 0.98 | 1.448 | 2.436 | 8.831 | 2.7702 | 33.65 | 6.1 | 10 | 2022-12-01
2022-12-02 | Click Here |  | 7.11 | 5.52 | 5.36 | 5.45 | 5.5 | 6.71 | 6.96 | 1.6 | 1.85 | 2.09 | 2.06 | 46 | 39 | 15 | 3 | 2 | 0 | 1.1 | 0.796 | 1.15 | 0.114 | 0.634 | 0.407 | 8.2 | 21.4 | 20.4 | 20.6 | 28.3 | 11.8 | 33.8 | 26.8 | 27.1 | 39.2 | 2.96 | 3.08 | 2.9 | 5.8 | 0.016 | 7.7 | 6.8 | 0.67916 | 60 | 89.1 | 0.2213 | 0.0501 | 13.6 | 12.61 | 13.57 | 0.96 | ? | ? | ? | 2.6992 | 33.45 | 6.3 | 10 | 2022-12-02
2022-12-03 | Click Here |  | 7.03 | 5.48 | 5.32 | 5.45 | 5.48 | 6.86 | 6.97 | 1.64 | 1.9 | 2.14 | 2.11 | 40 | 35 | 13 | 0 | 0 | 0 | 0.741 | 0.593 | 1.06 | 0.103 | 0.497 | 0.401 | 8.1 | 21.4 | 20.2 | 20.4 | 28.1 | 11.5 | 34.9 | 26.9 | 27 | 38.7 | 2.995 | 3.13 | 2.9 | 5.9 | 0.024 | 7.4 | 6.8 | 0.81257 | 60.3 | 88.9 | 0.221 | 0.0511 | 13.89 | 13.04 | 13.99 | 0.95 | 0 | 0 | 0 | 2.8626 | 33.6 | 6.3 | 10.2 | 2022-12-03
2022-12-04 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.8874 | 0 | 0 | 0 | 0 | 13.69 | 12.73 | 13.65 | 0.92 | 0 | 0 | 0 | 2.8474 | 0 | 6.2 | 10.2 | 2022-12-04
2022-12-05 | Click Here |  | 6.52 | 5.39 | 5.33 | 5.44 | 5.47 | 7.04 | 6.9 | 1.47 | 1.69 | 1.88 | 1.93 | 39 | 33 | 11 | 0 | 2 | 0 | 0.689 | 0.309 | 0.864 | 0.219 | 0.964 | 1.22 | 8.1 | 21.7 | 20.2 | 19.8 | 31.6 | 11.8 | 35.5 | 27.1 | 27.2 | 46.5 | 3.07 | 3.13 | 2.9 | 6 | 0.013 | 8.1 | 9 | 0.94499 | 60.7 | 89 | 0.2162 | 0.0504 | 14.45 | 13.53 | 14.53 | 1 | 0 | 0 | 0 | 2.925 | 33.78 | 6.2 | 10.2 | 2022-12-05
2022-12-06 | Click Here |  | 6.49 | 5.24 | 5.3 | 5.46 | 5.54 | 7.2 | 7.16 | 1.47 | 1.54 | 1.99 | 2.04 | 33 | 24 | 14 | 1 | 3 | 0 | 0.647 | 0.323 | 1.01 | 0.307 | 0.81 | 0.855 | 8.1 | 21.4 | 20.7 | 20.8 | 31.3 | 11.6 | 35.7 | 27.2 | 27.6 | 43.9 | 2.98 | 3.09 | 3 | 5.9 | 0.029 | 7.4 | 7.2 | 0.76647 | 63.3 | 89.2 | 0.1986 | 0.0494 | 13.52 | 12.53 | 13.5 | 0.97 | 0 | 0 | 0 | 2.7965 | 34.3 | 6.2 | 10.2 | 2022-12-06
2022-12-07 | Click Here |  | 6.93 | 5.36 | 5.25 | 5.5 | 5.6 | 6.7 | 6.98 | 1.61 | 1.72 | 2.08 | 2.06 | 54 | 47 | 13 | 1 | 2 | 0 | 0.829 | 0.32 | 1.12 | 0.126 | 0.514 | 0.637 | 8.1 | 20.3 | 20.2 | 19.7 | 30.5 | 11.6 | 34.9 | 26.8 | 26.3 | 41.4 | 2.94 | 3.05 | 2.9 | 5.8 | 0.011 | 7.8 | 6 | 0.97327 | 63.6 | 88.7 | 0.1983 | 0.0517 | 14.42 | 13.5 | 14.49 | 0.99 | 0 | 0 | 0 | 2.9433 | 34 | 5.8 | 9 | 2022-12-07
2022-12-08 | Click Here |  | 6.83 | 5.36 | 5.39 | 5.34 | 5.45 | 6.62 | 6.83 | 1.39 | 1.58 | 1.84 | 1.69 | 37 | 32 | 19 | 2 | 4 | 0 | 0.667 | 0.316 | 1.29 | 0.173 | 0.685 | 0.591 | 8.1 | 20 | 20.4 | 19.9 | 26.6 | 11.7 | 32.1 | 26.7 | 26.1 | 36.3 | 2.98 | 3.11 | 2.9 | 5.8 | 0.012 | 7.6 | 6.2 | 1.165 | 63.9 | 95.2 | 0.198 | 0.0214 | 14.31 | 13.37 | 14.38 | 1.01 | 1.81 | 2.49 | 8.779 | 2.995 | 37.56 | 5.8 | 9.3 | 2022-12-08
2022-12-09 | Click Here |  | 6.18 | 5.39 | 5.49 | 5.51 | 5.53 | 6.71 | 7.15 | 1.65 | 1.81 | 1.82 | 1.87 | 40 | 31 | 37 | 8 | 3 | 0 | 0.388 | 0.307 | 1.47 | 0.233 | 1.32 | 1.6 | 8 | 20 | 21.2 | 21.2 | 27.9 | 11.9 | 33.5 | 27.4 | 27.7 | 38.6 | 3.04 | 3.21 | 3 | 6 | 0.058 | 9 | 6.6 | 1.033 | 58.3 | 89.3 | 0.2343 | 0.049 | 13.75 | 12.71 | 13.69 | 0.98 | 1.784 | 2.483 | 8.796 | 2.993 | 35.99 | 6.9 | 9.5 | 2022-12-09
2022-12-10 | Click Here |  | 6.34 | 5.49 | 5.51 | 5.55 | 5.54 | 7.13 | 6.82 | 1.68 | 1.92 | 2.04 | 2.02 | 40 | 29 | 30 | 6 | 3 | 0 | 0.59 | 0.346 | 1.61 | 0.161 | 0.771 | 0.72 | 7.6 | 20.7 | 20.4 | 21.1 | 27.6 | 11.4 | 34.9 | 26.8 | 27.7 | 38.6 | 3.04 | 3.26 | 3.1 | 5.9 | 0.044 | 9.2 | 7.1 | 1.1137 | 59.3 | 91.7 | 0.2266 | 0.0376 | 13.59 | 12.58 | 13.57 | 0.99 | 1.673 | 2.518 | 8.53 | 3.1037 | 36.17 | 7.2 | 9.7 | 2022-12-10
2022-12-11 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-12-11
2022-12-12 | Click Here |  | 6.32 | 5.49 | 5.51 | 5.53 | 5.56 | 7.31 | 7.07 | 1.71 | 1.83 | 2 | 1.95 | 43 | 32 | 35 | 8 | 9 | 0 | 0.33 | 0.269 | 1.16 | 0.259 | 0.793 | 0.676 | 8.4 | 21.9 | 21.4 | 21.3 | 28.4 | 12.1 | 36.9 | 27.7 | 28 | 39.6 | 2.96 | 3.17 | 3 | 5.8 | 0.041 | 7.8 | 7 |  | 56.7 | 91.2 | 0.2459 | 0.0399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 37.01 | 7.5 | 9.7 | 2022-12-12
2022-12-13 | Click Here |  | 6.7 | 5.48 | 5.5 | 5.52 | 5.47 | 7.64 | 7.49 | 1.76 | 1.89 | 1.99 | 2.01 | 47 | 39 | 25 | 1 | 4 | 0 | 0.596 | 0.284 | 0.968 | 0.21 | 0.468 | 0.455 | 8.3 | 22.2 | 21.3 | 21.4 | 28.8 | 12.1 | 36.9 | 27.7 | 28.1 | 39.9 | 3.03 | 3.19 | 3 | 6.1 | 0.018 | 7.9 | 6.7 | 0.94432 | 62.7 | 91 | 0.2025 | 0.0409 | 14.47 | 13.74 | 14.51 | 0.77 | 1.735 | 2.881 | 9.093 | 2.9143 | 36.94 | 7.5 | 9.7 | 2022-12-13
2022-12-14 | Click Here |  | 6.51 | 5.57 | 5.69 | 5.58 | 5.62 | 7.54 | 7.73 | 1.56 | 1.61 | 2.08 | 2.02 | 36 | 27 | 28 | 2 | 4 | 0 | 0.424 | 0.318 | 1.13 | 0.228 | 0.701 | 0.678 | 7.9 | 21.4 | 21.1 | 21.2 | 31.1 | 11.6 | 36 | 27.5 | 28 | 42.9 | 3.03 | 3.21 | 3.1 | 6.1 | 0.034 | 8.1 | 6.5 | 0.87831 | 58.1 | 88.8 | 0.2353 | 0.0512 | 13.94 | 13.08 | 13.88 | 0.8 | 1.735 | 2.881 | 9.093 | 2.9083 | 37.37 | 7.8 | 9.3 | 2022-12-14
2022-12-15 | Click Here |  | 6.17 | 5.62 | 5.69 | 5.67 | 5.71 | 7.5 | 7.63 | 1.67 | 1.89 | 1.94 | 1.95 | 42 | 33 | 22 | 6 | 10 | 1 | 0.409 | 0.317 | 2.21 | 0.133 | 0.488 | 0.384 | 8.6 | 22 | 21.6 | 21.8 | 29.9 | 12.7 | 37.8 | 28.6 | 29 | 41.3 | 3 | 3.21 | 3 | 5.9 | 0.039 | 8.6 | 6.6 | 0.95431 | 58.4 | 91 | 0.2334 | 0.0408 | 14.03 | 13.13 | 13.97 | 0.84 | 1.735 | 2.881 | 9.093 | 2.9643 | 37.32 | 7.8 | 9 | 2022-12-15
2022-12-16 | Click Here |  | 6.245 | 5.61 | 5.55 | 5.59 | 5.63 | 7.24 | 7.18 | 1.72 | 1.93 | 1.98 | 1.98 | 44 | 37 | 20 | 3 | 5 | 0 | 0.568 | 0.301 | 1.9 | 0.144 | 0.392 | 0.361 | 8.5 | 22.7 | 21.7 | 22 | 30.4 | 12.3 | 38.4 | 28.9 | 29.3 | 42.7 | 3.06 | 3.28 | 2.9 | 5.9 | 0.024 | 8.5 | 6.5 | 0.9844 | 59.3 | 91.7 | 0.2264 | 0.0375 | 14.3 | 13.58 | 14.4 | 0.82 | 1.735 | 2.881 | 9.093 | 2.9744 | 36.96 | 7.5 | 9 | 2022-12-16
2022-12-17 | Click Here |  | 6.32 | 5.62 | 5.58 | 5.6 | 5.79 | 7.08 | 7.13 | 1.69 | 1.84 | 2.04 | 1.98 | 43 | 34 | 19 | 1 | 0 | 0 | 0.62 | 0.303 | 1.43 | 0.169 | 0.419 | 0.407 | 8.4 | 20.4 | 20.5 | 20.6 | 27.3 | 12.4 | 34.6 | 27.2 | 27.7 | 37.7 | 3.06 | 3.17 | 3 | 5.8 | 0.03 | 8.9 | 6.6 | 1.063 | 58.6 | 90.1 | 0.2315 | 0.0452 | 13.63 | 12.71 | 13.54 | 0.83 | 0 | 0 | 0 | 2.993 | 34.21 | 7 | 8.7 | 2022-12-17
2022-12-18 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2022-12-18
2022-12-19 | Click Here |  | 6.26 | 5.66 | 5.57 | 5.64 | 5.65 | 7.11 | 7.27 | 1.71 | 1.9 | 1.94 | 1.93 | 49 | 38 | 40 | 9 | 8 | 0 | 0.378 | 0.356 | 2.18 | 0.27 | 0.426 | 0.42 | 7.8 | 19.3 | 19.9 | 20.4 | 26.5 | 11.8 | 33 | 26.4 | 26.8 | 37.2 | 2.96 | 3.25 | 2.9 | 5.8 | 0.033 | 8.7 | 7.2 | 0.81075 | 52.9 | 89.4 | 0.2726 | 0.0483 | 13.15 | 12.24 | 13.07 | 0.83 | 1.735 | 2.881 | 9.093 | 2.7808 | 34.83 | 7 | 8.7 | 2022-12-19
2022-12-20 | Click Here |  | 6.15 | 5.69 | 5.58 | 5.65 | 5.72 | 7.02 | 7 | 1.66 | 1.81 | 2.02 | 1.82 | 45 | 36 | 53 | 25 | 10 | 0 | 0.689 | 0.418 | 3.43 | 0.997 | 0.551 | 0.538 | 8.5 | 18.9 | 18.2 | 19.6 | 25.7 | 12.7 | 32 | 24 | 26.3 | 36.1 | 3.11 | 3.23 | 3.1 | 5.9 | 0.014 | 9.2 | 7.1 | 0.89071 | 53.3 | 89.5 | 0.2731 | 0.0479 | 14.6 | 12.29 | 13.16 | 0.87 | 1.342 | 2.264 | 8.784 | 2.8507 | 33.36 | 6.8 | 8.7 | 2022-12-20
2022-12-21 | Click Here |  | 6.35 | 5.64 | 5.67 | 5.76 | 5.68 | 7.06 | 7.33 | 1.61 | 1.87 | 2.02 | 1.92 | 45 | 34 | 40 | 6 | 6 | 0 | 0.693 | 0.303 | 3.54 | 0.392 | 0.628 | 0.409 | 8.2 | 17.5 | 17.9 | 19.1 | 25.8 | 11.9 | 30.1 | 23.7 | 29.7 | 35.9 | 3.12 | 3.2 | 2.9 | 6 | 0.023 | 8.4 | 6.8 | 1.0713 | 52.1 | 90.2 | 0.2826 | 0.0446 | 14.32 | 12.1 | 13 | 0.9 | 1.272 | 2.437 | 8.528 | 3.0613 | 30.78 | 6 | 8.7 | 2022-12-21
2022-12-22 | Click Here |  | 6.34 | 5.54 | 5.53 | 5.62 | 5.67 | 7.26 | 7.06 | 1.65 | 1.85 | 2.02 | 2 | 46 | 35 | 14 | 2 | 1 | 0 | 0.28 | 0.304 | 0.695 | 0.33 | 0.307 | 0.289 | 8.2 | 19.3 | 19.1 | 19.2 | 24.1 | 12 | 31.3 | 25 | 25.4 | 33.7 | 3.01 | 3.18 | 3 | 6 | 0.045 | 8.4 | 7.1 | 0.85247 | 51 | 88.4 | 0.2921 | 0.0532 | 13.56 | 12.59 | 13.52 | 0.93 | 1.281 | 2.58 | 9.448 | 2.8625 | 29.85 | 5.8 | 8.7 | 2022-12-22
2022-12-23 | Click Here |  | 6.84 | 5.71 | 5.57 | 5.65 | 5.68 | 6.79 | 7.11 | 1.55 | 1.92 | 2.03 | 1.98 | 50 | 44 | 12 | 1 | 1 | 0 | 0.465 | 0.301 | 0.572 | 0.092 | 0.237 | 0.271 | 8 | 18.6 | 19.1 | 18.3 | 24.7 | 11.7 | 29.9 | 25 | 24.4 | 33.9 | 3.04 | 3.22 | 2.9 | 5.9 | 0.02 | 7.4 | 6.3 | 0.97412 | 51.3 | 90 | 0.2919 | 0.0448 | 13.32 | 12.37 | 13.29 | 0.92 | 1.143 | 2.389 | 8.849 | 2.9941 | 30.89 | 5.8 | 8.7 | 2022-12-23
2022-12-24 | Click Here |  | 7.01 | 5.52 | 5.45 | 5.51 | 5.59 | 7.22 | 7.34 | 1.66 | 1.99 | 2.11 | 2.06 | 35 | 31 | 2 | 0 | 0 | 0 | 0.618 | 0.309 | 0.595 | 0.074 | 0.197 | 0.341 | 8 | 19.6 | 19.1 | 18.7 | 25 | 11.4 | 32.4 | 24.5 | 24.8 | 34.1 | 3 | 3.18 | 3 | 6 | 0.022 | 3 | 6 | 1.0393 | 51.6 | 91.4 | 0.2917 | 0.0444 | 12.68 | 11.65 | 12.59 | 0.94 | 0 | 0 | 0 | 3.0393 | 31.54 | 5.6 | 8.9 | 2022-12-24
2022-12-25 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 1.0074 | 0 | 0 | 0 | 0 | 12.93 | 11.74 | 12.66 | 0.92 | 0.998 | 2.239 | 8.614 | 2.9974 | 0 | 5.6 | 8.9 | 2022-12-25
2022-12-26 | Click Here |  | 6.36 | 5.6 | 5.51 | 5.74 | 5.78 | 7.33 | 7.28 | 1.77 | 1.98 | 2.09 | 2.02 | 41 | 33 | 10 | 0 | 3 | 0 | 0.424 | 0.284 | 0.669 | 0.089 | 0.322 | 0.409 | 8.7 | 19.3 | 19.4 | 19.3 | 24.6 | 12.6 | 32.7 | 24.8 | 25.5 | 34.3 | 3.01 | 3.22 | 3 | 5.9 | 0.104 | 7.9 | 7 | 0.97178 | 58.4 | 89.6 | 0.2335 | 0.0474 | 12.72 | 11.69 | 12.64 | 0.95 | 1.012 | 2.24 | 8.624 | 3.0118 | 31.72 | 5.6 | 8.9 | 2022-12-26
2022-12-27 | Click Here |  | 6.29 | 5.88 | 5.99 | 5.63 | 5.77 | 7.49 | 7.65 | 1.73 | 1.88 | 2.01 | 1.98 | 46 | 38 | 19 | 0 | 4 | 0 | 0.314 | 0.308 | 0.597 | 0.072 | 0.356 | 0.684 | 8.4 | 19.9 | 19.1 | 19.2 | 25.2 | 11.9 | 31.2 | 24.5 | 25.4 | 34.5 | 3.04 | 3.27 | 2.9 | 5.9 | 0.03 | 7.1 | 6.3 | 0.84817 | 59.6 | 91.8 | 0.2244 | 0.0368 | 12.59 | 11.68 | 12.53 | 0.85 | 1.018 | 2.32 | 8.442 | 2.8282 | 30.91 | 5.6 | 8.9 | 2022-12-27
2022-12-28 | Click Here |  | 6.74 | 5.61 | 5.46 | 6.16 | 5.87 | 7.28 | 7.35 | 1.67 | 1.83 | 2.05 | 2.03 | 54 | 48 | 15 | 1 | 1 | 0 | 0.5645 | 0.304 | 0.531 | 0.083 | 0.094 | 0.306 | 8.1 | 19.7 | 18.9 | 19 | 24.9 | 11.7 | 32.1 | 24.4 | 25.2 | 23.9 | 3.07 | 3.28 | 3 | 6 | 0.033 | 7.7 | 6.1 | 1.0612 | 59.4 | 89.9 | 0.2246 | 0.0477 | 12.92 | 11.85 | 12.82 | 0.97 | 1.022 | 2.346 | 8.484 | 3.0412 | 30.47 | 5.5 | 8.9 | 2022-12-28
2022-12-29 | Click Here |  | 6.81 | 5.43 | 5.44 | 5.54 | 5.52 | 7.44 | 7.31 | 1.62 | 1.97 | 2.08 | 2.03 | 51 | 46 | 12 | 1 | 0 | 0 | 0.434 | 0.305 | 0.766 | 0.096 | 0.146 | 0.292 | 8.3 | 19.3 | 19.2 | 19 | 24.3 | 12 | 31.9 | 24.6 | 24.7 | 32.9 | 3.03 | 3.12 | 2.9 | 6 | 0.024 | 7.7 | 5.8 | 1.0677 | 59.7 | 90 | 0.2243 | 0.0473 | 13.25 | 12.32 | 13.25 | 0.93 | 1.133 | 2.382 | 9.006 | 3.0877 | 30.13 | 5.4 | 8.9 | 2022-12-29
2022-12-30 | Click Here |  | 6.54 | 5.46 | 5.43 | 5.52 | 5.61 | 7.18 | 7.2 | 1.66 | 1.84 | 2.02 | 2.1 | 48 | 37 | 13 | 2 | 0 | 0 | 0.377 | 0.318 | 0.701 | 0.092 | 0.38 | 0.53 | 8.2 | 19.5 | 19.3 | 19.1 | 26.6 | 12.1 | 32.1 | 25.1 | 24.8 | 38.2 | 3.13 | 3.22 | 3 | 6.1 | 0.033 | 7.8 | 6.1 | 1.0555 | 59.1 | 90.4 | 0.2255 | 0.047 | 13.13 | 12.21 | 13.12 | 0.91 | 1.288 | 2.393 | 8.297 | 3.0955 | 28.47 | 5.4 | 8.9 | 2022-12-30
2022-12-31 | Click Here |  | 6.43 | 5.49 | 5.44 | 5.45 | 5.53 | 7.1 | 7.49 | 1.65 | 1.78 | 1.93 | 1.99 | 50 | 39 | 16 | 1 | 5 | 0 | 0.343 | 0.316 | 1.68 | 0.108 | 0.664 | 0.464 | 8 | 18.9 | 19 | 18.8 | 23.9 | 11.5 | 30.9 | 24.2 | 24.5 | 32.7 | 3.01 | 3.23 | 3.1 | 5.9 | 0.029 | 7.6 | 6.2 | 0.86745 | 50.7 | 87.4 | 0.2942 | 0.0581 | 13.19 | 12.18 | 13.1 | 0.92 | 0 | 0 | 0 | 2.9175 | 27.82 | 5.5 | 8.9 | 2022-12-31
|  |  | pH | [6 empty] | Chlorine |  |  |  | Colour | [5 empty] | Turbidity | [5 empty] | Total Dissolved Solids |  |  |  |  | Conductivity |  |  |  |  | Hardness |  | Alkalinity |  | Aluminum | Temperature |  | Cl Demand | UVT |  | UVA |  | Flows withinin plant |  |  |  | Flows from plant |  |  | Chemical Dosages
|  |  | Raw | PTC | PTC (OL) | SWC | Filter | Finish (OL) | Finish | Free | Total | Sample | Analyzer | Raw A | Raw T | SWC A | Filter A | Finish A | Finish T | Raw | Raw (OL) | SWC | Filter | Finish | Finish (OL) | Raw | PTC | SWC | Filter | Finish | Raw | PTC | SWC | Filter | Finish | Raw | Finish | Raw | Finish | Finish (Free) | Raw | Finish |  | Raw | Filter | Raw | Filter | Raw | Finish | Filter | Backwash | Bishop's | Botwood | GFW | Chlorine | Alum | Lime (Pre) | Lime (Post)
January 2022 Average |  |  | 6.03 | 5.13 | 5.15 | 5.26 | 5.27 | 6.77 | 6.93 | 1.57 | 1.77 | 1.97 | 1.9 | 63.12 | 54.88 | 28.62 | 4.63 | 3.18 | #DIV/0! | 0.53 | 0.3 | 1.7 | 0.3 | 0.86 | 0.65 | 12.85 | 34.21 | 26.27 | 27.85 | 36.85 | 34.58 | 68.42 | 52.51 | 55.69 | 73.69 | 2.66 | 2.87 | 2.96 | 5.84 | 0.08 | 6.74 | 5.97 | 1.34 | 47.12 | 86.9 | 0.33 | 0.06 | 13.54 | 12.51 | 13.44 | 1 | 1.44 | 2.04 | 8.44 | 3.23 | 30.35 | 5.38 | 13.63
February 2022 Average |  |  | 5.83 | 5.14 | 5.19 | 5.24 | 5.28 | 7.03 | 7.19 | 1.53 | 1.69 | 1.88 | 1.82 | 69.75 | 60.67 | 23.92 | 2.95 | 5.18 | #DIV/0! | 0.56 | 0.34 | 1.99 | 0.23 | 0.67 | 0.68 | 11.27 | 31.65 | 24.86 | 25.1 | 36.4 | 22.54 | 62.88 | 49.73 | 50.2 | 72.85 | 2.82 | 3.02 | 3.01 | 5.9 | 0.04 | 7.08 | 5.44 | 1.1 | 45.67 | 88.91 | 0.34 | 0.05 | 13.33 | 12.52 | 13.3 | 0.93 | 1.54 | 2.01 | 8.38 | 2.93 | 29.79 | 7.5 | 14.76
March 2022 Average |  |  | 6.07 | 5.11 | 5.3 | 5.19 | 5.21 | 6.66 | 6.67 | 1.53 | 1.68 | 1.85 | 1.77 | 74.33 | 65.74 | 31.07 | 3.62 | 5.88 | 1 | 0.62 | 0.49 | 2.29 | 0.24 | 1.06 | 1.05 | 8.62 | 28.02 | 21.77 | 21.82 | 28.78 | 16.77 | 55.26 | 41.93 | 42.06 | 55.39 | 2.87 | 3.11 | 2.95 | 5.87 | 0.09 | 8.12 | 5.98 | 1.28 | 46.42 | 84.37 | 0.33 | 0.07 | 14.51 | 13.01 | 13.82 | 0.95 | 2.02 | 2.02 | 8.48 | 3.02 | 29.71 | 7.67 | 17.9
April 2022 Average |  |  | 5.89 | 5.12 | 5.23 | 5.16 | 5.23 | 7.38 | 7.26 | 1.6 | 1.75 | 1.89 | 1.81 | 64.62 | 55.92 | 20.08 | 2.74 | 3.85 | #DIV/0! | 0.5 | 0.33 | 1.28 | 0.18 | 0.37 | 0.3 | 5.86 | 20.11 | 17.33 | 17.38 | 27.12 | 10.15 | 36.34 | 28.21 | 28.5 | 44.51 | 2.78 | 2.9 | 3 | 6 | 0.13 | 8.63 | 5.79 | 0.87 | 50.5 | 90.67 | 0.3 | 0.04 | 14.77 | 13.57 | 14.32 | 1.01 | 1.26 | 1.99 | 8.38 | 2.68 | 29.56 | 6.57 | 10.63
May 2022 Average |  |  | 6.16 | 5.18 | 5.13 | 5.19 | 5.29 | 7.34 | 7.28 | 1.48 | 1.63 | 1.84 | 1.76 | 51.65 | 42.88 | 10.54 | 2.13 | 2.6 | #DIV/0! | 0.54 | 0.43 | 0.69 | 0.15 | 0.32 | 0.25 | 5.32 | 16.08 | 15.16 | 14.84 | 22.04 | 9.1 | 28.87 | 24.16 | 23.66 | 32.78 | 2.92 | 3.09 | 2.98 | 5.94 | 0.12 | 14.7 | 9.65 | 1.1 | 60.21 | 94.05 | 0.22 | 0.03 | 13.88 | 12.9 | 13.68 | 0.99 | 1.81 | 1.84 | 8.38 | 2.86 | 28.58 | 4.36 | 6.76
June 2022 Average |  |  | 6.69 | 5.31 | 5.28 | 5.39 | 5.38 | 7.3 | 7.24 | 1.53 | 1.67 | 1.95 | 1.85 | 46.04 | 36.65 | 12.81 | 1.56 | 1.25 | #DIV/0! | 0.62 | 0.55 | 0.89 | 0.13 | 0.3 | 0.26 | 5.63 | 15.73 | 15.28 | 15.03 | 20.88 | 10.56 | 30.34 | 27.44 | 26.79 | 34.68 | 3.04 | 3.24 | 3 | 5.94 | 0.11 | 18.27 | 14.19 | 1.2 | 61.2 | 93.8 | 0.21 | 0.03 | 15.33 | 13.94 | 14.82 | 1.03 | 1.32 | 2.51 | 10.08 | 3.05 | 27.75 | 3.45 | 5.3
July 2022 Average |  |  | 6.48 | 5.18 | 5.17 | 5.11 | 5.19 | 7.35 | 7.39 | 1.53 | 1.66 | 1.93 | 1.86 | 36.75 | 29.17 | 11.5 | 1.08 | #DIV/0! | #DIV/0! | 0.57 | 0.46 | 0.89 | 0.13 | 0.26 | 0.21 | 6.17 | 15.05 | 14.64 | 14.54 | 21.41 | 12.23 | 30.02 | 28.67 | 28.94 | 39.61 | 3.11 | 3.23 | 2.94 | 5.94 | 0.1 | 20.67 | 18.23 | 1.35 | 68.4 | 91.11 | 0.17 | 0.06 | 15.34 | 14.23 | 15.18 | 0.99 | 1.38 | 2.44 | 10.22 | 3.22 | 25.18 | 2.48 | 5.34
August 2022 Average |  |  | 6.4 | 5.44 | 5.35 | 5.57 | 5.7 | 7.45 | 7.41 | 1.59 | 1.7 | 2.1 | 2.04 | 29.3 | 21.52 | 18.19 | 1.56 | 1 | #DIV/0! | 0.52 | 0.4 | 1.35 | 0.19 | 0.25 | 0.2 | 6.89 | 13.9 | 13.52 | 13.69 | 21.46 | 13.89 | 28.54 | 26.64 | 27.91 | 41.07 | 3.12 | 3.28 | 2.91 | 5.93 | 0.09 | 21.84 | 20.21 | 1.27 | 70.1 | 91.11 | 0.15 | 0.04 | 15.84 | 14.66 | 15.64 | 0.98 | 1.51 | 2.34 | 10.32 | 3.28 | 20.95 | 2.16 | 4.47
September 2022 Average |  |  | 6.54 | 5.55 | 5.46 | 5.55 | 5.55 | 7.19 | 7.07 | 1.71 | 1.83 | 2.14 | 2.02 | 33.15 | 25.15 | 21.15 | 2.71 | 3.4 | #DIV/0! | 0.8 | 0.82 | 1.15 | 0.21 | 0.31 | 0.27 | 6.89 | 13.38 | 13.24 | 12.95 | 19.02 | 12.96 | 26.02 | 24.32 | 24.76 | 35.42 | 3.01 | 3.16 | 2.93 | 5.91 | 0.08 | 18.33 | 18.36 | 1.33 | 70.23 | 91.4 | 0.15 | 0.06 | 13.97 | 12.82 | 13.79 | 0.97 | 1.57 | 2.06 | 8.19 | 3.34 | 21.2 | 1.23 | 3.7
October 2022 Average |  |  | 6.57 | 5.29 | 5.34 | 5.23 | 5.29 | 6.98 | 7.2 | 1.7 | 1.83 | 2.01 | 1.9 | 34.23 | 26.46 | 27.41 | 6.04 | 3.21 | 2.33 | 0.74 | 0.72 | 1.6 | 0.39 | 0.64 | 0.5 | 7.31 | 15.63 | 15.15 | 15.08 | 18.99 | 12.46 | 28.28 | 24.7 | 25.51 | 32.85 | 2.97 | 3.26 | 2.94 | 5.87 | 0.08 | 14.4 | 14.66 | 0.98 | 63.38 | 88.61 | 0.2 | 0.05 | 14.39 | 13.26 | 14.26 | 1.04 | 1.46 | 2.1 | 7.46 | 3.23 | 24.23 | 2.14 | 5.33
November 2022 Average |  |  | 6.63 | 5.38 | 5.36 | 5.47 | 5.48 | 6.84 | 6.91 | 1.81 | 1.98 | 2.18 | 2.09 | 41.19 | 32.62 | 27.27 | 5 | 7.05 | 2 | 0.77 | 0.59 | 1.48 | 0.33 | 0.89 | 0.73 | 7.77 | 19.42 | 18.99 | 18.86 | 24.66 | 11.67 | 32.58 | 26.2 | 26.43 | 37.28 | 3.01 | 3.19 | 2.97 | 5.92 | 0.06 | 9.3 | 10.03 | 1.28 | 61.61 | 88.26 | 0.21 | 0.05 | 13.86 | 12.62 | 13.53 | 0.98 | 1.53 | 2.22 | 7.99 | 3.25 | 30.79 | 4.47 | 9.4
December 2022 Average |  |  | 6.53 | 5.52 | 5.49 | 5.57 | 5.61 | 7.13 | 7.2 | 1.64 | 1.83 | 2.01 | 1.98 | 43.78 | 35.59 | 20.78 | 4.29 | 4.14 | 1 | 0.55 | 0.34 | 1.31 | 0.2 | 0.53 | 0.56 | 8.2 | 20.31 | 20.03 | 20.09 | 27.37 | 11.92 | 33.79 | 26.2 | 26.74 | 37.64 | 3.02 | 3.18 | 2.97 | 5.92 | 0.03 | 7.83 | 6.71 | 0.94 | 57.86 | 90.11 | 0.24 | 0.05 | 13.65 | 12.61 | 13.53 | 0.92 | 1.42 | 2.52 | 8.81 | 2.94 | 33.45 | 6.33 | 9.26
2022 Average |  |  | 6.32 | 5.28 | 5.29 | 5.33 | 5.38 | 7.12 | 7.14 | 1.6 | 1.75 | 1.98 | 1.9 | 48.94 | 40.55 | 21.2 | 3.42 | 4.39 | 1.63 | 0.61 | 0.48 | 1.39 | 0.22 | 0.54 | 0.47 | 7.72 | 20.26 | 18 | 18.08 | 25.38 | 14.86 | 38.35 | 31.63 | 32.17 | 44.67 | 2.94 | 3.13 | 2.97 | 5.91 | 0.08 | 12.95 | 11.25 | 1.17 | 58.57 | 89.92 | 0.24 | 0.05 | 14.37 | 13.23 | 14.12 | 0.98 | 1.53 | 2.17 | 8.74 | 3.09 | 27.65 | 4.48 | 8.88
[52 empty] | 12.62 | 3.301 | 17.461

## 2021
Note: The password to unlock the sheets is "WTPLAB". Don't unlock any of them unless you plan on making permanent changes.
|  |  | pH | [6 empty] | Chlorine |  |  |  | Colour | [5 empty] | Turbidity | [5 empty] | Total Dissolved Solids |  |  |  |  | Conductivity |  |  |  |  | Hardness |  | Alkalinity |  | Aluminum | Temperature |  | Cl Used | Cl Demand | UVT |  | UVA |  | Flows withinin plant |  |  |  | Flows from plant |  |  | Chemical Dosages |  |  |  |  | Dennis Penney
Date | Shortcut | Start Time | Raw | PTC | PTC (OL) | SWC | Filter | Finish (OL) | Finish | Free | Total | Sample | Analyzer | Raw A | Raw T | SWC A | Filter A | Finish A | Finish T | Raw | Raw (OL) | SWC | Filter | Finish | Finish (OL) | Raw | PTC | SWC | Filter | Finish | Raw | PTC | SWC | Filter | Finish | Raw | Finish | Raw | Finish | Finish (Free) | Raw | Finish |  |  | Raw | Filter | Raw | Filter | Raw | Finish | Filter | Backwash | Bishop's | Botwood | GFW | Chlorine | Alum | Lime (Pre) | Lime (Post) | Date | Jerry Loveless
2021-01-01 | Click Here |  | 6.07 | 5.19 | 5.25 | 5.28 | 5.34 | 7.42 | 7.53 | 1.74 | 1.9 | 2.09 | 2.13 | 39 | 31 | 16 |  |  |  | 0.471 | 0.506 | 1.17 | 0.144 | 0.377 | 0.431 | 13.3 | 32.9 | 29 | 30.4 | 37.2 | 26.6 | 65.8 | 58 | 60.8 | 74.4 | 3.01 | 4.14 | 3.1 | 5.9 | 0.047 | 6.5 | 5.6 | 82.07 | 0.7888 | 59 | 90.6 | 0.2294 | 0.0429 | 13.951 | 12.898 | 13.874 | 0.976 | 1.41 | 2.711 | 8.168 | 2.8888 | 30.56 | 4.8 | 9.3 | 2021-01-01 | Nolan Simms
2021-01-02 | Click Here |  | 6.01 | 5.14 | 5.23 | 5.3 | 5.37 | 7.46 | 7.51 | 1.82 | 2.04 | 2.04 | 2 | 39 | 32 | 19 | 1 |  |  | 0.418 | 0.497 | 1.24 | 0.16 | 0.391 | 0.447 | 13.8 | 33.1 | 29.2 | 29.4 | 36.8 | 27.6 | 66.2 | 58.4 | 58.8 | 73.6 | 3.01 | 4.01 | 3.1 | 5.9 | 0.037 | 6.4 | 5.4 | 81.6 | 1.0644 | 58.8 | 90.9 | 0.2306 | 0.0409 | 13.32 | 12.29 | 13.26 | 0.97 |  |  |  | 3.0143 | 30.38 | 4.8 | 9.3 | 2021-01-02
2021-01-03 | Click Here | [58 empty] | 2021-01-03
2021-01-04 | Click Here |  | 5.83 | 5.17 | 5.21 | 5.36 | 5.37 | 6.8 | 7.39 | 1.58 | 1.86 | 1.94 | 1.95 | 48 | 40 | 27 | 2 |  |  | 0.534 | 0.485 | 1.19 | 0.175 | 0.466 | 0.508 | 13.6 | 37 | 27.9 | 28.6 | 38.8 | 27.2 | 74 | 55.8 | 75.2 | 77.6 | 2.95 | 2.96 | 3 | 5.9 | 0.012 | 7 | 5.5 | 77.18 | 0.57786 | 54.4 | 90 | 0.2642 | 0.0454 | 13.95 | 12.94 | 13.91 | 0.97 | 1.508 | 2.63 | 8.423 | 2.7079 | 31.92 | 4.8 | 9.3 | 2021-01-04 | Continuous
2021-01-05 | Click Here |  | 6.01 | 5.25 | 5.21 | 5.4 | 5.45 | 7.24 | 6.93 | 1.66 | 1.77 | 1.92 | 1.95 | 50 | 42 | 32 | 8 |  |  | 0.524 | 0.481 | 1.21 | 0.212 | 0.55 | 0.525 | 14.1 | 38.6 | 28 | 28.9 | 39.2 | 28.2 | 77.2 | 56 | 57.8 | 78.4 | 3.08 | 3.23 | 3 | 5.9 | 0.022 | 8.2 | 5.5 | 79.38 | 0.77585 | 53.8 | 89.6 | 0.2689 | 0.0475 | 16.68 | 12.89 | 13.87 | 0.98 | 1.508 | 2.67 | 8.424 | 2.7959 | 31.69 | 4.8 | 9.6 | 2021-01-05 | Grab
2021-01-06 | Click Here |  | 6.14 | 5.29 | 5.28 | 5.36 | 5.42 | 7.29 | 7.4 | 1.62 | 1.84 | 1.92 | 1.85 | 49 | 42 | 36 | 4 |  |  | 0.65 | 0.453 | 1.1 | 0.176 | 0.399 | 0.456 | 13.4 | 36.8 | 27.8 | 28.6 | 39 | 26.4 | 73.6 | 55.6 | 57.2 | 78 | 3.14 | 3.31 | 3 | 6 | 0.097 | 6.9 | 5.7 | 79.69 | 0.67671 | 55.2 | 90.4 | 0.2579 | 0.0435 | 15.55 | 13.22 | 14.2 | 0.98 | 1.502 | 2.676 | 8.7 | 2.7367 | 29.63 | 4.8 | 9.6 | 2021-01-06 | ^ Stuff for form dropdown menus
2021-01-07 | Click Here |  | 5.99 | 5.16 | 5.24 | 5.22 | 5.29 | 7.34 | 7.29 | 1.55 | 1.76 | 1.84 | 1.92 | 47 | 40 | 7 |  |  |  | 0.396 | 0.459 | 0.31 | 0.112 | 0.407 | 0.45 | 13.6 | 36.5 | 28.1 | 28.8 | 39 | 27.2 | 73 | 56.2 | 57.6 | 78 | 3.06 | 3.21 | 2.9 | 5.8 | 0.074 | 7.3 | 6.3 | 79.38 | 0.75991 | 54.9 | 87.9 | 0.2614 | 0.0557 | 13.75 | 12.69 | 13.67 | 0.98 | 1.51 | 2.69 | 8.319 | 2.8399 | 30.64 | 4.8 | 9.4 | 2021-01-07
2021-01-08 | Click Here |  | 6.02 | 5.26 | 5.48 | 5.34 | 5.42 | 7.12 | 7.18 | 1.68 | 1.89 | 2.05 | 2.02 | 46 | 39 | 6 |  |  |  | 0.408 | 0.495 | 0.296 | 0.097 | 0.553 | 0.607 | 13.4 | 33.1 | 28.2 | 27.9 | 37.6 | 26.8 | 66.2 | 56.4 | 55.8 | 75.2 | 3.12 | 3.45 | 3.1 | 5.9 | 0.052 | 7.4 | 6.6 | 79.69 | 0.65127 | 54.6 | 89.9 | 0.2712 | 0.0464 | 14.17 | 13.15 | 14.09 | 0.94 | 1.579 | 2.702 | 8.652 | 2.7513 | 30.28 | 4.8 | 9.4 | 2021-01-08
2021-01-09 | Click Here |  | 5.99 | 5.24 | 5.29 | 5.29 | 5.36 | 7.29 | 7.4 | 1.7 | 1.93 | 2.09 | 2.08 | 47 | 40 | 5 |  |  |  | 0.364 | 0.391 | 0.249 | 0.089 | 0.474 | 0.524 | 13.1 | 33.9 | 28.4 | 28 | 37.4 | 26.2 | 67.8 | 56.8 | 56 | 74.8 | 3.04 | 3.38 | 3 | 5.9 | 0.061 | 7.3 | 6.4 | 74.88 | 0.50457 | 55.1 | 90.2 | 0.2687 | 0.0451 | 13.54 | 13.36 | 13.36 |  |  |  |  | 2.5446 | 30.46 | 4.8 | 9.4 | 2021-01-09
2021-01-10 | Click Here | [41 empty] | 84.03 | 0.7825 |  |  |  |  | 14.74 | 13.76 | 14.71 | 0.95 | 1.519 | 2.736 | 8.764 | 2.7725 |  |  |  | 2021-01-10
2021-01-11 | Click Here |  | 6.04 | 5.19 | 5.29 | 5.34 | 5.41 | 7.19 | 7.26 | 1.67 | 1.89 | 2.01 | 1.98 | 44 | 36 | 4 |  |  |  | 0.391 | 0.457 | 0.299 | 0.107 | 0.524 | 0.926 | 13.2 | 34.4 | 28.6 | 29.1 | 37.7 | 26.4 | 68.8 | 57.2 | 58.2 | 75.4 | 3.17 | 3.58 | 3 | 6 | 0.061 | 7.4 | 6.3 | 93.87 | 0.75375 | 53.7 | 89.9 | 0.2794 | 0.0464 | 16.01 | 15.2 | 16.21 | 1.01 | 1.603 | 2.757 | 8.918 | 2.8037 | 29.96 | 4.8 | 9.4 | 2021-01-11
2021-01-12 | Click Here |  | 6.34 | 5.28 | 5.27 | 5.48 | 5.64 | 7.72 | 7.11 | 1.7 | 1.94 | 1.96 | 1.8 | 49 | 42 | 5 |  |  |  | 0.594 |  | 0.371 | 0.104 | 0.368 | 0.446 | 12.7 | 32.6 | 23.4 | 25.1 | 35.2 | 25.4 | 65.2 | 46.8 | 50.2 | 70.4 | 3.17 | 3.39 | 3.1 | 5.9 | 0.047 | 3.1 | 5.9 | 74.97 | 0.57072 | 96 | 88.9 | 0.2817 | 0.0509 | 13.43 | 13.24 | 13.24 |  | 1.547 | 2.758 | 8.42 | 2.5707 | 30.38 | 4.8 | 9.4 | 2021-01-12
2021-01-13 | Click Here |  | 6.08 | 5.2 | 5.25 | 5.35 | 5.39 | 7.1 | 7.54 | 1.42 | 1.56 | 1.74 | 1.76 | 52 | 45 | 18 | 2 |  |  | 0.569 | 0.421 | 1.06 | 0.1 | 0.542 | 0.607 | 14.1 | 37.8 | 27.4 | 28.5 | 37.8 | 28.2 | 75.6 | 54.8 | 57 | 75.6 | 3.16 | 3.18 | 3 | 6 | 0.011 | 7.6 | 5.9 | 63.95 | 0.25891 | 53.5 | 88.2 | 0.271 | 0.0544 | 13.82 | 12.74 | 13.73 | 0.99 | 1.631 | 2.77 | 8.483 | 2.2789 | 29.57 | 4.8 | 9.4 | 2021-01-13
2021-01-14 | Click Here |  | 5.97 | 5.26 | 5.27 | 5.35 | 5.38 | 7.18 | 7.24 | 1.57 | 1.82 | 2.05 | 2.09 | 47 | 40 | 12 |  |  |  | 0.409 | 0.326 | 1.02 | 0.096 | 0.436 | 0.499 | 13.8 | 36.6 | 27.5 | 29.1 | 37.2 | 27.6 | 73.2 | 55 | 58.2 | 74.4 | 3.15 | 3.27 | 3 | 5.9 | 0.014 | 7.4 | 5.8 | 77.18 | 0.70213 | 54.1 | 90 | 0.2656 | 0.0475 | 13.75 | 12.64 | 13.62 | 0.98 | 1.657 | 2.787 | 7.773 | 2.7721 | 29.57 | 4.8 | 9.4 | 2021-01-14
2021-01-15 | Click Here |  | 5.93 | 5.37 | 5.14 | 5.39 | 5.42 | 7.08 | 7.09 | 1.57 | 1.65 | 2.02 | 2.07 | 50 | 42 | 16 |  |  |  | 0.474 | 0.312 | 1.34 | 0.082 | 0.445 | 0.525 | 14 | 33.8 | 27.4 | 27.7 | 39 | 28 | 67.6 | 54.8 | 55.4 | 78 | 3.03 | 3.23 | 3.1 | 6 | 0.015 | 7.5 | 5.6 | 79.38 | 0.7129 | 8 | 88.5 | 0.2767 | 0.0526 | 13.93 | 12.95 | 13.89 | 0.94 | 1.742 | 2.755 | 7.946 | 2.7829 | 29.8 | 4.8 | 9.4 | 2021-01-15
2021-01-16 | Click Here |  | 6.02 | 5.26 | 5.29 | 5.31 | 5.44 | 7.03 | 7.08 | 1.62 | 1.79 | 2.05 | 2.03 | 46 | 39 | 14 |  |  |  | 0.496 | 0.381 | 1.21 | 0.094 | 0.326 | 0.39 | 13.8 | 33.1 | 27.5 | 28.2 | 38.8 | 27.6 | 66.2 | 55 | 56.4 | 77.6 | 3.01 | 3.33 | 3 | 5.8 | 0.021 | 7.4 | 5.4 | 74.97 | 0.61422 | 54.1 | 89.2 | 0.2491 | 0.0488 | 13.61 | 12.54 | 13.52 | 0.98 | 1.647 | 2.766 | 7.83 | 2.7142 | 30.04 | 4.8 | 9.4 | 2021-01-16
2021-01-17 | Click Here | [58 empty] | 2021-01-17
2021-01-18 | Click Here |  | 6.36 | 5.27 | 5.23 | 5.39 | 5.38 | 6.89 | 7.22 | 1.69 | 1.84 | 2.16 | 2.22 | 45 | 38 | 16 | 1 | O | O | 0.452 | 0.357 | 1.09 | 0.14 | 0.896 | 0.436 | 14.2 | 35 | 27.7 | 28.1 | 38.6 | 28.4 | 70 | 55.4 | 56.2 | 77.2 | 3.04 | 3.27 | 3 | 5.9 | 0.029 | 7.7 | 5.7 | 77.18 | 0.62652 | 54.3 | 120 | 0.2489 | -0.079 | 13.64 | 12.62 | 13.6 | 0.98 | 1.76 | 2.763 | 8.231 | 2.7765 | 26.56 | 4.8 | 9.4 | 2021-01-18
2021-01-19 | Click Here |  | 6.34 | 5.22 | 5.22 | 5.34 | 5.38 | 6.82 | 7.2 | 1.78 | 2 | 2.2O+ | 2.2 | 44 | 37 | 15 |  |  |  | 0.52 | 0.363 | 0.816 | 0.095 | 0.086 | 0.427 | 14.2 | 35.7 | 28.2 | 28.1 | 38.4 | 28.4 | 71.4 | 56.4 | 56.2 | 76.8 | 3.11 | 3.31 | 3 | 5.7 | 0.033 | 7.7 | 5.6 | 77.18 | 0.57205 | 51.5 | 89.4 | 0.2879 | 0.0485 | 13.93 | 12.92 | 13.91 | 0.99 | 1.672 | 2.78 | 8.073 | 2.7121 | 28.26 | 4.8 | 9.4 | 2021-01-19
2021-01-20 | Click Here |  | 5.97 | 5.25 | 5.23 | 5.4 | 5.42 | 7.26 | 7.22 | 1.61 | 1.74 | 1.88 | 2 | 43 | 36 | 12 |  |  |  | 0.465 | 0.361 | 0.863 | 0.092 | 0.67 | 0.434 | 14.4 | 36.1 | 27.9 | 28.2 | 38.8 | 28.8 | 72.2 | 55.8 | 56.4 | 77.6 | 2.99 | 3.18 | 3 | 5.8 | 0.018 | 7.9 | 5.8 | 74.97 | 0.48416 | 54.9 | 90.5 | 0.2607 | 0.0433 | 13.27 | 13.07 | 13.07 |  | 1.507 | 2.786 | 8.057 | 2.6042 | 30.51 | 4.8 | 9.7 | 2021-01-20
2021-01-21 | Click Here |  | 5.98 | 5.26 | 5.24 | 5.35 | 5.44 | 7.1 | 7.13 | 1.59 | 1.71 | 1.86 | 1.96 | 41 | 33 | 14 |  |  |  | 0.451 | 0.252 | 1.18 | 0.157 | 0.457 | 0.481 | 14.4 | 36.4 | 27.8 | 28.4 | 38.3 | 28.8 | 72.8 | 55.6 | 56.8 | 76.6 | 3.08 | 3.23 | 3 | 5.9 | 0.022 | 7.8 | 5.9 | 73.96 | 0.61769 | 52.1 | 89.4 | 0.2829 | 0.0483 | 13.32 | 12.31 | 13.27 | 0.96 | 1.539 | 2.783 | 8.212 | 2.7277 | 30.28 | 4.8 | 9.7 | 2021-01-21
2021-01-22 | Click Here |  | 6.02 | 5.21 | 5.27 | 5.39 | 5.46 | 7.19 | 7.13 | 1.64 | 1.8 | 1.94 | 2.06 | 44 | 37 | 9 |  |  |  | 0.396 | 0.308 | 1.09 | 0.104 | 0.421 | 0.461 | 14.5 | 37.4 | 28 | 28.3 | 38.1 | 29 | 74.8 | 56 | 56.6 | 76.2 | 3.06 | 3.25 | 3.1 | 5.9 | 0.0041 | 7.9 | 6.5 | 79.74 | 0.61028 | 53.8 | 91 | 0.2689 | 0.0397 | 14.227 | 13.163 | 14.135 | 0.972 | 1.519 | 2.788 | 8.147 | 2.7503 | 30.43 | 4.8 | 9.7 | 2021-01-22
2021-01-23 | Click Here |  | 6.04 | 5.16 | 5.28 | 5.33 | 5.41 | 7.1 | 7.29 | 1.54 | 1.71 | 1.94 | 1.92 | 49 | 41 | 12 | 1 |  |  | 0.336 | 0.317 | 0.991 | 0.113 | 0.594 | 0.637 | 14.1 | 37 | 27.8 | 28.2 | 38.4 | 28.2 | 74 | 55.6 | 56.4 | 76.8 | 2.96 | 3.1 | 3 | 5.9 | 0.061 | 7.7 | 6.4 | 72.77 | 0.64773 | 53.5 | 90.4 | 0.2701 | 0.0421 | 12.99 | 11.98 | 12.96 | 0.98 |  |  |  | 2.7577 | 30.11 | 4.8 | 9.7 | 2021-01-23
2021-01-24 | Click Here | [58 empty] | 2021-01-24
2021-01-25 | Click Here |  | 5.99 | 5.31 | 5.32 | 5.58 | 5.46 | 7.05 | 7.1 | 1.49 | 1.6 | 2.06 | 2.16 | 41 | 34 | 10 |  |  |  | 0.412 | 0.308 | 1.75 | 0.173 | 0.428 | 0.525 | 14 | 34.7 | 28.3 | 28.2 | 38.9 | 28 | 69.4 | 56.6 | 56.4 | 77.8 | 2.94 | 3.29 | 3 | 5.9 | 0.013 | 6.9 | 5.9 | 70.56 | 0.44456 | 53.7 | 89.1 | 0.2695 | 0.0498 | 13.65 | 12.54 | 13.53 | 0.99 | 1.582 | 2.78 | 8.277 | 2.5546 | 29.57 | 4.8 | 9.7 | 2021-01-25
2021-01-26 | Click Here |  | 5.84 | 5.28 | 5.34 | 5.32 | 5.37 | 6.96 | 6.97 | 1.53 | 1.61 | 2.09 | 2.16 | 40 | 33 | 9 |  |  |  | 0.419 | 0.363 | 1.98 | 0.138 | 0.593 | 0.647 | 14.2 | 34.6 | 28.3 | 28.2 | 38.3 | 28.4 | 69.2 | 56.6 | 56.4 | 76.6 | 2.97 | 3.28 | 3.1 | 5.9 | 0.016 | 3.1 | 5.9 | 74.97 | 0.51656 | 53.9 | 89.8 | 0.268 | 0.0463 | 13.41 | 13.21 | 13.21 |  | 1.545 | 2.786 | 8.265 | 2.5766 | 30.04 | 4.8 | 9.7 | 2021-01-26
2021-01-27 | Click Here |  | 6.04 | 5.25 | 5.24 | 5.42 | 5.44 | 6.93 | 6.92 | 1.55 | 1.7 | 1.89 | 1.94 | 56 | 49 | 24 | 5 | 2 |  | 0.398 | 0.307 | 1.41 | 0.224 | 0.677 | 0.625 | 14.3 | 35.3 | 28.3 | 28.4 | 37.8 | 28.6 | 70.6 | 56.6 | 56.8 | 75.6 | 3.12 | 3.26 | 3 | 5.8 | 0.071 | 7.4 | 5.7 | 80.73 | 0.78295 | 55 | 90.1 | 0.259 | 0.0451 | 14.28 | 13.17 | 14.16 | 0.99 | 1.662 | 2.762 | 8.583 | 2.783 | 29.88 | 4.8 | 9.7 | 2021-01-27
2021-01-28 | Click Here |  | 5.97 | 5.17 | 5.33 | 5.4 | 5.42 | 6.9 | 6.88 | 1.6 | 1.81 | 1.9 | 1.85 | 53 | 47 | 19 | 3 | 2 |  | 0.346 | 0.301 | 1.47 | 0.113 | 0.594 | 0.675 | 14.5 | 35.1 | 28.3 | 28.6 | 37.4 | 29 | 70.2 | 56.6 | 57.2 | 74.8 | 3.03 | 3.26 | 3.1 | 5.9 | 0.051 | 6.9 | 5.9 | 79.38 | 0.81112 | 54.8 | 89.9 | 0.2602 | 0.0471 | 13.85 | 12.82 | 13.76 | 0.94 | 1.602 | 2.712 | 8.4 | 2.8111 | 29.73 | 4.8 | 9.7 | 2021-01-28
2021-01-29 | Click Here |  | 6.19 | 5.22 | 5.3 | 5.31 | 5.35 | 6.89 | 7.02 | 1.64 | 1.87 | 1.96 | 1.93 | 52 | 45 | 18 | 2 | 1 |  | 0.443 | 0.357 | 1.54 | 0.161 | 0.664 | 0.914 | 14 | 35.9 | 28.3 | 28.5 | 38 | 28 | 71.8 | 56.6 | 57 | 76 | 3 | 3.27 | 3 | 6.1 | 0.042 | 7.2 | 5.6 | 74.3 | 0.91634 | 54.6 | 87.4 | 0.2604 | 0.0583 | 13.08 | 12.02 | 13 | 0.98 | 1.541 | 2.709 | 8.057 | 2.8063 | 29.58 | 4.8 | 9.9 | 2021-01-29
2021-01-30 | Click Here |  | 6.27 | 5.25 | 5.12 | 5.33 | 5.36 | 6.71 | 6.84 | 1.61 | 1.86 | 1.94 | 1.91 | 53 | 46 | 16 | 1 |  |  | 0.433 | 0.342 | 1.16 | 0.141 | 0.49 | 0.483 | 14.2 | 36 | 28.7 | 29.2 | 37.7 | 28.4 | 72 | 57.4 | 58.4 | 75.4 | 3.05 | 3.19 | 3.1 | 5.9 | 0.028 | 7.4 | 5.6 | 74.86 | 0.72088 | 54.8 | 89.6 | 0.2602 | 0.0465 | 13.35 | 12.31 | 13.29 | 0.98 |  |  |  | 2.7609 | 28.75 | 4.8 | 9.9 | 2021-01-30
2021-01-31 | Click Here | [41 empty] | 73.27 | 0.72744 |  |  |  |  | 13.05 | 12.02 | 12.97 | 0.95 | 1.49 | 2.734 | 7.257 | 2.7674 |  | 4.8 | 10.1 | 2021-01-31
2021-02-01 | Click Here |  | 6.14 | 5.24 | 5.3 | 5.34 | 5.39 | 6.91 | 6.87 | 1.73 | 1.98 | 2.09 | 2.13 | 55 | 49 | 19 | 1 |  |  | 0.406 | 0.347 | 1.2 | 0.123 | 0.508 | 0.542 | 14.4 | 35.8 | 29.1 | 29.6 | 38.1 | 28.8 | 71.6 | 58.2 | 59.2 | 76.2 | 3.1 | 3.14 | 3 | 5.8 | 0.034 | 7.3 | 5.5 | 83.79 | 0.90532 | 55.1 | 89.9 | 0.2586 | 0.0441 | 13.5 | 12.41 | 13.39 | 0.98 | 1.593 | 2.753 | 5.666 | 3.0653 | 29.58 | 4.8 | 10.1 | 2021-02-01
2021-02-02 | Click Here |  | 6.06 | 5.25 | 5.28 | 5.31 | 5.4 | 6.89 | 6.85 | 1.69 | 1.82 | 2.11 | 2.09 | 40 | 33 | 16 | 1 |  |  | 0.344 | 0.291 | 1.14 | 0.107 | 0.767 | 0.874 | 14.2 | 34.6 | 30 | 27.9 | 37.5 | 28.4 | 69.2 | 60 | 55.8 | 75 | 3.01 | 3.3 | 3 | 6 | 0.029 | 7 | 5.6 | 92.61 | 0.90781 | 55.2 | 90.1 | 0.2584 | 0.0438 | 14.8 | 13.75 | 14.7 | 0.95 | 1.558 | 2.739 | 9.109 | 3.0578 | 30.04 | 4.8 | 10.1 | 2021-02-02
2021-02-03 | Click Here |  | 6.27 | 5.26 | 5.34 | 5.32 | 5.36 | 6.71 | 6.9 | 1.71 | 1.9 | 2.16 | 2.12 | 40 | 34 | 18 | 1 |  |  | 0.408 | 0.336 | 1.26 | 0.121 | 0.837 | 1.23 | 14.1 | 36.5 | 28.8 | 28.7 | 38.7 | 28.2 | 73 | 57.6 | 57.4 | 77.4 | 3.06 | 3.25 | 3 | 5.9 | 0.047 | 6.8 | 5.5 | 79.62 | 0.73402 | 55.6 | 89.9 | 0.258 | 0.044 | 13.8 | 12.8 | 13.78 | 0.98 | 1.541 | 2.759 | 8.25 | 2.824 | 30.48 | 4.8 | 10.3 | 2021-02-03
2021-02-04 | Click Here |  | 6.34 | 5.32 | 5.19 | 5.35 | 5.37 | 6.83 | 6.96 | 1.45 | 1.55 | 1.79 | 1.96 | 42 | 36 | 26 | 4 | 2 |  | 0.405 | 0.374 | 2.58 | 0.163 | 0.748 | 0.563 | 14.5 | 38 | 29.1 | 29.2 | 39.7 | 29 | 76 | 58.2 | 58.4 | 79.4 | 3.11 | 3.5 | 3.1 | 6 | 0.032 | 7.6 | 5.5 | 79.38 | 0.70936 | 52.6 | 87.1 | 0.2783 | 0.0599 | 13.96 | 12.92 | 13.86 | 0.94 | 1.582 | 2.761 | 8.446 | 2.7894 | 28.07 | 5 | 10.6 | 2021-02-04
2021-02-05 | Click Here |  | 5.89 | 5.36 | 5.27 | 5.43 | 5.4 | 7.43 | 7.35 | 1.5 | 1.61 | 2.13 | 2.16 | 40 | 32 | 18 | 1 |  |  | 0.401 | 0.338 | 2.82 | 0.349 | 0.543 | 0.538 | 14.7 | 35.2 | 29.1 | 29.1 | 42.6 | 29.4 | 70.4 | 58.2 | 58.2 | 85.2 | 3.06 | 3.28 | 3.1 | 5.9 | 0.036 | 7.4 | 5.5 | 57.33 | 0.020561 | 53 | 90 | 0.2755 | 0.0454 | 13.55 | 12.51 | 13.48 | 0.97 | 1.578 | 2.765 | 8.253 | 2.0806 | 30.51 | 4.7 | 10.6 | 2021-02-05
2021-02-06 | Click Here |  | 6.02 | 5.33 | 5.39 | 5.41 | 5.45 | 7.36 | 7.44 | 1.56 | 1.72 | 2.11 | 2.14 | 41 | 32 | 17 | 1 |  |  | 0.396 | 0.334 | 2.56 | 0.322 | 0.689 | 0.737 | 14.6 | 34.6 | 29 | 28.8 | 41.5 | 29.2 | 69.2 | 58 | 57.6 | 83 | 3.09 | 3.17 | 3 | 5.8i | 0.031 | 7.3 | 5.4 | 86.4 | 1.3467 | 53.2 | 90.4 | 0.2746 | 0.0441 | 12.33 | 11.25 | 12.21 | 0.96 | 1.519 | 2.775 | 5.751 | 3.4867 | 30.28 | 4.7 | 10.6 | 2021-02-06
2021-02-07 | Click Here |  | 6.27 | 5.28 | 5.33 | 5.31 | 5.36 | 6.93 | 7.37 | 1.59 | 1.83 | 1.87 | 1.9 | 40 | 33 | 21 | 2 |  |  | 0.324 | 0.286 | 2.47 | 0.216 | 0.761 | 0.974 | 14.1 | 35.3 | 28.8 | 29.1 | 42.2 | 28.2 | 70.6 | 57.6 | 58.2 | 84.4 | 3.07 | 3.16 | 3.1 | 5.9 | 0.036 | 6.7 | 5.3 | 82.62 | 0.958 | 53.5 | 90 | 0.2743 | 0.0444 | 13.84 | 12.03 | 13.88 | 1.85 | 1.588 | 2.776 | 5.851 | 3.118 | 32.22 | 4.7 | 10.6 | 2021-02-07
2021-02-08 | Click Here | [58 empty] | 2021-02-08
2021-02-09 | Click Here |  | 6.25 | 5.25 | 5.34 | 5.31 | 5.37 | 6.94 | 7.32 | 1.67 | 1.97 | 2.09 | 2.14 | 41 | 36 | 23 | 3 | 1 |  | 0.369 | 0.338 | 2.55 | 0.183 | 0.567 | 0.477 | 14.4 | 35.1 | 28.7 | 28.6 | 41.3 | 28.8 | 70.2 | 57.4 | 57.2 | 82.6 | 3.12 | 3.24 | 3 | 6 | 0.033 | 7.2 | 5.4 | 74.97 | 0.4999 | 50.6 | 86.9 | 0.2957 | 0.061 | 12.73 | 12.56 | 12.56 |  | 1.456 | 2.776 | 5.867 | 2.7099 | 28.62 | 4.7 | 10.6 | 2021-02-09
2021-02-10 | Click Here |  | 5.84 | 5.31 | 5.24 | 5.35 | 5.37 | 7.51 | 6.92 | 1.45 | 1.62 | 1.99 | 2.04 | 40 | 33 | 18 | 1 |  |  | 0.402 | 0.318 | 1.97 | 0.339 | 0.458 | 0.475 | 14.3 | 36 | 28.7 | 28.6 | 39.2 | 28.6 | 72 | 57.4 | 57.2 | 78.4 | 3.17 | 3.25 | 3.1 | 5.9 | 0.017 | 7.5 | 5.9 | 70.56 | 0.67593 | 54.8 | 92.3 | 0.2613 | 0.0348 | 12.67 | 11.54 | 12.52 | 0.98 | 1.35 | 2.776 | 5.953 | 2.7759 | 30.28 | 4.7 | 10.6 | 2021-02-10
2021-02-11 | Click Here |  | 6.01 | 5.33 | 5.41 | 5.36 | 5.44 | 7.12 | 7.83 | 1.54 | 1.78 | 2.02 | 2.1 | 40 | 32 | 19 | 1 |  |  | 0.414 | 0.325 | 1.93 | 0.341 | 0.529 | 0.58 | 14.4 | 35.6 | 28.1 | 29 | 40.1 | 28.8 | 71.2 | 56.2 | 58 | 80.2 | 2.98 | 3.5 | 3 | 5.8 | 0.021 | 7.3 | 5.3 | 88.2 | 1.0668 | 54.5 | 92 | 0.2592 | 0.0355 | 13.28 | 13.22 | 12.22 | 1 | 1.432 | 2.772 | 5.815 | 3.2768 | 30.04 | 4.7 | 10.3 | 2021-02-11
2021-02-12 | Click Here |  | 6 | 5.29 | 5.36 | 5.33 | 5.4 | 7.21 | 7.17 | 1.5 | 1.74 | 2.06 | 2.15 | 42 | 36 | 21 | 2 |  |  | 0.367 | 0.317 | 1.88 | 0.219 | 0.412 | 0.474 | 14.1 | 34.6 | 28.7 | 29.3 | 41.1 | 28.2 | 69.2 | 57.4 | 58.6 | 82.2 | 3.29 | 3.17 | 3 | 5.9 | 0.029 | 7.2 | 6.3 | 79.27 | 0.69699 | 55.1 | 91.7 | 0.2571 | 0.0378 | 13.44 | 12.38 | 13.37 | 0.99 | 1.591 | 2.768 | 5.733 | 2.907 | 29.16 | 4.7 | 10.3 | 2021-02-12
2021-02-13 | Click Here |  | 5.94 | 5.31 | 5.35 | 5.39 | 5.42 | 7.14 | 7.1 | 1.63 | 1.94 | 2.09 | 2.16 | 54 | 47 | 21 | 2 |  |  | 0.29 | 0.315 | 1.98 | 0.212 | 0.496 | 0.581 | 14.4 | 35.1 | 27.9 | 28.3 | 38.8 | 28.8 | 70.2 | 55.8 | 56.6 | 77.6 | 3.12 | 3.34 | 2.9 | 6 | 0.037 | 6.7 | 5.9 | 81.59 | 0.83373 | 54.6 | 90.6 | 0.2712 | 0.0413 | 13.3 | 12.21 | 13.17 | 0.96 |  |  |  | 3.0337 | 30.07 | 4.7 | 10.3 | 2021-02-13
2021-02-14 | Click Here | [58 empty] | 2021-02-14
2021-02-15 | Click Here |  | 6.04 | 5.32 | 5.3 | 5.37 | 5.46 | 7.12 | 7.06 | 1.59 | 1.78 | 2.05 | 2.11 | 44 | 36 | 20 | 1 |  |  | 0.341 | 0.306 | 1.95 | 0.189 | 0.881 | 0.966 | 14.3 | 34.6 | 28.1 | 28.4 | 39.9 | 28.6 | 69.2 | 56.2 | 56.8 | 79.8 | 2.94 | 3.15 | 3.1 | 5.9 | 0.029 | 3.1 | 5.9 | 72.76 | 0.41719 | 54.5 | 90.4 | 0.2716 | 0.0421 | 13.67 | 12.67 | 13.61 | 0.94 | 1.659 | 2.766 | 7.305 | 2.6072 | 30.04 | 4.7 | 10.3 | 2021-02-15
2021-02-16 | Click Here |  | 5.91 | 5.31 | 5.32 | 5.41 | 5.43 | 7.08 | 7.08 | 1.36 | 1.52 | 1.76 | 1.74 | 48 | 39 | 64 | 14 | 9 |  | 0.452 | 0.316 | 4.05 | 0.894 | 0.864 | 0.967 | 14.1 | 39 | 28.9 | 29.9 | 40.8 | 28.2 | 78 | 57.8 | 59.8 | 81.6 | 3.1 | 3.34 | 3.1 | 6 | 0.013 | 3.1 | 6 | 83.79 | 1.1269 | 55 | 92.6 | 0.2594 | 0.0331 | 13.87 | 12.05 | 13.02 | 0.97 | 1.625 | 2.763 | 5.665 | 3.1569 | 30.28 | 4.7 | 10.3 | 2021-02-16
2021-02-17 | Click Here |  | 6.02 | 5.36 | 5.31 | 5.48 | 5.53 | 7.25 | 7.15 | 1.64 | 1.93 | 1.96 | 2.12 | 50 | 42 | 20 | 8 | 5 |  | 0.371 | 0.319 | 1.65 | 0.2 | 0.812 | 0.791 | 14.1 | 36.5 | 28.8 | 29.3 | 40.6 | 28.2 | 73 | 57.6 | 58.6 | 81.2 | 3.21 | 3.4 | 3.1 | 5.9 | 0.041 | 6.8 | 5.5 | 83.67 | 0.72231 | 54.5 | 90.2 | 0.2634 | 0.0446 | 13.79 | 12.78 | 13.73 | 0.95 | 1.613 | 2.768 | 8.727 | 2.9723 | 29.64 | 4.7 | 10.3 | 2021-02-17
2021-02-18 | Click Here |  | 5.95 | 5.38 | 5.41 | 5.4 | 5.47 | 7.14 | 7.18 | 1.5 | 1.69 | 1.89 | 1.93 | 51 | 44 | 29 | 7 | 4 |  | 0.304 | 0.321 | 2.96 | 0.174 | 0.612 | 0.599 | 14.6 | 35.9 | 28.6 | 29 | 41.3 | 29.2 | 71.8 | 57.2 | 58 | 82.6 | 3.29 | 3.55 | 3 | 5.9 | 0.023 | 6.7 | 5.4 | 79.38 | 0.47944 | 54.1 | 89.9 | 0.2614 | 0.0492 | 14.33 | 13.45 | 13.45 |  | 1.664 | 2.759 | 7.915 | 2.6794 | 29.44 | 4.7 | 10.3 | 2021-02-18
2021-02-19 | Click Here |  | 5.97 | 5.19 | 5.36 | 5.3 | 5.24 | 6.91 | 7.2 | 1.74 | 2 | 2.11 | 2 | 50 | 44 | 10 | 2 |  |  | 0.414 | 0.321 | 0.766 | 0.12 | 0.716 | 0.758 | 14.5 | 37.2 | 28.8 | 29.4 | 41.1 | 29 | 74.4 | 57.6 | 58.8 | 82.2 | 3.24 | 3.47 | 3 | 6 | 0.038 | 7.2 | 5.3 | 85.55 | 0.96619 | 54.4 | 89 | 0.2611 | 0.0502 | 14.09 | 12.19 | 14.13 | 1.94 | 1.646 | 2.766 | 7.599 | 3.1862 | 28.69 | 4.7 | 10.3 | 2021-02-19
2021-02-20 | Click Here |  | 6.21 | 5.22 | 5.35 | 5.23 | 5.28 | 6.79 | 7.06 | 1.46 | 1.63 | 1.71 | 1.82 | 49 | 43 | 13 |  |  |  | 0.532 | 0.317 | 0.765 | 0.15 | 0.71 | 0.556 | 14.6 | 35.7 | 29.4 | 29.3 | 39.9 | 29.2 | 71.4 | 58.8 | 58.6 | 79.8 | 3.14 | 3.41 | 3.1 | 5.9 | 0.047 | 3.1 | 5.9 | 73.4 | 0.73378 | 51.3 | 89.9 | 0.2896 | 0.046 | 12.47 | 11.32 | 12.29 | 0.97 |  |  |  | 2.9438 | 30.2 | 4.4 | 10.3 | 2021-02-20
2021-02-21 | Click Here | [41 empty] | 76.34 | 0.53066 |  |  |  |  | 12.8 | 12.6 | 12.6 |  |  |  |  | 2.7507 |  | 4.4 | 10.7 | 2021-02-21
2021-02-22 | Click Here |  | 6.14 | 5.17 | 5.2 | 5.29 | 5.36 | 6.95 | 7.17 | 1.68 | 1.93 | 1.95 | 2.01 | 47 | 40 | 11 |  |  |  | 0.367 | 0.314 | 0.529 | 0.109 | 0.623 | 0.551 | 14.5 | 36.2 | 28.8 | 29.1 | 40.4 | 29 | 72.4 | 57.6 | 58.2 | 80.8 | 3.18 | 3.5 | 3 | 5.8 | 0.051 | 7 | 5.2 | 90.39 | 0.74858 | 51.9 | 90.4 | 0.2841 | 0.0433 | 14.54 | 13.64 | 14.63 | 0.99 | 1.632 | 2.772 | 8.279 | 3.0086 | 30.53 | 4.4 | 10.7 | 2021-02-22
2021-02-23 | Click Here |  | 6.19 | 5.26 | 5.32 | 5.36 | 5.41 | 7.09 | 7.18 | 1.79 | 1.98 | 2.09 | 2.21 | 45 | 38 | 9 |  |  |  | 0.286 | 0.304 | 0.328 | 0.096 | 0.426 | 0.564 | 14.2 | 35.8 | 28.4 | 28.8 | 41.3 | 28.4 | 71.6 | 56.8 | 57.6 | 82.6 | 3.1 | 3.42 | 2.9 | 5.9 | 0.037 | 6.8 | 5.1 | 70.56 | 0.43636 | 52.3 | 92.6 | 0.2792 | 0.031 | 13.69 | 12.63 | 13.62 | 0.99 | 1.644 | 2.769 | 7.653 | 2.5364 | 30.34 | 4.4 | 10.7 | 2021-02-23
2021-02-24 | Click Here |  | 6.18 | 5.23 | 5.28 | 5.34 | 5.35 | 6.81 | 7.08 | 1.74 | 1.96 | 2.01 | 2.06 | 46 | 36 | 10 |  |  |  | 0.36 | 0.314 | 0.419 | 0.06 | 0.664 | 0.956 | 14.5 | 36.7 | 29.8 | 30.3 | 41.2 | 29 | 73.4 | 59.6 | 60.6 | 82.4 | 3.17 | 3.34 | 3 | 6 | 0.028 | 6.5 | 5.2 | 79.27 | 0.85305 | 52.5 | 87.6 | 0.279 | 0.0575 | 13.55 | 12.57 | 13.55 | 0.98 | 1.642 | 2.768 | 8.058 | 2.863 | 29.82 | 4.4 | 10.7 | 2021-02-24
2021-02-25 | Click Here |  | 6.15 | 5.2 | 5.15 | 5.31 | 5.34 | 6.79 | 7.07 | 1.55 | 1.82 | 1.87 | 1.92 | 47 | 38 | 14 | 1 |  |  | 0.348 | 0.246 | 0.811 | 0.079 | 0.61 | 0.503 | 14.5 | 37.2 | 29.6 | 30.3 | 40.9 | 29 | 74.4 | 59.2 | 60.3 | 81.8 | 3.22 | 3.29 | 3 | 6.1 | 0.036 | 6.4 | 5.2 | 77.18 | 0.60273 | 52.5 | 88.1 | 0.2792 | 0.0548 | 13.51 | 13.36 | 13.36 |  | 1.621 | 2.77 | 8.166 | 2.6227 | 29.17 | 4.4 | 11 | 2021-02-25
2021-02-26 | Click Here |  | 5.94 | 5.17 | 5.22 | 5.24 | 5.27 | 6.87 | 6.98 | 1.48 | 1.68 | 1.82 | 1.8 | 45 | 37 | 11 |  |  |  | 0.383 | 0.236 | 0.972 | 0.158 | 0.732 | 0.56 | 15 | 35.8 | 29.3 | 30 | 41.3 | 30 | 71.6 | 58.6 | 60 | 82.6 | 3.26 | 3.19 | 3 | 6 | 0.012 | 7.3 | 5.3 | 74.97 | 0.61053 | 52.2 | 88.9 | 0.2816 | 0.0509 | 13.91 | 12.89 | 13.86 | 0.97 | 1.676 | 2.766 | 8.494 | 2.6405 | 31.45 | 4.2 | 11 | 2021-02-26
2021-02-27 | Click Here |  | 5.98 | 5.21 | 5.19 | 5.23 | 5.36 | 7.02 | 7.04 | 1.51 | 1.76 | 2.04 | 2.02 | 41 | 34 | 10 |  |  |  | 0.367 | 0.259 | 0.881 | 0.123 | 0.525 | 0.491 | 14.8 | 35 | 29.5 | 30.6 | 39.8 | 29.6 | 70 | 59 | 61.2 | 79.6 | 3.12 | 3.33 | 3.1 | 5.9 | 0.016 | 7.2 | 5.2 | 82.68 | 0.67669 | 52.4 | 89.2 | 0.2789 | 0.0481 | 14.44 | 13.47 | 14.44 | 0.97 | 1.591 | 2.771 | 8.693 | 2.7867 | 30.51 | 4.2 | 11.3 | 2021-02-27
2021-02-28 | Click Here | [58 empty] | 2021-02-28
2021-03-01 | Click Here |  | 6.17 | 5.24 | 5.18 | 5.33 | 5.35 | 6.93 | 7.3 | 1.7 | 1.99 | 2.19 | 2.17 | 42 | 36 | 13 |  |  |  | 0.373 | 0.241 | 0.862 | 0.079 | 0.761 | 0.736 | 14.6 | 35.9 | 28.8 | 29.2 | 41.7 | 29.2 | 71.8 | 57.6 | 58.4 | 83.4 | 3.15 | 3.32 | 3 | 6 | 0.022 | 6.5 | 5 | 82.69 | 0.72787 | 52.6 | 87.7 | 0.2787 | 0.056 | 14.3 | 13.37 | 14.35 | 0.98 | 1.661 | 2.795 | 8.789 | 2.8079 | 32.21 | 4.2 | 11.3 | 2021-03-01
2021-03-02 | Click Here |  | 6.26 | 5.29 | 5.26 | 5.35 | 5.38 | 6.79 | 7.23 | 1.5 | 1.69 | 1.84 | 1.9 | 41 | 35 | 18 | 1 |  |  | 0.446 | 0.246 | 0.905 | 0.161 | 0.618 | 0.506 | 15 | 37.4 | 28.6 | 29.1 | 41.3 | 30 | 74.8 | 57.2 | 58.2 | 82.6 | 3.18 | 3.31 | 3 | 5.9 | 0.027 | 7 | 4.8 | 81.59 | 0.7335 | 53.3 | 90.4 | 0.2725 | 0.0434 | 14.29 | 13.26 | 14.21 | 0.95 | 1.651 | 2.818 | 8.593 | 2.7935 | 26.31 | 4.2 | 11.3 | 2021-03-02
2021-03-03 | Click Here |  | 5.86 | 5.2 | 5.25 | 5.26 | 5.33 | 7.05 | 7.02 | 1.67 | 1.77 | 1.99 | 2.04 | 53 | 45 | 20 | 4 |  |  | 0.366 | 0.287 | 1.26 | 0.165 | 0.527 | 0.537 | 15 | 37.3 | 29.2 | 29.5 | 41.3 | 30 | 74.6 | 58.4 | 59 | 82.6 | 3.1 | 3.25 | 3.1 | 6.1 | 0.013 | 7.1 | 5.3 | 72.76 | 0.36178 | 53.1 | 89.6 | 0.2746 | 0.0475 | 14.66 | 13.64 | 14.61 | 0.97 | 1.673 | 2.832 | 8.899 | 2.4218 | 30.98 | 4.2 | 11.3 | 2021-03-03
2021-03-04 | Click Here |  | 5.91 | 5.23 | 5.2 | 5.28 | 5.36 | 7.07 | 7.03 | 1.57 | 1.72 | 2.01 | 2.03 | 50 | 43 | 16 | 1 |  |  | 0.308 | 0.226 | 0.944 | 0.159 | 0.577 | 0.593 | 14.8 | 37.1 | 29.5 | 29.3 | 40.8 | 29.6 | 74.2 | 59 | 58.6 | 81.6 | 2.97 | 3.22 | 3 | 5.9 | 0.015 | 7 | 5.2 | 88.2 | 0.75597 | 53.5 | 90 | 0.2738 | 0.0467 | 15.09 | 14.07 | 15.05 | 0.98 | 1.665 | 3.031 | 9.211 | 2.846 | 30.28 | 4.2 | 11.3 | 2021-03-04
2021-03-05 | Click Here |  | 5.99 | 5.19 | 5.33 | 5.32 | 5.39 | 7.04 | 6.97 | 1.67 | 1.94 | 2.09 | 2.12 | 50 | 46 | 14 |  |  |  | 0.314 | 0.247 | 0.719 | 0.104 | 0.546 | 0.604 | 15.6 | 35 | 29.3 | 29.6 | 40.8 | 31.2 | 70 | 58.6 | 59.2 | 81.6 | 3.06 | 3.32 | 3.1 | 6 | 0.029 | 7.4 | 5.1 | 85.55 | 0.5143 | 55.8 | 89.9 | 0.2534 | 0.0463 | 14.93 | 14.8 | 14.8 |  | 1.629 | 3.091 | 9.315 | 2.6243 | 30.68 | 4.2 | 11.3 | 2021-03-05
2021-03-06 | Click Here |  | 6.04 | 5.24 | 5.31 | 5.29 | 5.33 | 7.34 | 7.15 | 1.72 | 1.98 | 2.07 | 2.12 | 51 | 46 | 16 | 1 |  |  | 0.198 | 0.243 | 0.791 | 0.113 | 0.592 | 0.667 | 15.4 | 34.8 | 29.1 | 29.8 | 40.5 | 30.8 | 69.6 | 58.2 | 59.6 | 81 | 3.02 | 3.31 | 3 | 5.9 | 0.039 | 7.2 | 5 | 83.79 | 0.73366 | 56.1 | 90.1 | 0.2502 | 0.043 | 14.45 | 13.52 | 14.47 | 0.95 |  |  |  | 2.8137 | 30.6 | 4.2 | 11.3 | 2021-03-06
2021-03-07 | Click Here | [58 empty] | 2021-03-07
2021-03-08 | Click Here |  | 5.79 | 5.16 | 5.25 | 5.28 | 5.34 | 7.37 | 6.96 | 1.68 | 1.86 | 2.05 | 2.09 | 51 | 44 | 25 | 2 |  |  | 0.348 | 0.241 | 1.67 | 0.236 | 0.76 | 0.775 | 15.5 | 37.4 | 29.3 | 29.5 | 41 | 31 | 74.8 | 58.6 | 59 | 82 | 3.02 | 3.32 | 3.1 | 5.8 | 0.015 | 7.5 | 5 | 79.38 | 0.39315 | 54.1 | 90.5 | 0.2661 | 0.043 | 15.28 | 15.28 | 14.34 | 0.94 | 1.573 | 2.981 | 9.701 | 2.5131 | 32.39 | 4.2 | 11.3 | 2021-03-08
2021-03-09 | Click Here |  | 5.82 | 5.23 | 5.17 | 5.26 | 5.4 | 7.38 | 7.44 | 1.65 | 1.84 | 2.04 | 2.06 | 50 | 43 | 19 | 1 |  |  | 0.351 | 0.265 | 1.18 | 0.244 | 0.594 | 0.63 | 15.4 | 36.6 | 29.1 | 29.3 | 40.4 | 30.8 | 73.2 | 58.2 | 58.6 | 80.8 | 2.98 | 3.38 | 3 | 5.9 | 0.18 | 7.4 | 5 | 88.2 | 0.72589 | 54.3 | 90.7 | 0.2657 | 0.0423 | 15.13 | 14.12 | 15.06 | 0.94 | 1.589 | 2.802 | 9.526 | 2.8359 | 30.28 | 4.2 | 11.3 | 2021-03-09
2021-03-10 | Click Here |  | 6.04 | 5.21 | 5.2 | 5.37 | 5.4 | 7.38 | 7.19 | 1.72 | 1.94 | 2.09 | 2.13 | 49 | 41 | 9 |  |  |  | 0.271 | 0.225 | 0.924 | 0.121 | 0.438 | 0.529 | 15.6 | 36.4 | 28.6 | 29 | 38.6 | 31.2 | 72.8 | 57.2 | 58 | 77.2 | 2.92 | 3.46 | 3.1 | 5.9 | 0.06 | 7.5 | 5 | 75.29 | 0.26077 | 54.3 | 90.8 | 0.2652 | 0.0418 | 13.72 | 13.56 | 13.56 |  | 1.553 | 2.829 | 7.801 | 2.5208 | 30.52 | 4.2 | 11.3 | 2021-03-10
2021-03-11 | Click Here |  | 6.04 | 5.24 | 5.17 | 5.37 | 5.41 | 7.38 | 7.44 | 1.79 | 2 | 2.14 | 2.33 | 49 | 42 | 15 | 1 |  |  | 0.314 | 0.281 | 0.901 | 0.112 | 0.476 | 0.599 | 15.8 | 37.4 | 29.1 | 30.8 | 41.5 | 31.6 | 74.8 | 58.2 | 61.6 | 83 | 2.98 | 3.53 | 3 | 6 | 0.027 | 7.4 | 5.1 | 85.99 | 0.61993 | 54.5 | 91.7 | 0.2631 | 0.0364 | 14.38 | 13.37 | 14.35 | 0.98 | 1.557 | 2.822 | 6.617 | 2.9199 | 29.74 | 4.2 | 11.3 | 2021-03-11
2021-03-12 | Click Here |  | 6.11 | 5.21 | 5.18 | 5.29 | 5.35 | 6.81 | 7.39 | 1.81 | 2.04 | 2.16 | 2.26 | 48 | 43 | 16 | 1 |  |  | 0.304 | 0.256 | 0.913 | 0.121 | 0.572 | 0.603 | 15.8 | 37.5 | 28.9 | 29 | 41 | 31.6 | 75 | 57,8 | 58 | 82 | 3.01 | 3.46 | 3.1 | 5.9 | 0.033 | 7.4 | 5 | 77.17 | 0.41622 | 54.7 | 91.3 | ,2629 | 0.0368 | 15.34 | 14.5 | 15.45 | 0.95 | 1.568 | 2.801 | 10 | 2.4162 | 30.08 | 4.2 | 11.3 | 2021-03-12
2021-03-13 | Click Here |  | 6.19 | 5.27 | 5.18 | 5.33 | 5.39 | 6.93 | 7.45 | 1.59 | 1.82 | 1.91 | 1.8 | 49 | 43 | 17 | 1 |  |  | 0.342 | 0.27 | 0.829 | 0.1 | 0.63 | 0.76 | 15.5 | 37.1 | 28.7 | 29 | 40.4 | 31 | 74.2 | 57.4 | 58 | 80.8 | 2.99 | 3.36 | 3 | 6 | 0.029 | 7.2 | 5 | 85.99 | 1.1976 | 52.5 | 86.8 | 0.2792 | 0.0611 | 13.86 | 12.81 | 13.81 | 1 | 1.45 | 2.819 | 6.053 | 3.0476 | 29.79 | 4.2 | 11.6 | 2021-03-13
2021-03-14 | Click Here | [41 empty] | 82.62 | 0.89211 |  |  |  |  | 14.36 | 13.58 | 14.52 | 0.94 | 1.467 | 2.808 | 6.734 | 2.7621 |  | 4.2 | 11.6 | 2021-03-14
2021-03-15 | Click Here |  | 6.07 | 5.24 | 5.3 | 5.37 | 5.42 | 7.19 | 7.24 | 1.54 | 1.77 | 1.9 | 1.83 | 51 | 46 | 19 | 2 |  |  | 0.304 | 0.261 | 0.924 | 0.127 | 0.941 | 1.26 | 15.6 | 36.5 | 28.4 | 29.6 | 39.8 | 31.2 | 73 | 56.8 | 59.2 | 79.2 | 3.01 | 3.51 | 3 | 5.9 | 0.031 | 7.3 | 5.1 | 97.84 | 1.1702 | 53 | 87.7 | 0.2761 | 0.0548 | 16.6 | 15.53 | 16.7 | 0.97 | 1.59 | 2.79 | 10 | 2.8602 | 30.08 | 4.2 | 11.6 | 2021-03-15
2021-03-16 | Click Here |  | 6.11 | 5.35 | 5.35 | 5.41 | 5.5 | 7.1 | 7.26 | 1.45 | 1.7 | 1.94 | 1,69 | 49 | 43 | 17 |  |  |  | 0.291 | 0.267 | 1.47 | 0.316 | 0.725 | 0.789 | 15.9 | 36.4 | 29.3 | 29.6 | 42 | 31.8 | 72.8 | 58.6 | 59.2 | 84 | 2.86 | 3.42 | 3 | 6.1 | 0.064 | 7.4 | 5.3 | 90.4 | 1.1662 | 53.8 | 89 | 0.2689 | 0.0505 | 15.34 | 14.42 | 15.35 | 0.93 | 1.639 | 2.761 | 9.296 | 2.8462 | 29.71 | 4.2 | 11.6 | 2021-03-16
2021-03-17 | Click Here |  | 6.1 | 5.3 | 5.32 | 5.33 | 5.39 | 6.79 | 7.04 | 1.44 | 1.63 | 1.87 | 1.44 | 50 | 44 | 27 | 4 | 1 |  | 0.379 | 0.289 | 1.93 | 0.316 | 0.717 | 0.709 | 16 | 38 | 29.6 | 29.9 | 42 | 32 | 76 | 59.2 | 59.8 | 84 | 2.91 | 3.41 | 3 | 5.9 | 0.058 | 7.4 | 5 | 81.36 | 0.75165 | 54.3 | 88.4 | 0.2652 | 0.0535 | 14.94 | 13.93 | 14.92 | 0.99 | 1.713 | 2.78 | 9.928 | 2.6517 | 29.41 | 4.2 | 11.6 | 2021-03-17
2021-03-18 | Click Here |  | 5.98 | 5.17 | 5.16 | 5.25 | 5.3 | 6.83 | 7.06 | 1.66 | 1.87 | 2 | 2.16 | 49 | 42 | 31 | 5 | 2 |  | 0.36 | 0.276 | 1.9 | 0.314 | 1.45 | 1.5 | 16 | 35.2 | 29.6 | 30 | 42.2 | 32 | 70.4 | 59.2 | 60 | 84.4 | 2.95 | 3.39 | 3 | 5.8 | 0.063 | 7.2 | 4.9 | 88.2 | 0.64595 | 54.5 | 86.9 | 0.263 | 0.061 | 15.27 | 14.22 | 15.17 | 0.95 | 1.639 | 2.776 | 9.81 | 2.8159 | 32.44 | 3.7 | 12 | 2021-03-18
2021-03-19 | Click Here |  | 5.87 | 5.21 | 5.12 | 5.31 | 5.29 | 6.89 | 7.06 | 1.65 | 1.81 | 1.91 | 2.12 | 49 | 42 | 20 | 6 |  |  | 0.36 | 0.287 | 2.85 | 0.704 | 0.904 | 0.77 | 16.1 | 35.1 | 29 | 29.2 | 42.3 | 32.2 | 70.2 | 58 | 58.4 | 84.6 | 3.02 | 3.38 | 3 | 5.8 | 0.017 | 7.2 | 4.9 | 90.4 | 1.0899 | 54.2 | 90 | 0.2653 | 0.0457 | 14.87 | 13.96 | 14.85 | 0.89 | 1.576 | 2.677 | 9.635 | 2.9399 |  | 3.7 | 12.3 | 2021-03-19
2021-03-20 | Click Here |  | 5.88 | 5.27 | 5.22 | 5.32 | 5.41 | 7.02 | 6.87 | 1.62 | 1.84 | 1.96 | 2.01 | 48 | 41 | 17 | 1 |  |  | 0.313 | 0.274 | 0.897 | 0.091 | 0.586 | 0.6 | 16.2 | 35.3 | 30.1 | 28.9 | 41.2 | 32.4 | 70.6 | 60.2 | 57.8 | 82.4 | 2.95 | 3.29 | 3.1 | 6 | 0.022 | 7.2 | 5.1 | 85.99 | 0.77255 | 54.1 | 90.2 | 0.2662 | 0.0448 | 14.93 | 13.93 | 14.97 | 1.04 |  |  |  | 2.8026 | 30.04 | 3.7 | 12.3 | 2021-03-20
2021-03-21 | Click Here | [58 empty] | 2021-03-21
2021-03-22 | Click Here |  | 6.1 | 5.23 | 5.15 | 5.23 | 5.25 | 6.84 | 7 | 1.52 | 1.85 | 1.87 | 1.89 | 49 | 43 | 21 | 1 |  |  | 0.301 | 0.264 | 1.03 | 0.214 | 0.862 | 0.774 | 16 | 37 | 28.6 | 29.3 | 42.2 | 32 | 74 | 57.2 | 58.6 | 84.4 | 2.98 | 3.34 | 3 | 5.9 | 0.037 | 7.9 | 5 | 95.83 | 1.1045 | 54.3 | 85.2 | 0.266 | 0.0694 | 15.62 | 13.88 | 15.82 | 1.94 | 1.635 | 2.779 | 9.888 | 3.1345 | 32.26 | 3.7 | 12.3 | 2021-03-22
2021-03-23 | Click Here |  | 6.16 | 5.22 | 5.13 | 5.25 | 5.26 | 6.79 | 6.98 | 1.53 | 1.79 | 1.96 | 2.01 | 50 | 44 | 20 | 1 |  |  | 0.333 | 0.261 | 1.51 | 0.31 | 0.699 | 0.714 | 16 | 33.8 | 28.2 | 28.3 | 41.2 | 32 | 67.6 | 56.4 | 56.6 | 82.4 | 3.01 | 3.35 | 3 | 5.9 | 0.055 | 7.4 | 4.8 | 94.82 | 0.97362 | 52.6 | 87.2 | 0.2788 | 0.0595 | 15.35 | 14.38 | 15.33 | 0.95 | 1.66 | 2.774 | 10 | 2.9936 | 25.47 | 3.4 | 12.5 | 2021-03-23
2021-03-24 | Click Here |  | 5.88 | 5.23 | 5.25 | 5.31 | 5.42 | 7.07 | 7.02 | 1.58 | 1.82 | 2.02 | 2.07 | 46 | 39 | 17 | 1 |  |  | 0.323 | 0.268 | 2.03 | 0.483 | 0.878 | 0.799 | 12 | 27.1 | 21.5 | 28.6 | 41.9 | 24 | 54.2 | 43 | 57.2 | 83.8 | 3.01 | 3.36 | 3 | 5.9 | 0.037 | 7.6 | 5.9 | 81.58 | 0.5701 | 54.9 | 89.8 | 0.2599 | 0.0467 | 15.19 | 14.19 | 15.15 | 0.97 | 1.645 | 2.771 | 10 | 2.6101 | 29.57 | 3.4 | 12.5 | 2021-03-24
2021-03-25 | Click Here |  | 5.72 | 5.32 | 5.25 | 5.37 | 5.412 | 7.08 | 7.1 | 1.62 | 1.85 | 2.11 | 2.08 | 47 | 39 | 40 | 8 |  |  | 0.361 |  | 3.06 | 0.597 | 0.716 | 0.712 | 12.3 | 25.9 | 20.7 | 21.2 | 35.3 | 24.6 | 51.8 | 41.4 | 42.4 | 70.6 | 2.99 | 3.46 | 3 | 5.8 | 0.045 | 7.7 | 4.9 | 94.81 | 0.88618 | 54.1 | 89.9 | 0.2666 | 0.046 | 15.53 | 14.61 | 15.56 | 0.96 | 1.617 | 2.772 | 9.925 | 2.9462 | 27.7 | 3.4 | 12.5 | 2021-03-25
2021-03-26 | Click Here |  | 5.87 | 5.21 | 5.33 | 5.33 | 5.39 | 6.82 | 6.41 | 1.59 | 1.78 | 1.94 | 2.1 | 51 | 42 | 29 | 6 |  |  | 0.426 |  | 2.92 | 0.413 | 0.926 | 1.94 | 12.7 | 29.2 | 24.1 | 24.7 | 36.2 | 25.4 | 58.4 | 48.2 | 49.4 | 72.4 | 3.03 | 3.52 | 2.9 | 5.8 | 0.069 | 7.5 | 4.8 | 79.18 | 0.66587 | 54.6 | 90.4 | 0.2634 | 0.0434 | 15.02 | 14.12 | 15.09 | 0.97 | 1.573 | 2.767 | 9.987 | 2.5459 | 27.96 | 3.4 | 12 | 2021-03-26
2021-03-27 | Click Here |  | 5.94 | 5.34 | 5.77 | 5.4 | 5.47 | 7.51 | 7.62 | 1.54 | 1.77 | 1.92 | 2.08 | 49 | 42 | 36 | 4 | 1 |  | 0.514 |  | 3.12 | 0.167 | 0.371 | 0.462 | 13.1 | 29.9 | 25.2 | 25.8 | 37.3 | 26.2 | 58.8 | 50.4 | 51.6 | 74.6 | 3.1 | 3.45 | 3.1 | 6 | 0.043 | 7.4 | 4.7 | 97.02 | 1.0904 | 54.1 | 89.8 | 0.2647 | 0.0464 | 15.28 | 14.44 | 15.38 | 0.094 |  |  |  | 3.0503 | 31.38 | 3.4 | 12 | 2021-03-27
2021-03-28 | Click Here | [58 empty] | 2021-03-28
2021-03-29 | Click Here |  | 5.9 | 5.21 | 5.26 | 5.28 | 5.33 | 6.83 | 6.74 | 1.61 | 1.77 | 2.08 | 2 | 56 | 48 | 47 | 10 |  |  | 0.398 |  | 2.75 | 0.68 | 1.04 | 0.886 | 16.1 | 36.9 | 29.5 | 29.8 | 41.6 | 32.2 | 73.8 | 59 | 59.6 | 83.2 | 3.05 | 3.25 | 3.1 | 5.9 | 0.069 | 7.5 | 5 | 90.41 | 0.85936 | 51.6 | 89.2 | 0.2866 | 0.0496 | 14.91 | 14.06 | 15.02 | 0.96 | 1.562 | 2.77 | 9.403 | 2.9194 | 31.92 | 3.4 | 12 | 2021-03-29
2021-03-30 | Click Here |  | 5.84 | 5.18 | 5.39 | 5.28 | 5.35 | 6.92 | 6.9 | 1.65 | 1.83 | 2.01 | 1.96 | 49 | 41 | 36 | 4 |  |  | 0.46 | 0.271 | 2.86 | 0.538 | 0.846 | 0.783 | 16.5 | 38.2 | 29.6 | 30.3 | 42.3 | 33 | 76.4 | 59.2 | 60.6 | 84.6 | 2.91 | 3.32 | 3 | 5.9 | 0.019 | 8.2 | 4.7 | 101.43 | 1.1005 | 58.2 | 89.3 | 0.2348 | 0.0488 | 15.68 | 14.71 | 15.68 | 0.97 | 1.685 | 2.763 | 10 | 3.1305 | 31.92 | 3.7 | 12 | 2021-03-30
2021-03-31 | Click Here |  | 6.14 | 5.25 | 5.18 | 5.33 | 5.27 | 7.01 | 7.18 | 1.61 | 1.81 | 1.98 | 1.92 | 49 | 43 | 30 | 2 |  |  | 0.422 | 0.257 | 2.01 | 0.419 | 0.793 | 0.774 | 16 | 38.7 | 29.8 | 30.6 | 46.8 | 32 | 77.4 | 59.6 | 61.2 | 93.6 | 2.95 | 3.27 | 3 | 5.8 | 0.024 | 7.6 | 4.8 | 94.82 | 1.0173 | 58.6 | 89.7 | 0.2342 | 0.0484 | 15.15 | 14.22 | 15.14 | 0.92 | 1.63 | 2.761 | 9.954 | 3.0273 |  | 3.9 | 12.3 | 2021-03-31
2021-04-01 | Click Here |  | 6.18 | 5.3 | 5.2 | 5.39 | 5.41 | 7.07 | 7.71 | 1.64 | 1.87 | 2.06 | 2.15 | 50 | 44 | 26 | 3 | 1 |  | 0.316 | 0.254 | 1.87 | 0.336 | 0.689 | 0.641 | 16.2 | 39.3 | 29.6 | 29.8 | 45.1 | 32.4 | 78.6 | 59.2 | 59.6 | 90.2 | 2.99 | 3.43 | 3 | 6 | 0.061 | 7.7 | 4.9 | 94.22 | 0.81992 | 58.8 | 89.9 | 0.234 | 0.0482 | 15.66 | 14.7 | 15.65 | 0.95 | 1.634 | 2.756 | 10 | 2.9099 | 28.52 | 3.9 | 12.3 | 2021-04-01
2021-04-02 | Click Here | [58 empty] | 2021-04-02
2021-04-03 | Click Here |  | 6.18 | 5.28 | 5.1 | 5.32 | 5.35 | 6.89 | 6.83 | 1.6 | 1.84 | 2.03 | 2.14 | 50 | 43 | 20 |  |  |  | 0.329 | 0.276 | 1.81 | 0.306 | 0.594 | 0.568 | 17 | 37 | 30.6 | 30.9 | 44.8 | 34 | 74 | 61.2 | 61.8 | 89.6 | 2.97 | 3.14 | 3 | 6.1 | 0.059 | 9 | 4.8 | 94.97 | 0.96925 | 58.5 | 90 | 0.2342 | 0.0481 | 14.91 | 14.14 | 15.06 | 0.92 |  |  |  | 3.0492 | 24.51 | 3.8 | 11.4 | 2021-04-03
2021-04-04 | Click Here | [41 empty] | 93.03 | 0.94635 |  |  |  |  | 14.84 | 13.91 | 14.83 | 0.92 | 1.437 | 2.766 | 10 | 3.0364 |  | 3.4 | 11.6 | 2021-04-04
2021-04-05 | Click Here |  | 6.09 | 5.16 | 5.1 | 5.29 | 5.37 | 6.92 | 6.9 | 1.66 | 1.92 | 1.96 | 2.04 | 49 | 42 | 19 |  |  |  | 0.291 | 0.274 | 1.77 | 0.261 | 0.496 | 0.534 | 15.8 | 36.8 | 29.7 | 30.2 | 43.4 | 31.6 | 73.6 | 59.4 | 60.4 | 86.4 | 3.02 | 3.2 | 3.1 | 6 | 0.074 | 9.1 | 5 | 95.96 | 0.9454 | 58.9 | 90.4 | 0.2334 | 0.0436 | 14.96 | 14.12 | 15.12 | 1 | 1.49 | 2.766 | 9.681 | 3.0854 | 29.61 | 3.4 | 11.6 | 2021-04-05
2021-04-06 | Click Here |  | 6.11 | 5.17 | 5.02 | 5.38 | 5.4 | 7.22 | 6.85 | 1.73 | 1.98 | 2.04 | 1.91 | 54 | 47 | 42 | 2 |  |  | 0.368 | 0.31 | 3.24 | 0.261 | 0.774 | 0.854 | 14.3 | 34.6 | 26.6 | 29.2 | 41 | 24.6 | 69.2 | 53.2 | 58.4 | 82 | 2.99 | 3.26 | 3 | 6 | 0.039 | 7.3 | 4.6 | 90.41 | 0.99176 | 48.5 | 90.3 | 0.314 | 0.0441 | 16.18 | 13.45 | 14.4 | 0.95 | 1.459 | 2.769 | 9.527 | 3.0518 | 29.54 | 3.4 | 11.6 | 2021-04-06
2021-04-07 | Click Here |  | 5.98 | 5.07 | 5.1 | 5.14 | 5.13 | 6.91 | 7.24 | 1.76 | 2 | 2.09 | 2.06 | 55 | 49 | 38 | 2 | 1 |  | 0.328 | 0.306 | 3.01 | 0.24 | 0.539 | 0.567 | 14 | 32.4 | 28 | 29.2 | 39.8 | 28 | 62.8 | 56 | 58.4 | 79.6 | 3.03 | 3.26 | 3 | 6 | 0.044 | 8.5 | 6 | 86.68 | 0.98713 | 48.2 | 90.1 | 0.3142 | 0.044 | 15.4 | 13 | 13.92 | 0.92 | 1.516 | 2.766 | 9.262 | 3.0271 | 37.7 | 3.4 | 11.6 | 2021-04-07
2021-04-08 | Click Here |  | 5.94 | 5 | 5.09 | 5.1 | 5.15 | 6.83 | 7.1 | 1.79 | 2.01 | 2.08 | 2.1 | 55 | 48 | 24 | 3 |  |  | 0.321 | 0.307 | 1.58 | 0.201 | 0.563 | 0.54 | 12.8 | 34 | 28 | 28.4 | 38.7 | 25.6 | 68 | 56 | 56.8 | 77.4 | 3.02 | 3.21 | 3 | 5.9 | 0.049 | 6.9 | 4.6 | 90.41 | 1.095 | 48.4 | 83.8 | 0.314 | 0.0768 | 13.98 | 13.01 | 13.96 | 0.95 | 1.376 | 2.766 | 9.186 | 3.155 | 30.33 | 3.5 | 11.6 | 2021-04-08
2021-04-09 | Click Here |  | 5.59 | 5 | 5.13 | 5.08 | 5.18 | 6.95 | 6.94 | 1.25 | 1.56 | 1.84 | 2.03 | 70 | 61 | 34 | 2 |  |  | 0.538 | 0.325 | 1.85 | 0.131 | 1.31 | 1.099 | 11.8 | 32.8 | 27.3 | 27.1 | 37.4 | 23.4 | 65.6 | 54.6 | 54.2 | 74.8 | 2.93 | 3.23 | 3.1 | 6 | 0.024 | 6.8 | 4.8 | 79.38 | 1.1329 | 45.2 | 84.8 | 0.3443 | 0.0715 | 12.62 | 11.54 | 12.51 | 0.97 | 1.258 | 2.779 | 6.813 | 3.1229 | 30.28 | 3.1 | 11.9 | 2021-04-09
2021-04-10 | Click Here |  | 5.63 | 5.03 | 4.9 | 5.11 | 5.24 | 7.01 | 6.96 | 1.46 | 1.79 | 1.98 | 2.01 | 64 | 55 | 28 | 1 |  |  | 0.525 | 0.34 | 1.44 | 0.128 | 0.852 | 0.772 | 11.6 | 32.2 | 28 | 27.4 | 38.1 | 23.2 | 64.4 | 56 | 54.8 | 76.2 | 2.93 | 3.24 | 3 | 5.8 | 0.021 | 6.8 | 4.9 | 82.67 | 1.2734 | 46.6 | 86.4 | 0.3319 | 0.0651 | 12.82 | 11.79 | 12.76 | 0.97 |  |  |  | 3.1834 | 30.04 | 3.1 | 11.9 | 2021-04-10
2021-04-11 | Click Here | [41 empty] | 84.67 | 1.1308 |  |  |  |  | 12.72 | 12.6 | 12.6 |  | 1.101 | 2.773 | 6.336 | 3.0508 |  | 3.1 | 11.9 | 2021-04-11
2021-04-12 | Click Here |  | 5.82 | 4.89 | 4.93 | 5.09 | 5.19 | 6.99 | 7.1 | 1.28 | 1.6 | 1.79 | 1.96 | 69 | 63 | 19 |  |  |  | 0.467 | 0.386 | 1.24 | 0.109 | 0.794 | 0.896 | 12.2 | 32.9 | 28.4 | 27.7 | 39.4 | 24.4 | 65.8 | 56.8 | 55.4 | 78.8 | 3.03 | 3.32 | 3.1 | 5.9 | 0.046 | 6.7 | 4.9 | 81.08 | 1.0425 | 46.8 | 88.9 | 0.3298 | 0.0509 | 13.22 | 12.26 | 13.2 | 0.94 | 1.726 | 2.769 | 6.126 | 3.0025 | 31.04 | 3.3 | 11.9 | 2021-04-12
2021-04-13 | Click Here | 7:10 PM | 5.96 | 5.06 | 4.9 | 5.35 | 5.37 | 8.42 | 7.29 | 1.59 | 1.88 | 1.89 | 2.01 | 64 | 57 | 24 | 2 |  |  | 0.533 | 0.389 | 2.16 | 0.285 | 0.596 | 0.734 | 11.2 | 33.5 | 25.4 | 25.5 | 36.1 | 22.4 | 67 | 50.8 | 51 | 72.2 | 3.01 | 3.23 | 3 | 6.2 | 0.037 | 6.8 | 5.1 | 94.82 | 1.0549 | 48.6 | 85.7 | 0.3135 | 0.067 | 14.94 | 14 | 14.96 | 0.96 | 1.804 | 2.763 | 5.972 | 3.0749 | 29.65 | 3.3 | 11.9 | 2021-04-13
2021-04-14 | Click Here |  | 5.45 | 4.95 | 5.08 | 5.07 | 5.13 | 7.18 | 7.5 | 1.62 | 1.77 | 2.13 | 2.08 | 72 | 65 | 30 |  |  |  | 0.551 | 0.393 | 1.59 | 0.15 | 0.637 | 0.593 | 10.9 | 34.5 | 25.9 | 25.8 | 35.6 | 21.8 | 69 | 51.8 | 51.6 | 71.2 | 2.91 | 3.24 | 3 | 5.8 | 0.015 | 8 | 5 | 90.41 | 1.2244 | 47.1 | 86.4 | 0.3265 | 0.0631 | 13.36 | 12.31 | 13.31 | 1 | 1.682 | 2.764 | 6.103 | 3.3344 | 29.11 | 3.5 | 11.4 | 2021-04-14
2021-04-15 | Click Here |  | 5.52 | 4.99 | 5.12 | 5.14 | 5.18 | 7.41 | 7.27 | 1.6 | 1.73 | 2.1 | 2.11 | 76 | 67 | 29 |  |  |  | 0.798 | 0.386 | 1.46 | 0.092 | 0.6 | 0.541 | 10.9 | 31 | 26 | 25.9 | 35.7 | 21.8 | 62 | 52 | 51.8 | 71.4 | 2.9 | 3.35 | 3.1 | 5.9 | 0.062 | 8.4 | 5.1 | 90.93 | 0.97217 | 56.4 | 86.6 | 0.2482 | 0.0621 | 14.36 | 13.57 | 14.41 | 0.84 | 1.678 | 2.75 | 8.009 | 3.0422 | 29.57 | 3.5 | 11.4 | 2021-04-15
2021-04-16 | Click Here |  | 5.64 | 5.04 | 4.99 | 5.18 | 5.24 | 7.51 | 7.64 | 1.65 | 1.84 | 2.04 | 2.01 | 69 | 60 | 22 |  |  |  | 0.593 | 0.422 | 1.26 | 0.071 | 0.596 | 0.567 | 7.9 | 24.1 | 19.2 | 19.1 | 28.2 | 15.8 | 48.2 | 38.4 | 38.2 | 56.4 | 2.95 | 3.42 | 3 | 5.9 | 0.054 | 3.2 | 5.9 | 81.65 | 0.81403 | 55.9 | 89.6 | 0.2506 | 0.0475 | 13.19 | 13.08 | 13.08 |  | 1.693 | 2.757 | 8.214 | 2.834 | 29.44 | 3.5 | 11.4 | 2021-04-16
2021-04-17 | Click Here |  | 6 | 5 | 4.96 | 5.47 | 5.54 | 7.59 | 7.71 | 1.7 | 1.88 | 2.01 | 1.9 | 64 | 57 | 17 |  |  |  | 0.396 | 0.415 | 1.37 | 0.084 | 0.496 | 0.557 | 8.4 | 25.1 | 19.9 | 20.4 | 30.6 | 16.8 | 50.2 | 39.8 | 40.8 | 61.2 | 2.88 | 3.43 | 2.9 | 5.8 | 0.072 | 8.7 | 6.2 | 74.97 | 0.99546 | 56.2 | 90.9 | 0.2488 | 0.0414 | 12.23 | 11.25 | 12.18 | 0.93 |  |  |  | 3.0255 | 29.94 | 3.5 | 11.4 | 2021-04-17
2021-04-18 | Click Here | [58 empty] | 2021-04-18
2021-04-19 | Click Here |  | 5.64 | 4.97 | 4.92 | 5.1 | 5.07 | 6.91 | 7.72 | 1.46 | 1.69 | 2.04 | 2.09 | 71 | 64 | 35 | 1 |  |  | 0.721 | 0.414 | 1.18 | 0.265 | 0.563 | 0.444 | 7.9 | 23.6 | 18.9 | 18.5 | 28.5 | 15.8 | 47.2 | 37.8 | 37 | 57 | 2.78 | 3.21 | 3.1 | 6 | 0.021 | 8.2 | 5.5 | 77.18 | 0.98366 | 47.6 | 86.6 | 0.3221 | 0.0622 | 12.45 | 11.4 | 12.36 | 0.96 | 1.546 | 2.758 | 5.641 | 3.0737 | 29.11 | 3.7 | 11.2 | 2021-04-19
2021-04-20 | Click Here |  | 6.23 | 4.97 | 4.96 | 5.07 | 5.13 | 6.94 | 6.86 | 1.6 | 1.83 | 2.19 | 2.26 | 65 | 57 | 21 | 1 |  |  | 0.613 | 0.476 | 1.02 | 0.104 | 0.492 | 0.437 | 9.1 | 26.2 | 18.8 | 19.3 | 27.2 | 18.2 | 52.4 | 37.6 | 38.6 | 54.4 | 2.81 | 3.31 | 3.1 | 5.9 | 0.018 | 11.3 | 5.8 | 85.99 | 0.53483 | 47.8 | 90.2 | 0.322 | 0.0448 | 14.12 | 13.12 | 14.09 | 0.97 | 1.523 | 2.757 | 5.66 | 2.7648 |  | 3.9 | 11.2 | 2021-04-20
2021-04-21 | Click Here |  | 6.14 | 5.02 | 4.98 | 5.1 | 5.19 | 7.04 | 7.14 | 1.69 | 1.98 | 2.2 | 2.32 | 68 | 60 | 17 |  |  |  | 0.526 | 0.457 | 0.992 | 0.11 | 0.382 | 0.391 | 8.8 | 26.5 | 19.2 | 19.8 | 26.8 | 17.6 | 53 | 38.4 | 39.6 | 53.6 | 2.85 | 3.43 | 3 | 6.1 | 0.0028 | 11.2 | 5.9 | 84.65 | 0.62547 | 48.2 | 90.7 | 0.3198 | 0.0401 | 13.75 | 13.65 | 13.65 |  | 1.38 | 2.747 | 8.396 | 2.8155 | 29.41 | 3.9 | 11.2 | 2021-04-21
2021-04-22 | Click Here |  | 6.17 | 5.01 | 4.95 | 5.14 | 5.18 | 7.04 | 6.97 | 1.67 | 1.92 | 2.06 | 2.1 | 65 | 58 | 19 | 1 |  |  | 0.399 | 0.426 | 1.04 | 0.084 | 0.417 | 0.496 | 9.2 | 27 | 18.8 | 19.4 | 27.4 | 18.4 | 54 | 37.6 | 38.8 | 54.8 | 2.73 | 3.35 | 3.1 | 5.9 | 0.042 | 11.3 | 6 | 81.58 | 0.97677 | 48 | 91.4 | 0.3208 | 0.0364 | 12.9 | 11.96 | 12.92 | 0.96 | 1.368 | 2.759 | 7.472 | 3.0968 | 30.8 | 3.9 | 11.2 | 2021-04-22
2021-04-23 | Click Here |  | 6.29 | 4.97 | 4.94 | 5.12 | 5.15 | 7.01 | 6.93 | 1.52 | 1.89 | 2.01 | 2.06 | 63 | 56 | 28 | 1 |  |  | 0.483 | 0.511 | 1.16 | 0.091 | 0.503 | 0.567 | 8.5 | 26.9 | 22.5 | 20.3 | 28.2 | 17 | 53.8 | 45 | 40.6 | 56.4 | 2.77 | 3.42 | 3.1 | 6 | 0.031 | 11.2 | 6.5 | 79.2 | 0.84412 | 51.9 | 83.8 | 0.2842 | 0.0762 | 12.93 | 11.89 | 12.85 | 0.96 | 1.323 | 2.752 | 8.546 | 3.0241 | 28.68 | 3.9 | 11.2 | 2021-04-23
2021-04-24 | Click Here |  | 6.31 | 5.13 | 5.09 | 5.16 | 5.23 | 7.14 | 7.23 | 1.59 | 1.93 | 2.08 | 2.1 | 61 | 55 | 20 |  |  |  | 1.13 | 0.794 | 1.06 | 0.124 | 0.693 | 0.553 | 8.2 | 23.2 | 20.1 | 20.2 | 27.4 | 16.4 | 46.4 | 40.2 | 40.4 | 54.8 | 2.72 | 3.37 | 3 | 6 | 0.026 | 9.5 | 6.5 | 75.72 | 0.75842 | 45.6 | 85.5 | 0.3403 | 0.0679 | 12.67 | 11.62 | 12.6 | 0.98 |  |  |  | 2.9584 | 28.38 | 3.9 | 11.2 | 2021-04-24
2021-04-25 | Click Here | [41 empty] | 75.54 | 0.58801 |  |  |  |  | 12.63 | 12.48 | 12.48 |  | 1.229 | 2.757 | 8.429 | 2.748 |  | 3.9 | 11.2 | 2021-04-25
2021-04-26 | Click Here |  | 6.24 | 5.14 | 5.08 | 5.22 | 5.3 | 7.19 | 7.14 | 1.62 | 1.98 | 2.11 | 2.13 | 63 | 57 | 17 |  |  |  | 0.826 | 0.654 | 0.921 | 0.14 | 0.492 | 0.517 | 8.3 | 24.1 | 19.9 | 20.1 | 28.2 | 16.6 | 48.2 | 39.8 | 40.2 | 56.4 | 2.82 | 3.46 | 2.9 | 6 | 0.034 | 9.6 | 6.7 | 78.83 | 0.7802 | 45.4 | 86.7 | 0.3427 | 0.0621 | 13 | 12.09 | 13.02 | 0.93 | 1.365 | 2.773 | 7.448 | 2.9602 | 29.23 | 3.9 | 11.2 | 2021-04-26
2021-04-27 | Click Here |  | 6.14 | 5.08 | 5.07 | 5.19 | 5.26 | 7.1 | 7.13 | 1.66 | 1.99 | 2.08 | 2.1 | 69 | 60 | 19 |  |  |  | 0.746 | 0.621 | 1.07 | 0.113 | 0.498 | 0.536 | 9.1 | 25.2 | 18.9 | 19.7 | 27.7 | 18.2 | 50.4 | 37.8 | 39.4 | 55.4 | 2.73 | 3.52 | 3 | 5.9 | 0.036 | 9.7 | 6.8 | 81.58 | 0.77099 | 44.9 | 88.6 | 0.3491 | 0.0521 | 13.27 | 12.26 | 13.17 | 0.91 | 1.406 | 2.814 | 8.161 | 3.021 | 29.62 | 3.9 | 11.2 | 2021-04-27
2021-04-28 | Click Here |  | 6.16 | 5.05 | 5.07 | 5.13 | 5.16 | 7.09 | 7.64 | 1.69 | 2.01 | 2.11 | 2.14 | 68 | 58 | 20 |  |  |  | 0.699 | 0.583 | 1.1 | 0.119 | 0.572 | 0.581 | 9.9 | 30.2 | 23.8 | 23.4 | 30.4 | 19.8 | 60.4 | 47.6 | 46.8 | 60.8 | 2.67 | 3.36 | 3 | 5.9 | 0.032 | 11.5 | 7.8 | 78.72 | 0.73872 | 44.7 | 88.4 | 0.3493 | 0.0518 | 12.75 | 11.8 | 12.77 | 0.97 | 1.441 | 2.808 | 7.499 | 3.0287 | 28.46 | 3.9 | 11.2 | 2021-04-28
2021-04-29 | Click Here |  | 6.37 | 5 | 5.01 | 5.11 | 5.16 | 6.91 | 7.36 | 1.7 | 2.04 | 2.15 | 2.2 | 66 | 54 | 18 |  |  |  | 0.621 | 0.563 | 0.993 | 0.102 | 0.742 | 0.961 | 9.6 | 27.7 | 23.2 | 22.8 | 28.6 | 19.2 | 55.4 | 46.4 | 45.6 | 57.2 | 2.63 | 3.38 | 3 | 5.7 | 0.039 | 12 | 7.7 | 81.59 | 0.67004 | 44.9 | 89.3 | 0.349 | 0.0514 | 13.43 | 12.43 | 13.39 | 0.96 | 1.496 | 2.773 | 8.255 | 2.98 | 28.88 | 3.9 | 11.2 | 2021-04-29
2021-04-30 | Click Here |  | 5.77 | 5.13 | 5.08 | 5.17 | 5.22 | 7.43 | 7.78 | 1.37 | 1.53 | 2.03 | 2.22 | 69 | 62 | 29 | 6 |  |  | 0.803 | 0.553 | 1.69 | 0.105 | 0.481 | 0.426 | 9 | 25.5 | 22.6 | 22.1 | 31.4 | 18 | 51 | 45.2 | 44.2 | 62.8 | 2.9 | 3.28 | 3.1 | 5.9 | 0.021 | 11.7 | 5.9 | 77.18 | 0.89291 | 48.4 | 91.1 | 0.3148 | 0.0404 | 12.49 | 11.44 | 12.38 | 0.91 | 1.665 | 2.76 | 6.071 | 3.0629 | 30.51 | 3.9 | 11.2 | 2021-04-30
2021-05-01 | Click Here |  | 6.04 | 5.12 | 5.07 | 5.15 | 5.19 | 7.28 | 7.06 | 1.5 | 1.66 | 2.13 | 2.19 | 73 | 67 | 29 | 2 |  |  | 0.506 | 0.855 | 1.01 | 0.121 | 0.627 | 0.527 | 8.6 | 26.4 | 22.6 | 22.3 | 29.5 | 17.2 | 52.8 | 45.2 | 44.6 | 59 | 2.99 | 3.26 | 3.1 | 5.8 | 0.024 | 12.2 | 7.9 | 81.59 | 0.90974 | 48.6 | 87.8 | 0.3134 | 0.0565 | 13.02 | 11.95 | 12.94 | 0.99 |  |  |  | 3.0997 | 29.57 | 3.9 | 10.3 | 2021-05-01
2021-05-02 | Click Here | [58 empty] | 2021-05-02
2021-05-03 | Click Here |  | 6.31 | 5.03 | 5.11 | 5.14 | 5.16 | 6.83 | 7.18 | 1.43 | 1.63 | 1.89 | 2.05 | 74 | 68 | 22 | 3 | 1 |  | 0.872 | 0.577 | 1.1 | 0.128 | 0.768 | 0.637 | 9.8 | 27.3 | 22.2 | 22.3 | 28.7 | 19.6 | 54.6 | 44.4 | 44.6 | 57.4 | 3.02 | 3.23 | 3 | 5.9 | 0.027 | 12 | 8.1 | 82.69 | 1.1845 | 40.8 | 81.7 | 0.3889 | 0.0875 | 12.47 | 11.5 | 12.42 | 0.92 | 1.485 | 2.747 | 5.947 | 3.2645 | 27.27 | 3.9 | 10.3 | 2021-05-03
2021-05-04 | Click Here |  | 6.31 | 5.06 | 5.14 | 5.08 | 5.12 | 6.73 | 6.99 | 1.61 | 1.73 | 2.04 | 2.07 | 67 | 61 | 28 | 4 | 1 |  | 0.797 | 0.506 | 1.15 | 0.126 | 0.916 | 0.834 | 8.7 | 27.8 | 23.4 | 23.6 | 27.9 | 17.4 | 55.6 | 46.8 | 47.2 | 55.8 | 3.03 | 3.3 | 3.1 | 5.7 | 0.021 | 11.5 | 8.2 | 88.2 | 1.3121 | 38.8 | 84.2 | 0.411 | 0.0744 | 12.91 | 11.91 | 12.88 | 0.97 | 1.567 | 2.745 | 5.86 | 3.3621 | 31.54 | 3.9 | 10.3 | 2021-05-04
2021-05-05 | Click Here |  | 5.64 | 5.03 | 5.01 | 5.08 | 5.12 | 6.97 | 6.95 | 1.55 | 1.66 | 1.96 | 1.78 | 67 | 58 | 28 | 6 |  |  | 0.725 | 0.53 | 1.49 | 0.079 | 1.31 | 0.613 | 8.7 | 27.6 | 23.1 | 23.2 | 29.8 | 17.4 | 55.2 | 46.2 | 46.4 | 59.6 | 3.75 | 4.16 | 3 | 5.8 | 0.027 | 11.9 | 8.4 | 82.79 | 0.77822 | 48.7 | 86.2 | 0.3121 | 0.0642 | 13.76 | 12.88 | 13.79 | 0.91 | 1.683 | 2.736 | 5.86 | 2.9182 | 30.98 | 4.1 | 10.6 | 2021-05-05
2021-05-06 | Click Here |  | 5.9 | 5.1 | 5.05 | 5.2 | 5.18 | 7.16 | 7.14 | 1.74 | 1.89 | 2.2 | 2.34 | 67 | 59 | 38 |  |  |  | 0.828 | 0.529 | 1.89 | 0.112 | 0.625 | 0.614 | 9 | 29.2 | 24.5 | 23.9 | 29.9 | 18 | 58.4 | 49 | 47.8 | 59.8 | 3.88 | 3.99 | 3 | 5.9 | 0.021 | 13.1 | 8.8 | 72.76 | 0.29959 | 59.7 | 86.5 | 0.2234 | 0.063 | 13.6 | 12.61 | 13.58 | 0.97 | 1.644 | 2.75 | 7.478 | 2.6196 | 31.45 | 4.1 | 10.6 | 2021-05-06
2021-05-07 | Click Here |  | 5.87 | 5.16 | 5.17 | 5.25 | 5.31 | 6.84 | 6.72 | 1.69 | 1.94 | 2.2 | 2.38 | 69 | 60 | 29 | 1 |  |  | 0.621 | 0.488 | 1.77 | 0.104 | 0.592 | 0.635 | 8.7 | 26.7 | 23.4 | 22.6 | 28.6 | 17.4 | 53.4 | 46.8 | 45.2 | 57.2 | 3.27 | 4.18 | 3.1 | 5.8 | 0.044 | 12.7 | 8.7 | 93.45 | 1.0414 | 50.2 | 84.4 | 0.2989 | 0.0732 | 13.44 | 12.51 | 13.44 | 0.93 | 1.556 | 2.768 | 7.159 | 3.3914 | 31.36 | 4.1 | 10.6 | 2021-05-07
2021-05-08 | Click Here |  | 6.04 | 5.12 | 5.09 | 5.3 | 5.32 | 7.1 | 6.9 | 1.8 | 2.07 | 2.2 | 2.23 | 69 | 62 | 24 |  |  |  | 0.493 | 0.466 | 1.97 | 0.098 | 0.546 | 0.724 | 8.7 | 27.1 | 23.2 | 23.1 | 29.5 | 17.4 | 54.2 | 46.4 | 46.2 | 59 | 3.19 | 3.67 | 2.9 | 5.8 | 0.027 | 12.3 | 8.8 | 86 | 1.1506 | 49 | 86.5 | 0.3092 | 0.0626 | 12.11 | 11.25 | 12.05 | 0.8 |  |  |  | 3.4706 | 30.44 | 4.1 | 10.6 | 2021-05-08
2021-05-09 | Click Here | [58 empty] | 2021-05-09
2021-05-10 | Click Here |  | 5.81 | 5.09 | 5 | 5.14 | 5.18 | 6.79 | 6.56 | 1.71 | 1.87 | 2.2 | 2.27 | 63 | 55 | 35 | 6 |  |  | 0.768 | 0.49 | 1.69 | 0.083 | 0.952 | 1.04 | 9.1 | 28.2 | 23.5 | 23.6 | 30.1 | 18.2 | 56.4 | 47 | 47.2 | 60.2 | 4.53 | 3.65 | 3.1 | 5.9 | 0.021 | 12.1 | 8.9 | 99.22 | 0.98084 | 50.4 | 85.5 | 0.2969 | 0.0676 | 14.69 | 13.73 | 14.7 | 0.97 | 1.288 | 2.733 | 8.635 | 3.2808 | 29.8 | 4.1 | 10.6 | 2021-05-10
2021-05-11 | Click Here |  | 6.04 | 5.03 | 5.07 | 5.07 | 5.09 | 6.82 | 7.03 | 1.73 | 1.88 | 2.2 | 2.27 | 61 | 54 | 37 | 1 |  |  | 0.669 | 0.482 | 1.84 | 0.149 | 0.806 | 0.785 | 8.9 | 28.5 | 23.4 | 23.9 | 30.2 | 17.8 | 57 | 46.8 | 47.8 | 60.4 | 3.49 | 2.74 | 3 | 5.9 | 0.013 | 12 | 9.4 | 105.84 | 1.0502 | 61.3 | 83.2 | 0.2125 | 0.0796 | 15.16 | 14.3 | 15.21 | 0.91 | 1.288 | 2.733 | 8.635 | 3.3602 | 30.04 | 4.1 | 10.6 | 2021-05-11
2021-05-12 | Click Here |  | 6.01 | 5.09 | 5.02 | 5.1 | 5.14 | 7.04 | 6.95 | 1.77 | 1.96 | 2.2 | 2.34 | 64 | 57 | 34 |  |  |  | 0.513 | 0.0486 | 1.78 | 0.119 | 0.712 | 0.694 | 9.1 | 28.4 | 22.9 | 23.6 | 30.4 | 18.2 | 56.8 | 45.8 | 47.2 | 60.8 | 3.3 | 2.79 | 2.9 | 6.1 | 0.019 | 12.2 | 8.7 | 98.47 | 1.0883 | 54.3 | 87.7 | 0.265 | 0.0567 | 14 | 13.04 | 13.95 | 0.91 | 1.288 | 2.733 | 8.635 | 3.4283 | 30.13 | 4.1 | 10.6 | 2021-05-12
2021-05-13 | Click Here |  | 6 | 5.11 | 5.01 | 5.27 | 5.33 | 7.07 | 6.84 | 1.64 | 1.9 | 2.14 | 2.26 | 64 | 58 | 23 |  |  |  | 0.443 | 0.474 | 1.94 | 0.094 | 0.776 | 0.831 | 9.1 | 29.8 | 24.7 | 25.2 | 30 | 18.2 | 59.6 | 49.4 | 50.4 | 60 | 3.45 | 2.49 | 3 | 5.9 | 0.063 | 12.4 | 8.9 | 90.4 | 0.92211 | 54.9 | 81.7 | 0.2621 | 0.0873 | 13.59 | 12.62 | 13.56 | 0.94 | 1.288 | 2.733 | 8.635 | 3.2521 | 29.65 | 4.1 | 10.6 | 2021-05-13
2021-05-14 | Click Here |  | 6.25 | 5.06 | 5 | 5.08 | 5.14 | 6.81 | 6.85 | 1.62 | 1.74 | 2.04 | 2.08 | 64 | 59 | 21 | 1 |  |  | 0.451 | 0.458 | 1.63 | 0.113 | 0.771 | 0.736 | 9.3 | 29.8 | 23.4 | 23.1 | 29.9 | 18.6 | 59.6 | 46.8 | 46.2 | 59.8 | 3.59 | 2.92 | 3 | 5.7 | 0.027 | 12.5 | 8.9 | 90.4 | 1.2708 | 54.8 | 85.2 | 0.2622 | 0.0695 | 12.73 | 11.69 | 12.62 | 0.93 | 1.626 | 2.763 | 6.987 | 3.5108 | 27.96 | 4.1 | 10.6 | 2021-05-14
2021-05-15 | Click Here |  | 6.31 | 5.04 | 5.08 | 5.1 | 5.11 | 6.72 | 6.91 | 1.75 | 1.94 | 2.17 | 2.28 | 60 | 53 | 23 | 1 |  |  | 0.671 | 0.463 | 1.23 | 0.065 | 0.812 | 0.774 | 9.5 | 27.8 | 23.8 | 23.9 | 28.7 | 19 | 55.6 | 47.6 | 47.8 | 57.4 | 3.53 | 2.81 | 3.1 | 5.8 | 0.025 | 13.2 | 9.1 | 89.04 | 1.0615 | 52.6 | 86.3 | 0.2784 | 0.0638 | 12.98 | 11.99 | 12.96 | 0.97 |  |  |  | 3.3715 | 30.08 | 4.1 | 10.9 | 2021-05-15
2021-05-16 | Click Here | [41 empty] | 89.9 | 1.0612 |  |  |  |  | 12.96 | 11.93 | 12.9 | 0.97 | 1.312 | 2.757 | 7.368 | 3.4212 |  | 4.1 | 11.2 | 2021-05-16
2021-05-17 | Click Here |  | 6.12 | 5.07 | 5.01 | 5.15 | 5.19 | 7.01 | 7.08 | 1.84 | 2.01 | 2.2 | 2.35 | 62 | 56 | 16 |  |  |  | 0.596 | 0.442 | 1.12 | 0.091 | 0.594 | 0.994 | 9.6 | 29.4 | 24.9 | 25.2 | 29.7 | 19.2 | 58.8 | 49.8 | 50.4 | 59.4 | 3.66 | 2.75 | 3.1 | 6 | 0.061 | 13.1 | 9.2 | 97.31 | 1.0147 | 57.1 | 89.1 | 0.2431 | 0.05 | 14.05 | 13.13 | 14.06 | 0.93 | 1.502 | 2.719 | 8.409 | 3.3647 | 30.57 | 4.1 | 11.2 | 2021-05-17
2021-05-18 | Click Here |  | 6.04 | 5 | 4.96 | 5.1 | 5.12 | 6.92 | 7.06 | 1.7 | 1.92 | 2.14 | 2.29 | 67 | 60 | 21 | 1 |  |  | 0.398 | 0.471 | 1.74 | 0.072 | 0.623 | 0.756 | 9.9 | 31.4 | 26.5 | 25.7 | 31.2 | 19.8 | 62.8 | 53 | 51.4 | 62.4 | 3.31 | 2.59 | 2.9 | 6 | 0.059 | 14.2 | 9.8 | 94.87 | 0.98705 | 9 | 86.8 | 0.2657 | 0.0614 | 13.82 | 12.83 | 13.81 | 0.98 | 1.534 | 2.693 | 8.079 | 3.3571 | 29.28 | 4.1 | 11.2 | 2021-05-18
2021-05-19 | Click Here |  | 6.22 | 5.02 | 4.97 | 5.06 | 5.1 | 6.9 | 6.96 | 1.63 | 1.89 | 2.1 | 2.22 | 65 | 57 | 20 | 1 |  |  | 0.441 | 0.446 | 1.38 | 0.081 | 0.712 | 0.773 | 10.3 | 32.2 | 26.9 | 26.2 | 30.8 | 20.6 | 64.4 | 53.8 | 52.4 | 61.6 | 3.33 | 2.47 | 3 | 5.9 | 0.038 | 14.6 | 1 | 90.45 | 0.94967 | 54.6 | 86.1 | 0.2449 | 0.0646 | 13.31 | 12.37 | 13.31 | 0.94 | 1.624 | 2.711 | 8.009 | 3.3197 | 30.21 | 4.1 | 11.2 | 2021-05-19
2021-05-20 | Click Here |  | 6.21 | 5.04 | 5.1 | 5.09 | 5.14 | 6.92 | 6.85 | 1.66 | 1.94 | 2.2 | 2.38 | 62 | 57 | 19 | 1 |  |  | 0.397 | 0.437 | 1.3 | 0.074 | 0.692 | 0.774 | 10.1 | 31.7 | 25.9 | 26.4 | 31 | 20.2 | 63.4 | 51.8 | 52.8 | 62 | 3.32 | 2.52 | 3 | 6 | 0.047 | 14.1 | 10.1 | 97.02 | 0.95346 | 55.1 | 86.7 | 0.2596 | 0.062 | 13.95 | 12.98 | 13.93 | 0.95 | 1.625 | 2.711 | 7.851 | 3.3935 | 29.49 | 4.1 | 11.2 | 2021-05-20
2021-05-21 | Click Here |  | 5.78 | 4.97 | 4.97 | 5.01 | 5.03 | 6.72 | 7.05 | 1.7 | 1.88 | 2.2 | 2.45 | 58 | 51 | 37 | 4 |  |  | 0.559 | 0.467 | 1.89 | 0.118 | 0.965 | 0.764 | 10.3 | 32.2 | 29.3 | 28.2 | 34.7 | 20.6 | 64.4 | 58.6 | 56.4 | 69.4 | 3.23 | 3.25 | 3.1 | 5.9 | 0.022 | 15.8 | 10.4 | 83.79 | 0.5139 | 52.8 | 87.3 | 0.2808 | 0.059 | 13.47 | 12.58 | 13.5 | 0.92 | 1.632 | 2.729 | 7.824 | 3.0239 | 30.04 | 4.5 | 11.4 | 2021-05-21
2021-05-22 | Click Here |  | 5.75 | 5.01 | 4.93 | 5.06 | 5.14 | 6.94 | 6.67 | 1.72 | 1.89 | 2.2 | 2.45 | 49 | 42 | 26 | 1 |  |  | 0.686 | 0.404 | 1.69 | 0.098 | 0.772 | 0.658 | 10.9 | 31.6 | 28.4 | 27.7 | 31.2 | 21.8 | 63.2 | 56.8 | 55.4 | 62.4 | 3.32 | 3.42 | 3 | 6 | 0.028 | 16.9 | 11.2 | 82.69 | 0.70772 | 52.6 | 88.1 | 0.2814 | 0.0576 | 12.71 | 11.74 | 12.67 | 0.93 |  |  |  | 3.1977 | 30.04 | 4.5 | 11.4 | 2021-05-22
2021-05-23 | Click Here | [58 empty] | 2021-05-23
2021-05-24 | Click Here |  | 6.15 | 4.96 | 5.05 | 5.06 | 5.08 | 6.71 | 7.03 | 1.6 | 1.72 | 2.11 | 2.24 | 52 | 44 | 23 | 1 |  |  | 0.791 | 0.673 | 1.49 | 0.011 | 0.738 | 0.717 | 10 | 33.7 | 28.4 | 28.3 | 32.6 | 20 | 67.4 | 56.8 | 56.6 | 65.2 | 3.31 | 3.39 | 3 | 5.9 | 0.031 | 14 | 10.6 | 87.03 | 1.0147 | 52.5 | 87.5 | 0.2812 | 0.0577 | 12.9 | 11.92 | 12.86 | 0.94 | 1.248 | 2.731 | 7.662 | 3.3147 | 33.06 | 4.5 | 11.4 | 2021-05-24
2021-05-25 | Click Here |  | 6.3 | 4.99 | 5.07 | 5.05 | 5.09 | 8.63 | 8.55 | 1.62 | 1.72 | 2.03 | 2.08 | 57 | 49 | 26 | 1 |  |  | 0.724 | 0.518 | 1.47 | 0.103 | 0.435 | 0.436 | 9.5 | 35 | 28.4 | 28.5 | 51.6 | 19 | 70 | 56.8 | 57 | 103.2 | 3.32 | 3.47 | 3 | 6.1 | 0.026 | 12.8 | 10.2 | 86 | 1.0102 | 52.4 | 88.5 | 0.2806 | 0.0526 | 13.01 | 12.05 | 13.01 | 0.96 | 1.344 | 2.61 | 7.628 | 3.2402 | 36.04 | 4.5 | 11.4 | 2021-05-25
2021-05-26 | Click Here |  | 5.57 | 4.92 | 4.95 | 4.96 | 5.01 | 6.94 | 8.24 | 1.73 | 1.86 | 2.2 | 2.37 | 57 | 50 | 21 |  |  |  | 0.754 | 0.588 | 1.6 | 0.087 | 1.44 | 1.323 | 9.6 | 32.2 | 28.4 | 28.6 | 38.2 | 19.2 | 64.4 | 56.8 | 57.2 | 76.4 | 3.14 | 3.46 | 3 | 5.9 | 0.042 | 13.4 | 5.9 | 77.18 | 0.54876 | 51.7 | 88.4 | 0.2864 | 0.0536 | 13.26 | 12.3 | 13.25 | 0.95 | 1.356 | 2.519 | 8.168 | 2.8488 | 32.86 | 5.3 | 11 | 2021-05-26
2021-05-27 | Click Here |  | 6.14 | 5.1 | 4.9 | 5.13 | 5.19 | 7.1 | 6.92 | 1.29 | 1.43 | 1.72 | 1.77 | 58 | 50 | 36 | 3 |  |  | 0.786 | 0.611 | 1.77 | 0.182 | 0.6 | 0.537 | 10 | 32.9 | 28.2 | 28.2 | 35.5 | 20 | 65.8 | 56.4 | 56.4 | 71 | 3.31 | 3.33 | 3.1 | 5.8 | 0.041 | 14.3 | 10.1 | 92 | 1.2076 | 51.4 | 87.9 | 0.2887 | 0.0557 | 13.58 | 12.59 | 13.52 | 0.93 | 1.46 | 2.605 | 8.154 | 3.3176 | 34.03 | 5.3 | 11 | 2021-05-27
2021-05-28 | Click Here |  | 6.04 | 5.13 | 5.19 | 5.33 | 5.32 | 7.01 | 6.99 | 1.47 | 1.63 | 1.97 | 2.24 | 59 | 51 | 19 |  |  |  | 0.462 | 0.561 | 1.71 | 0.092 | 0.497 | 0.599 | 10.2 | 32.1 | 29.2 | 29.4 | 35 | 20.4 | 64.2 | 58.4 | 58.8 | 70 | 3.46 | 3.38 | 3 | 6 | 0.047 | 14.3 | 10.9 | 90.93 | 0.91057 | 51.9 | 87.7 | 0.2848 | 0.0566 | 13.69 | 12.7 | 13.68 | 0.98 | 1.417 | 2.751 | 7.315 | 3.2506 | 29.62 | 5.3 | 11 | 2021-05-28
2021-05-29 | Click Here |  | 6.04 | 5.12 | 5.17 | 5.33 | 5.39 | 7 | 6.87 | 1.75 | 1.96 | 2.2 | 2.4 | 60 | 54 | 19 | 1 |  |  | 0.617 | 0.572 | 1.79 | 0.093 | 0.594 | 0.629 | 9.7 | 31.6 | 28.4 | 29.7 | 34.5 | 19.4 | 63.2 | 56.8 | 59.4 | 69 | 3.34 | 3.16 | 2.9 | 5.8 | 0.063 | 13.1 | 10.7 | 86 | 0.83207 | 53.6 | 88.5 | 0.2708 | 0.0529 | 13.28 | 12.27 | 13.24 | 0.97 |  |  |  | 3.1821 | 30.57 | 5.3 | 11 | 2021-05-29
2021-05-30 | Click Here | [58 empty] | 2021-05-30
2021-05-31 | Click Here |  | 5.84 | 4.98 | 5.09 | 5.02 | 5.05 | 6.78 | 6.79 | 1.68 | 1.88 | 2.2 | 2.47 | 57 | 49 | 16 |  |  |  | 0.682 | 0.534 | 1.03 | 0.13 | 0.858 | 0.706 | 10.6 | 34.5 | 31.1 | 30.8 | 36 | 21.2 | 69 | 62.2 | 61.6 | 72 | 3.45 | 3.35 | 3.1 | 5.9 | 0.02 | 15.5 | 11.2 | 90.4 | 0.68295 | 43.1 | 89.1 | 0.3565 | 0.05 | 14.05 | 13.1 | 14.04 | 0.94 | 1.413 | 2.775 | 8.645 | 3.133 | 35.21 | 5.3 | 11 | 2021-05-31
2021-06-01 | Click Here |  | 5.84 | 5.03 | 4.99 | 5.08 | 5.12 | 7.04 | 7.01 | 1.77 | 1.9 | 2.2 | 2.5 | 61 | 54 | 69 | 7 |  |  | 0.786 | 0.591 | 3.59 | 0.0138 | 0.662 | 0.622 | 10.9 | 34.1 | 29.8 | 29.7 | 37.1 | 21.8 | 68.2 | 59.6 | 59.4 | 74.2 | 3.11 | 3.2 | 3.1 | 5.9 | 0.025 | 16.5 | 11.3 | 97.02 | 0.81933 | 51.9 | 89.7 | 0.2845 | 0.0469 | 15.79 | 13.23 | 14.17 | 0.94 | 1.406 | 2.772 | 8.495 | 3.3293 | 34.27 | 5.3 | 11.3 | 2021-06-01
2021-06-02 | Click Here |  | 6.02 | 5.1 | 5.08 | 5.09 | 5.17 | 7.28 | 7.18 | 1.84 | 2.09 | 2.2 | 2.67 | 58 | 51 | 29 | 1 |  |  | 0.627 | 0.714 | 2.41 | 0.095 | 0.419 | 0.526 | 11.3 | 32.2 | 30.4 | 30.7 | 37.2 | 22.6 | 64.4 | 60.8 | 61.4 | 74.4 | 3.23 | 3.21 | 2.9 | 6 | 0.037 | 17.2 | 11.8 | 99.93 | 0.70882 | 57.8 | 88.6 | 0.2379 | 0.0522 | 16.39 | 13.67 | 14.62 | 0.95 | 1.424 | 2.549 | 9.773 | 3.3188 | 30.07 | 5.3 | 11.3 | 2021-06-02
2021-06-03 | Click Here |  | 5.98 | 5.12 | 5.07 | 5.17 | 5.21 | 7.2 | 7.42 | 1.71 | 1.93 | 2.2 | 2.6 | 54 | 47 | 10 |  |  |  | 0.414 | 0.552 | 0.454 | 0.098 | 0.591 | 0.576 | 16.5 | 35.1 | 31.4 | 31.8 | 38 | 33 | 70.2 | 62.8 | 63.6 | 76 | 3.23 | 3.46 | 3 | 6.1 | 0.027 | 17.6 | 12.6 | 90.41 | 0.0064307 | 58.2 | 90.5 | 0.234 | 0.0431 | 16.39 | 15.51 | 16.46 | 0.95 | 1.546 | 2.792 | 10 | 2.6464 | 30.23 | 5.3 | 11.3 | 2021-06-03
2021-06-04 | Click Here |  | 6.43 | 4,99 | 5.04 | 5.01 | 5.08 | 6.83 | 7.25 | 1.83 | 2.03 | 2.2 | 2.75 | 53 | 46 | 6 |  |  |  | 0.644 | 0.506 | 0.507 | 0.064 | 0.515 | 0.473 | 12.1 | 36.5 | 32.6 | 31.4 | 37.7 | 24.2 | 73 | 65.2 | 61.8 | 75.4 | 3.28 | 3.36 | 3 | 5.9 | 0.019 | 18.7 | 12.9 | 92.61 | 0.4922 | 58.4 | 88.4 | 0.234 | 0.0533 | 14.07 | 13.13 | 14.06 | 0.93 | 1.438 | 2.795 | 8.039 | 3.2022 | 32.18 | 5.3 | 11.3 | 2021-06-04
2021-06-05 | Click Here |  | 6.87 | 5.06 | 5.06 | 5.1 | 5.04 | 6.85 | 7.34 | 1.93 | 1.98 | 2.2 | 2.64 | 51 | 42 | 7 |  |  |  | 0.664 | 0.536 | 0.407 | 0.085 | 0.554 | 0.471 | 11.4 | 34.6 | 31.1 | 30.8 | 36.5 | 22.8 | 79.2 | 62.1 | 61.6 | 73 | 3.27 | 1.61 | 3 | 5.9 | 0.022 | 17.7 | 13.2 | 94.37 | 0.65886 | 58.6 | 88.5 | 0.2339 | 0.0526 | 13.6 | 12.68 | 13.59 | 0.91 |  |  |  | 3.3789 | 30.36 | 5.3 | 11.3 | 2021-06-05
2021-06-06 | Click Here | [41 empty] | 88.02 | 0.55151 |  |  |  |  | 12.42 | 12.29 | 12.29 |  | 1.359 | 2.806 | 6.08 | 3.2515 |  | 5.3 | 11.5 | 2021-06-06
2021-06-07 | Click Here |  | 6.24 | 5.09 | 5.11 | 5.14 | 5.1 | 6.89 | 6.99 | 1.94 | 2.17 | 2.2 | 2.74 | 49 | 40 | 6 |  |  |  | 0.45 | 0.497 | 0.386 | 0.079 | 0.477 | 0.451 | 11.6 | 33 | 31.6 | 32.2 | 40.1 | 23.2 | 66 | 63.2 | 64.4 | 80.2 | 3.37 | 1.7 | 3.1 | 6 | 0.039 | 17.5 | 14 | 102.8 | 0.67533 | 58.4 | 89.6 | 0.2347 | 0.0478 | 15.08 | 14.12 | 15.1 | 0.98 | 1.524 | 2.272 | 10 | 3.3053 | 30.48 | 5.3 | 11.5 | 2021-06-07
2021-06-08 | Click Here |  | 6.11 | 5.04 | 5.11 | 5.03 | 5.2 | 7.56 | 6.99 | 1.74 | 1.8 | 2.2 | 2.66 | 52 | 44 | 14 | 2 |  |  | 0.801 | 0.541 | 0.424 | 0.146 | 0.368 | 0.361 | 11.9 | 32.8 | 30.8 | 30.4 | 40 | 23.8 | 65.6 | 61.6 | 60.8 | 80 | 3.16 | 1.81 | 2.9 | 6.1 | 0.103 | 18 | 13.9 | 114.66 | 0.6941 | 55.4 | 89.5 | 0.2559 | 0.0481 | 16.54 | 15.52 | 16.56 | 0.94 | 1.614 | 2.728 | 10 | 3.3541 | 31.22 | 5.3 | 11.5 | 2021-06-08
2021-06-09 | Click Here |  | 6.36 | 5.07 | 5.06 | 5.09 | 5.12 | 7.09 | 7.66 | 1.74 | 1.93 | 2.2 | 2.83 | 52 | 46 | 6 |  |  |  | 0.737 | 0.668 | 0.42 | 0.128 | 0.897 | 0.848 | 12.1 | 33.2 | 31.9 | 31.1 | 38.1 | 24.2 | 66.4 | 63.8 | 62.2 | 76.2 | 3.21 | 1.64 | 3 | 5.9 | 0.126 | 18.9 | 14.6 | 110.91 | 0.42496 | 51.4 | 88.2 | 0.2883 | 0.0545 | 15.97 | 15.96 | 16.93 | 0.97 | 1.667 | 2.852 | 10 | 3.155 | 30.43 | 5.3 | 11.4 | 2021-06-09
2021-06-10 | Click Here |  | 6.36 | 5.12 | 5.07 | 5.04 | 5.09 | 7.06 | 7.11 | 1.74 | 1.97 | 2.2 | 2.71 | 47 | 42 | 7 |  |  |  | 0.612 | 0.513 | 0.409 | 0.088 | 0.392 | 0.246 | 12.2 | 32.6 | 32.4 | 31.4 | 37.9 | 24.4 | 65.2 | 64.8 | 62.8 | 75.8 | 3.23 | 1.59 | 3 | 5.9 | 0.105 | 18.8 | 14 | 105.84 | 0.64259 | 50.5 | 88.8 | 0.2929 | 0.0516 | 15.3 | 14.29 | 15.27 | 0.98 | 1.483 | 2.904 | 9.107 | 3.3626 | 30.84 | 5.3 | 11.4 | 2021-06-10
2021-06-11 | Click Here |  | 6.25 | 5.1 | 5.12 | 5.12 | 5.16 | 7.16 | 7.07 | 1.71 | 1.93 | 2.2 | 2.63 | 50 | 42 | 8 | 2 |  |  | 0.532 | 1 | 0.62 | 0.187 | 0.483 | 0.281 | 11.3 | 31.6 | 29.1 | 29.4 | 39.9 | 22.6 | 63.2 | 58.2 | 58.8 | 79.8 | 3.05 | 3.49 | 3.1 | 5.8 | 0.135 | 17 | 14.4 | 97.02 | 0.69751 | 54.2 | 88.8 | 0.266 | 0.0516 | 13.92 | 13.08 | 13.08 |  | 1.394 | 2.904 | 9.825 | 3.3675 | 30.51 | 5.1 | 11.4 | 2021-06-11
2021-06-12 | Click Here |  | 6.12 | 5.26 | 5.04 | 5.25 | 5.22 | 7.2 | 7.27 | 1.53 | 1.83 | 2.2 | 2.65 | 57 | 49 | 15 | 5 |  |  | 0.683 | 0.444 | 1.05 | 0.075 | 0.443 | 0.317 | 11.4 | 29.1 | 27.4 | 28.5 | 39.1 | 22.8 | 58.2 | 54.8 | 57 | 78.2 | 3.05 | 3.48 | 3.1 | 6 | 0.108 | 16.4 | 14 | 97.02 | 0.6969 | 53.9 | 91.3 | 0.2683 | 0.0392 | 14.26 | 13.2 | 14.18 | 0.98 |  |  |  | 3.3369 | 27.7 | 5.1 | 11.4 | 2021-06-12
2021-06-13 | Click Here | [58 empty] | 2021-06-13
2021-06-14 | Click Here |  | 6.22 | 5.14 | 5.38 | 5.17 | 5.16 | 7.25 | 7.32 | 1.66 | 2.07 | 2.2 | 2.64 | 51 | 43 | 16 | 1 |  |  | 0.596 | 0.555 | 0.655 | 0.09 | 0.661 | 0.329 | 11.5 | 30.5 | 28 | 27.3 | 37.8 | 23 | 61 | 56 | 54.6 | 75.6 | 3.08 | 3.51 | 5 | 5.9 | 0.191 | 15.8 | 13.8 | 102.8 | 0.73915 | 57.9 | 88 | 0.2368 | 0.0501 | 14.64 | 13.69 | 14.63 | 0.94 | 1.434 | 2.881 | 9.604 | 3.4091 | 28.2 | 5.1 | 11.4 | 2021-06-14
2021-06-15 | Click Here |  | 6.4 | 5.11 | 5.13 | 5.16 | 5.18 | 7.33 | 7.25 | 1.78 | 1.92 | 2.2 | 2.6 | 53 | 44 | 16 |  |  |  | 0.504 | 0.395 | 0.598 | 0.086 | 0.366 | 0.217 | 11.5 | 31.7 | 27.5 | 27.6 | 37.2 | 23 | 63.4 | 55 | 55.2 | 74.4 | 3.06 | 3.48 | 3 | 6 | 0.138 | 16.2 | 13.8 | 105.84 | 0.72586 | 56.2 | 87.6 | 0.2498 | 0.0572 | 15.13 | 14.15 | 15.1 | 0.95 | 1.516 | 2.865 | 10 | 3.3959 | 28.21 | 4.9 | 11.4 | 2021-06-15
2021-06-16 | Click Here |  | 6.19 | 5.11 | 5.04 | 5.12 | 5.16 | 7.23 | 7.24 | 1.26 | 1.72 | 2.2 | 2.65 | 51 | 43 | 14 |  |  |  | 0.536 | 0.37 | 0.594 | 0.091 | 0.331 | 0.279 | 11.7 | 30.2 | 28.5 | 28.1 | 38.5 | 23.4 | 60.4 | 57 | 56.2 | 77 | 3.16 | 3.35 | 3.1 | 5.9 | 0.124 | 16.4 | 13.8 | 97.02 | 0.53247 | 54.8 | 89.7 | 0.2606 | 0.047 | 15.42 | 14.43 | 15.39 | 0.96 | 1.499 | 2.867 | 9.538 | 3.0525 | 28.64 | 4.3 | 11.4 | 2021-06-16
2021-06-17 | Click Here |  | 6.16 | 5.12 | 5.2 | 5.09 | 5.15 | 7.35 | 7.24 | 1.76 | 1.98 | 2.2 | 2.67 | 46 | 39 | 15 |  |  |  | 0.458 | 0.35 | 0.935 | 0.076 | 0.275 | 0.241 | 12.3 | 31.7 | 29.6 | 29.3 | 40.8 | 24.6 | 63.4 | 59.2 | 58.6 | 81.6 | 2.99 | 3.26 | 3.1 | 6 | 0.176 | 17 | 13.9 | 130 | 0.95031 | 56.6 | 88.8 | 0.247 | 0.0512 | 16.9 | 15.95 | 16.92 | 0.97 | 1.591 | 2.855 | 10 | 3.7003 | 28.87 | 4.3 | 11.4 | 2021-06-17
2021-06-18 | Click Here |  | 6.09 | 5.04 | 5 | 5.34 | 5.39 | 7.2 | 7.37 | 1.72 | 1.94 | 2.2 | 2.74 | 57 | 50 | 17 | 1 |  |  | 0.417 | 0.364 | 0.891 | 0.104 | 0.322 | 0.173 | 12.3 | 30.3 | 29.1 | 29.2 | 40.2 | 24.6 | 60.6 | 58.2 | 58.4 | 80.4 | 3.12 | 3.33 | 3 | 5.9 | 0.034 | 17.8 | 14.5 | 128.15 | 0.65693 | 54.1 | 88 | 0.2661 | 0.0555 | 17.69 | 16.83 | 17.79 | 0.96 | 1.738 | 2.887 | 10 | 3.4569 | 28.15 | 4.6 | 11.4 | 2021-06-18
2021-06-19 | Click Here |  | 6.07 | 5.04 | 4.99 | 5.3 | 5.36 | 7.49 | 7.43 | 1.8 | 1.99 | 2.2 | 2.81 | 59 | 53 | 11 |  |  |  | 0.446 | 0.377 | 0.781 | 0.091 | 0.21 | 0.163 | 12.8 | 32.4 | 30.5 | 30.4 | 40.3 | 25.6 | 64.8 | 61 | 60.8 | 80.6 | 3.06 | 3.27 | 2.9 | 6 | 0.041 | 18.7 | 15.1 |  |  | 53.8 | 89.9 | 0.269 | 0.0492 | [8 empty] | 28.61 | 4.6 | 11.4 | 2021-06-19
2021-06-20 | Click Here | [58 empty] | 2021-06-20
2021-06-21 | Click Here |  | 5.91 | 5.09 | 4.96 | 4.87 | 5.06 | T OF SERV | 5.2 | 1.86 | 1.91 | 2.2 | 2.93 | 46 | 38 | 20 |  |  |  | 0.527 | 0.355 | 1.04 | 0.097 | 0.126 | 0.107 | 13 | 32.4 | 31.1 | 29.5 | 31.8 | 26 | 64.8 | 62.2 | 59 | 63.6 | 3.01 | 3.29 | 3 | 5.8 | 0.249 | 18.9 | 15.3 | 127.89 | 0.58094 | 55.7 | 92 | 0.254 | 0.036 | 17.57 | 16.68 | 17.63 | 0.95 | 1.987 | 2.9 | 10 | 3.4809 | 27.23 | 4.6 | 11.4 | 2021-06-21
2021-06-22 | Click Here |  | 6.31 | 5.18 | 5.06 | 5.12 | 5.14 | 7.21 | 7.63 | 1.6 | 1.81 | 2.2 | 2.93 | 44 | 37 | 12 |  |  |  | 0.518 | 0.377 | 1.35 | 0.109 | 0.259 | 0.21 | 13.3 | 33.6 | 31.6 | 31.9 | 43.1 | 26.6 | 67.2 | 63.2 | 63.8 | 86.2 | 2.86 | 3.36 | 3.1 | 5.9 | 0.103 | 20.1 | 15.6 | 144.78 | 0.46292 | 56 | 90.3 | 0.2512 | 0.0422 | 20.3 | 19.43 | 20.38 | 0.95 | 2.093 | 2.885 | 14.52 | 3.3829 | 28.17 | 4.6 | 11.4 | 2021-06-22
2021-06-23 | Click Here |  | 6.01 | 5.15 | 5.05 | 5.29 | 5.3 | 7.72 | 7.92 | 1.57 | 1.78 | 2.2 | 2.97 | 62 | 54 | 21 | 1 |  |  | 0.492 | 0.39 | 1.47 | 0.118 | 0.307 | 0.187 | 14.1 | 34.7 | 33.2 | 33.5 | 44.8 | 28.1 | 69.4 | 66.4 | 67 | 89.6 | 2.94 | 3.43 | 2.9 | 6 | 0.19 | 21.4 | 16.3 | 136.97 | 0.30326 | 56.2 | 89.5 | 0.2498 | 0.04778 | 19.21 | 18.38 | 19.31 | 0.93 | 1.541 | 2.807 | 14.032 | 3.3833 | 28.8 | 5 | 11.4 | 2021-06-23
2021-06-24 | Click Here |  | 6.09 | 5.1 | 5.19 | 5.33 | 5.36 | 7.71 | 7.83 | 1.69 | 2.01 | 2.2 | 3.18 | 61 | 57 | 19 |  |  |  | 0.388 | 0.421 | 1.24 | 0.137 | 0.296 | 0.204 | 14.4 | 35.2 | 32.9 | 33.3 | 42.7 | 28.8 | 70.4 | 65.8 | 66.6 | 85.7 | 3.03 | 3.26 | 3 | 6 | 0.172 | 21.6 | 16.5 |  |  | 56.4 | 90.6 | 0.2469 | 0.0421 | [8 empty] | 28.04 | 5 | 10.9 | 2021-06-24
2021-06-25 | Click Here |  | 6.57 | 5.2 | 5.21 | 5.13 | 5.21 | 7.21 | 7.83 | 1.62 | 1.91 | 2.2 | 3.21 | 49 | 43 | 24 | 3 | 1 | 0 | 0.621 | 0.448 | 0.96 | 0.08 | 0.31 | 0.16 | 14.4 | 36.6 | 33.8 | 32.1 | 41.1 | 28.8 | 73.2 | 67.6 | 64.2 | 82.2 | 3.09 | 3.33 | 3 | 6.1 | 0.116 | 21.4 | 17.2 | 148.75 | 0.2945 | 58.5 | 87.8 | 0.2322 | 0.0563 | 20.23 | 18.53 | 20.43 | 1.9 | 1.705 | 2.851 | 13.974 | 3.6445 | 29.79 | 5 | 10.6 | 2021-06-25
2021-06-26 | Click Here |  | 6.44 | 5.02 | 5.1 | 4.99 | 5.1 | 7.08 | 7.07 | 1.76 | 2.02 | 2.2 | 3.25 | 50 | 43 | 8 | 1 | 0 | 0 | 0.615 | 0.416 | 0.811 | 0.07 | 0.326 | 0.372 | 14.3 | 36.5 | 36.2 | 34.7 | 42.3 | 28.6 | 73 | 72.4 | 75.4 | 84.6 | 3.04 | 3.29 | 3 | 6 | 0.098 | 21.1 | 17.5 | 134.43 | 0.16786 | 57.5 | 90 | 0.2403 | 0.0455 | 18.4 | 17.65 | 18.55 | 0.9 | 0 | 0 | 0 | 3.4579 | 30.23 | 5 | 10.6 | 2021-06-26
2021-06-27 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 102.33 | 0.23898 | 0 | 0 | 0 | 0 | 14.54 | 13.37 | 14.37 | 0.9 | 1.447 | 2.947 | 9.156 | 3.449 | 0 | 5 | 10.8 | 2021-06-27
2021-06-28 | Click Here |  | 6.41 | 5.05 | 5.05 | 5 | 5.13 | 7.28 | 6.85 | 1.59 | 1.78 | 2.2 | 3.02 | 46 | 39 | 23 | 1 | 0 | 0 | 0.641 | 0.529 | 2.61 | 0.157 | 0.87 | 0.539 | 14.1 | 36.2 | 36.8 | 36.3 | 45.4 | 28.2 | 72.4 | 73.6 | 72.6 | 90.8 | 2.97 | 3.37 | 2.9 | 5.8 | 0.003 | 20.7 | 17.2 | 113.84 | 0.45422 | 59.5 | 89.7 | 0.2251 | 0.047 | 13.84 | 14.3 | 15.26 | 0.96 | 1.438 | 2.899 | 8.96 | 3.6142 | 30.58 | 5 | 10.8 | 2021-06-28
2021-06-29 | Click Here |  | 6.27 | 5.07 | 5.03 | 5.04 | 5.31 | 7.5 | 7.35 | 1.67 | 1.99 | 2.2 | 2.96 | 44 | 36 | 24 | 1 | 0 | 0 | 0.526 | 0.519 | 2.7 | 0.124 | 0.46 | 0.362 | 13.8 | 36.8 | 36.2 | 35.1 | 46 | 27.6 | 73.6 | 72.4 | 70.2 | 92 | 3.06 | 3.35 | 2.9 | 6.1 | 0.004 | 19.8 | 17.1 | 119.09 | 0.73368 | 60.9 | 90.6 | 0.2163 | 0.0428 | 17.94 | 14.14 | 16.04 | 1.9 | 1.561 | 2.813 | 10 | 3.8237 | 30.53 | 5 | 10.8 | 2021-06-29
2021-06-30 | Click Here |  | 6.43 | 5.04 | 5.05 | 5.06 | 5.07 | 7.26 | 7.51 | 1.68 | 2.01 | 2.2 | 3.14 | 51 | 44 | 7 | 0 | 0 | 0 | 0.684 | 0.573 | 0.449 | 0.138 | 0.516 | 0.374 | 13.7 | 35.2 | 34.2 | 32.7 | 44.2 | 27.4 | 70.4 | 68.4 | 65.4 | 88.4 | 3.1 | 3.29 | 3 | 6 | 0.085 | 19.7 | 17.4 | 120.42 | 0.32361 | 57.7 | 90.4 | 0.2384 | 0.0438 | 18.6 | 15.83 | 16.8 | 0.97 | 1.606 | 2.761 | 11.458 | 3.4536 | 30.62 | 5 | 10.8 | 2021-06-30
2021-07-01 | Click Here |  | 6.2 | 4.98 | 5.04 | 4.95 | 5.04 | 6.91 | 7.25 | 1.99 | 2.13 | 2.2 | 3.18 | 47 | 43 | 9 | 1 | 0 | 0 | 0.626 | 0.513 | 0.572 | 0.116 | 0.351 | 0.272 | 13.4 | 35.1 | 32.7 | 32.5 | 41.5 | 26.8 | 70.2 | 65.4 | 65 | 83 | 3.05 | 3.23 | 3 | 6 | 0.122 | 19.3 | 17.1 | 154.35 | 0.36022 | 53.9 | 86.7 | 0.268 | 0.0616 | 20.59 | 19.85 | 20.8 | 0.95 | 1.373 | 2.722 | 10 | 3.5302 | 29.69 | 5 | 10.8 | 2021-07-01
2021-07-02 | Click Here |  | 6.07 | 5.11 | 5.02 | 5.13 | 5.18 | 7.43 | 6.9 | 1.35 | 1.47 | 1.87 | 2.25 | 46 | 39 | 12 | 1 | 0 | 0 | 0.624 | 0.502 | 0.883 | 0.083 | 0.29 | 0.218 | 12.6 | 34.2 | 32 | 32.1 | 43.8 | 25.2 | 68.4 | 64 | 64.2 | 87.6 | 3.04 | 3.25 | 3 | 5.9 | 0.064 | 17.5 | 16.4 | 150 | 0.5193 | 58.3 | 90.5 | 0.2339 | 0.0432 | 23.03 | 22.26 | 23.17 | 0.91 | 1.317 | 2.676 | 10 | 3.0593 | 29.57 | 5.2 | 10.8 | 2021-07-02
2021-07-03 | Click Here |  | 6.33 | 5.17 | 5.17 | 5.19 | 5.23 | 7.59 | 7.69 | 1.31 | 1.66 | 2.2 | 2.56 | 45 | 37 | 28 | 0 | 0 | 0 | 0.636 | 0.492 | 0.722 | 0.08 | 0.215 | 0.154 | 12.5 | 30.4 | 29.8 | 31.7 | 44.5 | 25 | 60.8 | 59.6 | 63.4 | 89 | 2.9 | 3.69 | 3.1 | 6 | 0.194 | 17 | 16 | 0 |  | 57.8 | 89 | 0.2377 | 0.0506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29.11 | 5.2 | 10.8 | 2021-07-03
2021-07-04 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2021-07-04
2021-07-05 | Click Here |  | 6.52 | 5.16 | 5.07 | 5.17 | 5.2 | 6.96 | 7.47 | 1.94 | 2.18 | 2.2 | 2.54 | 45 | 40 | 8 | 0 | 0 | 0 | 0.633 | 0.536 | 0.544 | 0.09 | 0.3 | 0.201 | 13.1 | 34.2 | 30.4 | 30.7 | 41.3 | 26.2 | 68.4 | 60.8 | 61.4 | 82.6 | 2.95 | 3.76 | 3 | 6 | 0.152 | 17.2 | 16 | 108.11 | 1.2168 | 60.2 | 88.3 | 0.2203 | 0.0537 | 14.93 | 13.03 | 14.97 | 1.94 | 1.412 | 2.759 | 9.033 | 3.7668 | 27.42 | 5.2 | 9.9 | 2021-07-05
2021-07-06 | Click Here |  | 6.36 | 5.05 | 5.12 | 5.03 | 5.11 | 7.06 | 7.23 | 2.04 | 2.2 | 2.2 | 2.66 | 44 | 39 | 7 | 0 | 0 | 0 | ,591 | 0.463 | 0.536 | 0.082 | 0.322 | 0.264 | 12.6 | 33.6 | 30.7 | 30.5 | 42.4 | 25.2 | 67.2 | 61.4 | 61 | 84.8 | 2.98 | 3.71 | 3 | 5.9 | 0.211 | 16.9 | 15.8 | 116.87 | 1.0139 | 60 | 88.1 | 0.2205 | 0.0547 | 15.89 | 15.82 | 15.82 | 0 | 1.474 | 2.721 | 10 | 3.3539 | 28.68 | 5.1 | 9.9 | 2021-07-06
2021-07-07 | Click Here |  | 5.73 | 5.01 | 4.99 | 5 | 5.05 | 7.18 | 7.17 | 1.87 | 2.01 | 2.2 | 2.2 | 45 | 37 | 10 | 0 | 0 | 0 | 6.31 | 5.1 | 0.428 | 0.083 | 0.313 | 0.267 | 13 | 34.2 | 32.8 | 32.7 | 45.2 | 26 | 68.4 | 65.6 | 65.4 | 90.4 | 2.99 | 3.39 | 3.1 | 5.9 | 0.047 | 18.2 | 16.1 | 105.84 | 0.91315 | 58.5 | 89.9 | 0.2327 | 0.0463 | 16.73 | 15.79 | 16.74 | 0.95 | 1.539 | 2.707 | 10 | 3.0432 | 30.75 | 5.2 | 9.9 | 2021-07-07
2021-07-08 | Click Here |  | 6.01 | 5.08 | 5.1 | 5.03 | 5.1 | 7.08 | 7.22 | 1.85 | 2 | 2.2 | 2.24 | 44 | 35 | 9 | 0 | 0 | 0 | 3.38 | 3 | ,416 | 0.08 | 0.273 | 0.226 | 13.5 | 35.9 | 33.4 | 32.8 | 42.9 | 27.1 | 71.8 | 66.8 | 65.6 | 85.8 | 2.96 | 3.43 | 3 | 5.9 | 0.046 | 18.9 | 16.4 | 119.07 | 1.4305 | 58.1 | 90.1 | 0.2331 | 0.046 | 15.77 | 14.89 | 15.87 | 0.94 | 1.417 | 2.717 | 10 | 3.6305 | 0 | 5.2 | 9.9 | 2021-07-08
2021-07-09 | Click Here |  | 6.09 | 5.11 | 5.09 | 5.07 | 5.14 | 7.13 | 7.22 | 1.96 | 2.17 | 2.18 | 2.2 | 41 | 33 | 10 | 0 | 0 | 0 | 1.492 | 2.428 | 0.399 | 0.141 | 0.824 | 0.739 | 12.9 | 34.1 | 33 | 32.8 | 44.2 | 25.8 | 68.2 | 66 | 65.6 | 88.4 | 3.13 | 3.46 | 2.9 | 6.1 | 0.122 | 18 | 16.5 | 114.9 | 1.4425 | 60.3 | 90.3 | 0.2193 | 0.0439 | 15.39 | 14.4 | 15.4 | 1 | 1.338 | 2.721 | 8.435 | 3.6225 | 30.7 | 5.2 | 9.9 | 2021-07-09
2021-07-10 | Click Here |  | 6.14 | 5.07 | 5.1 | 5.01 | 5.08 | 7.04 | 7.15 | 1.84 | 2.07 | 1.97 | 2.02 | 41 | 32 | 8 | 0 | 0 | 0 | 0.924 | 1.662 | 0.468 | 0.087 | 0.392 | 0.303 | 13.2 | 34.7 | 33.1 | 33.8 | 44.6 | 26.2 | 69.4 | 66.2 | 67.6 | 89.2 | 3.27 | 3.46 | 3 | 5.9 | 0.097 | 18 | 16.4 | 101.43 | 1.4131 | 60.9 | 91.1 | 0.2109 | 0.0402 | 13.76 | 12.71 | 13.71 | 1 | 0 | 0 | 0 | 3.6231 | 29.66 | 5.2 | 9.9 | 2021-07-10
2021-07-11 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2021-07-11
2021-07-12 | Click Here |  | 6.33 | 5.1 | 5.04 | 5.09 | 5.15 | 7.33 | 7.2 | 1.78 | 2.04 | 2.18 | 2.21 | 42 | 35 | 10 | 0 | 0 | 0 | 0.684 | 1.346 | 0.629 | 0.077 | 0.275 | 0.219 | 13.7 | 36.2 | 34.6 | 34.4 | 46.2 | 27.4 | 72.4 | 69.2 | 68.8 | 92.4 | 2.91 | 3.71 | 3.1 | 5.9 | 0.13 | 19.8 | 16.8 | 94.81 | 1.0461 | 59.8 | 90.7 | 0.2231 | 0.0424 | 14.32 | 13.26 | 14.26 | 1 | 1.447 | 2.744 | 8.553 | 3.2461 | 30.98 | 5.2 | 9.9 | 2021-07-12
2021-07-13 | Click Here |  | 6.2 | 5.13 | 5.19 | 5.15 | 5.19 | 7.31 | 7.37 | 1.78 | 2.14 | 2.16 | 2.1 | 45 | 37 | 21 | 0 | 0 | 0 | 0.735 | 0.679 | 0.864 | 0.087 | 0.267 | 0.191 | 13 | 35.2 | 32.5 | 33.6 | 44.9 | 26 | 70.4 | 65 | 67.2 | 89.8 | 2.91 | 3.45 | 3.1 | 6 | 0.112 | 18.3 | 16.8 | 116.86 | 1.4651 | 59.9 | 90.3 | 0.2226 | 0.0441 | 15.8 | 14.84 | 15.83 | 0.99 | 1.435 | 2.716 | 10 | 3.5751 | 30.04 | 5.2 | 9.9 | 2021-07-13
2021-07-14 | Click Here |  | 6.19 | 5.13 | 5.09 | 5.12 | 5.18 | 7.4 | 7.14 | 1.68 | 2.08 | 2.2 | 1.99 | 42 | 35 | 23 | 0 | 0 | 0 | 0.746 | 0.58 | 1.34 | 0.079 | 0.53 | 0.396 | 13.3 | 35.3 | 33.6 | 33.1 | 42.7 | 26.6 | 70.6 | 67.2 | 66.2 | 85.4 | 2.93 | 3.37 | 3 | 5.9 | 0.048 | 19 | 16.8 | 125.69 | 1.3858 | 59.9 | 89.9 | 0.222 | 0.0461 | 17.33 | 16.37 | 17.36 | 0.99 | 1.67 | 3.1 | 10 | 3.4858 | 30.51 | 5.2 | 9.6 | 2021-07-14
2021-07-15 | Click Here |  | 6.02 | 5.05 | 5.1 | 5.06 | 5.12 | 6.92 | 7.17 | 1.92 | 2.04 | 2.2 | 2.17 | 41 | 34 | 21 | 0 | 0 | 0 | 0.662 | 0.54 | 1.15 | 0.084 | 0.39 | 0.372 | 13.6 | 36.1 | 34.9 | 33.9 | 42.9 | 27.2 | 72.2 | 69.8 | 67.8 | 85.8 | 3.11 | 3.7 | 3.1 | 6 | 0.032 | 20.1 | 17.2 | 116.86 | 1.2031 | 59.9 | 90 | 0.2219 | 0.0456 | 16.68 | 15.87 | 16.67 | 0.8 | 1.778 | 2.731 | 10 | 3.3431 | 30.04 | 5.2 | 9.4 | 2021-07-15
2021-07-16 | Click Here |  | 6.46 | 5.04 | 5.08 | 4.95 | 5.02 | 6.34 | 6.69 | 1.79 | 2.2 | 2.2 | 2.33 | 42 | 37 | 12 | 1 | 0 | 0 | 1.21 | 0.59 | 0.566 | 0.09 | 0.61 | 0.34 | 13.8 | 36.4 | 35.4 | 33.9 | 39.9 | 26.6 | 72.8 | 70.8 | 67.8 | 79.8 | 3.06 | 3.64 | 3 | 5.8 | 0.061 | 20.3 | 17.6 | 121.27 | 1.1833 | 62.8 | 89.5 | 0.202 | 0.0428 | 17.06 | 16.13 | 17.12 | 0.99 | 1.783 | 2.806 | 10 | 3.4133 | 29.53 | 5.2 | 9.5 | 2021-07-16
2021-07-17 | Click Here |  | 6.44 | 5.03 | 5.15 | 5.01 | 5.04 | 6.46 | 6.63 | 1.93 | 2.13 | 2.2 | 2.45 | 41 | 35 | 21 | 1 | 0 | 0 | 0.744 | 0.003 | 1.09 | 0.088 | 0.414 | 0.394 | 14.2 | 37.7 | 35.1 | 34.7 | 41 | 28.4 | 75.4 | 70.2 | 69.4 | 82 | 3.08 | 3.67 | 3.1 | 5.7 | 0.233 | 21 | 17.8 | 112.46 | 1.1758 | 62.6 | 88.4 | 0.2022 | 0.0535 | 15.47 | 14.44 | 15.45 | 1.01 | 0 | 0 | 0 | 3.5358 | 29.24 | 5.2 | 9.7 | 2021-07-17
2021-07-18 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2021-07-18
2021-07-19 | Click Here |  | 6.09 | 5.02 | 5.02 | 5.03 | 5.07 | 7.05 | 7.03 | 1.83 | 2.04 | 2.2 | 2.33 | 46 | 38 | 31 | 0 | 0 | 0 | 0.628 | 0.549 | 0.98 | 0.086 | 0.447 | 0.418 | 14.6 | 38.1 | 36.9 | 37.4 | 44.6 | 29.2 | 76.2 | 73.8 | 74.8 | 89.2 | 2.91 | 3.63 | 3 | 6 | 0.032 | 21.3 | 18.2 | 0 |  | 60.9 | 90.8 | 0.2154 | 0.0419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30.98 | 5.3 | 9.9 | 2021-07-19
2021-07-20 | Click Here |  | 6.14 | 5.04 | 5.02 | 5.08 | 5.12 | 7.04 | 6.97 | 1.88 | 2.12 | 2.2 | 2.47 | 44 | 36 | 29 | 0 | 0 | 0 | 0.59 | 0.53 | 0.99 | 0.1 | 0.39 | 0.42 | 15.1 | 37.6 | 37.1 | 37.7 | 43.6 | 30.2 | 75.2 | 74.2 | 75.4 | 87.2 | 2.92 | 3.55 | 3.1 | 6 | 0.047 | 22.3 | 18.7 | 119.07 | 1.2653 | 61 | 91.2 | 0.2142 | 0.0378 | 16.42 | 14.55 | 16.56 | 2.01 | 1.603 | 2.919 | 7.801 | 3.7153 | 30.72 | 5.3 | 9.9 | 2021-07-20
2021-07-21 | Click Here |  | 6.37 | 5 | 5.03 | 5.04 | 5.08 | 6.68 | 6.9 | 1.78 | 2.2 | 2.2 | 2.45 | 46 | 38 | 15 | 1 | 0 | 0 | 0.731 | 0.55 | 0.713 | 0.09 | 0.42 | 0.39 | 15.2 | 38 | 36.1 | 36.2 | 42.5 | 30.4 | 76 | 72.2 | 72.4 | 85 | 3.14 | 3.59 | 3.1 | 5.7 | 0.15 | 21.8 | 18.9 | 113.99 | 1.4758 | 59.8 | 88.1 | 0.2145 | 0.0548 | 14.31 | 13.25 | 14.26 | 1.01 | 1.375 | 2.808 | 7.823 | 3.9058 | 29.02 | 5.3 | 9.9 | 2021-07-21
2021-07-22 | Click Here |  | 6.36 | 4.96 | 5.04 | 4.94 | 4.99 | 6.63 | 6.97 | 2.02 | 2.2 | 2.2 | 2.41 | 45 | 36 | 11 | 0 | 0 | 0 | 0.694 | 0.53 | 0.804 | 0.09 | 0.52 | 0.5 | 14.5 | 37.4 | 35 | 35.5 | 42.4 | 29 | 74.8 | 70 | 71 | 84.8 | 3.25 | 3.71 | 3 | 5.8 | 0.053 | 20.5 | 18.4 | 110.25 | 1.5141 | 60.2 | 90.2 | 0.2204 | 0.0447 | 14.03 | 12.92 | 13.92 | 1 | 1.344 | 2.723 | 8.235 | 3.8741 | 29.7 | 5.3 | 10.1 | 2021-07-22
2021-07-23 | Click Here |  | 5.98 | 5.07 | 5.11 | 5.1 | 5.14 | 6.92 | 6.99 | 2.1 | 2.2 | 2.2 | 2.23 | 44 | 36 | 19 | 0 | 0 | 0 | 0.674 | 0.531 | 1.76 | 0.095 | 0.4 | 0.336 | 13.9 | 35 | 33.4 | 33.5 | 43.8 | 27.8 | 70 | 66.8 | 67 | 87.6 | 2.99 | 3.54 | 3 | 5.9 | 0.027 | 19.3 | 18.3 | 103.64 | 1.5122 | 61.5 | 90.4 | 0.2106 | 0.0436 | 13.57 | 12.54 | 13.54 | 1 | 1.325 | 2.709 | 7.049 | 3.7522 | 29.81 | 5.3 | 10.3 | 2021-07-23
2021-07-24 | Click Here |  | 6.08 | 5.07 | 5.15 | 5.09 | 5.1 | 6.76 | 6.77 | 1.69 | 2.04 | 2.2 | 2.11 | 40 | 33 | 21 | 0 | 0 | 0 | 0.662 | 0.516 | 1.33 | 0.111 | 0.436 | 0.443 | 13.7 | 35.3 | 33.6 | 33.5 | 42.7 | 27.4 | 70.6 | 67.2 | 67 | 85.4 | 2.8 | 3.37 | 3.1 | 6 | 0.022 | 18.8 | 17.7 | 100.3 | 1.4258 | 61.5 | 89.9 | 0.2107 | 0.0459 | 13.44 | 12.49 | 13.39 | 0.9 | 0 | 0 | 0 | 3.6458 | 30.04 | 5.3 | 10.3 | 2021-07-24
2021-07-25 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2021-07-25
2021-07-26 | Click Here |  | 6.43 | 5.05 | 5.09 | 5.06 | 5.07 | 6.71 | 6.85 | 1.88 | 2.16 | 2.2 | 2.38 | 41 | 35 | 18 | 0 | 0 | 0 | 0.583 | 0.471 | 0.96 | 0.09 | 0.473 | 0.514 | 14.3 | 36.9 | 34.3 | 34.7 | 41.6 | 28.6 | 73.8 | 68.6 | 69.4 | 83.2 | 2.85 | 3.47 | 3 | 5.8 | 0.168 | 20 | 17.9 | 119.64 | 1.3408 | 62.8 | 85.3 | 0.2018 | 0.0688 | 16.53 | 14.96 | 16.61 | 1.65 | 1.425 | 2.669 | 10.866 | 3.6308 | 29.53 | 5.3 | 10.3 | 2021-07-26
2021-07-27 | Click Here |  | 6.59 | 4.88 | 5.23 | 4.92 | 4.99 | 6.41 | 6.69 | 1.94 | 2.1 | 2.2 | 2.18 | 47 | 39 | 12 | 0 | 0 | 0 | 0.754 | 0.49 | 0.769 | 0.075 | 0.828 | 1.249 | 14.5 | 36.5 | 35.4 | 34.9 | 40 | 29 | 73 | 70.8 | 69.8 | 80 | 2.8 | 3.43 | 3 | 5.7 | 0.173 | 20.4 | 18.1 | 110.25 | 1.2281 | 58.4 | 86.9 | 0.2334 | 0.0608 | 15.89 | 14.95 | 15.9 | 0.95 | 1.388 | 2.652 | 10 | 3.3481 | 30.69 | 5.3 | 10.3 | 2021-07-27
2021-07-28 | Click Here |  | 6.17 | 4.96 | 4.95 | 5.01 | 5.05 | 6.63 | 6.73 | 1.74 | 1.86 | 2.2 | 2.03 | 35 | 28 | 22 | 4 | 0 | 0 | 0.643 | 0.519 | 1.41 | 0.109 | 0.521 | 0.464 | 14.8 | 37.2 | 36.2 | 36.2 | 42.5 | 29.6 | 74.4 | 72.4 | 72.4 | 85 | 3.11 | 3.78 | 3.1 | 6 | 0.014 | 21 | 18.3 | 101.43 | 0.90557 | 61.8 | 90.2 | 0.2088 | 0.0444 | 16.15 | 15.22 | 16.18 | 0.96 | 1.36 | 2.622 | 10 | 3.0256 | 30.04 | 5.5 | 10.8 | 2021-07-28
2021-07-29 | Click Here |  | 6.36 | 4.97 | 4.98 | 5 | 5.04 | 6.71 | 6.81 | 1.74 | 1.94 | 2.2 | 2.12 | 41 | 33 | 22 | 0 | 0 | 0 | 0.608 | 0.497 | 1.25 | 0.084 | 0.46 | 0.465 | 14.5 | 37.9 | 36.7 | 36.5 | 43.5 | 29 | 75.8 | 73.4 | 73 | 47 | 2.99 | 3.51 | 3.1 | 5.9 | 0.008 | 20.8 | 18.5 | 115.52 | 1.0902 | 62.4 | 90.8 | 0.2043 | 0.0417 | 16.48 | 15.47 | 16.5 | 1.03 | 1.422 | 2.616 | 11.443 | 3.3902 | 30.51 | 5.5 | 11 | 2021-07-29
2021-07-30 | Click Here |  | 6.28 | 4.98 | 4.91 | 5.04 | 5.09 | 6.77 | 6.64 | 1.78 | 2.01 | 2.2 | 2.43 | 54 | 47 | 17 | 0 | 0 | 0 | 0.514 | 0.492 | 1.31 | 0.104 | 0.492 | 0.676 | 14.6 | 37.3 | 36.6 | 37.1 | 41.9 | 29.2 | 74.6 | 73.2 | 74.2 | 83.8 | 3.04 | 3.57 | 3 | 5.8 | 0.021 | 20.2 | 18.6 | 108.6 | 0.92795 | 62 | 91.1 | 0.2093 | 0.0372 | 16.05 | 14.95 | 16.02 | 1.07 | 1.419 | 2.601 | 10.93 | 3.298 | 30.54 | 5.5 | 11 | 2021-07-30
2021-07-31 | Click Here |  | 6.24 | 4.91 | 4.88 | 5.01 | 5.06 | 6.77 | 6.7 | 1.7 | 1.96 | 2.19 | 2.3 | 51 | 43 | 17 | 1 | 0 | 0 | 0.526 | 0.471 | 1.31 | 0.098 | 0.512 | 0.596 | 14.4 | 38.2 | 35.9 | 36.7 | 42.1 | 28.8 | 76.4 | 71.8 | 73.4 | 84.2 | 3.11 | 3.51 | 3 | 5.8 | 0.031 | 20.4 | 18.7 | 99.23 | 0.9133 | 61.7 | 90.9 | 0.2061 | 0.0389 | 15.04 | 14.02 | 15.05 | 1.03 | 0 | 0 | 0 | 3.2133 | 29.68 | 5.7 | 11 | 2021-07-31
2021-08-01 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2021-08-01
2021-08-02 | Click Here |  | 6.1 | 4.94 | 4.88 | 5.01 | 5.08 | 7.01 | 7.08 | 1.55 | 1.82 | 2.3 | 2.41 | 39 | 32 | 24 | 2 | 0 | 0 | 0.668 | 0.594 | 1.45 | 0.108 | 0.581 | 0.5 | 14.2 | 37.2 | 35.2 | 35.4 | 45.3 | 28.4 | 74.4 | 70.4 | 70.8 | 90.6 | 3.78 | 3.95 | 3.1 | 6 | 0.028 | 20 | 18.3 | 105.84 | 0.71234 | 62.4 | 90.5 | 0.2042 | 0.0432 | 16.68 | 15.64 | 16.7 | 1.06 | 1.421 | 2.58 | 10 | 3.0723 | 30.51 | 5.9 | 11.3 | 2021-08-02
2021-08-03 | Click Here |  | 6.36 | 5.01 | 4.93 | 5.08 | 5.07 | 7.22 | 7.16 | 1.58 | 1.72 | 2.1 | 2.18 | 38 | 30 | 27 | 3 | 0 | 0 | 0.738 | 0.545 | 2.79 | 0.224 | 0.601 | 0.51 | 14.1 | 38.4 | 36.4 | 36.1 | 47.9 | 28.2 | 76.8 | 72.8 | 72.2 | 95.8 | 3.38 | 3.5 | 3 | 5.9 | 0.018 | 20.1 | 18.3 | 108.04 | 1.0077 | 63 | 89.6 | 0.2004 | 0.0475 | 15.99 | 14.74 | 15.25 | 0.51 | 1.365 | 2.377 | 10 | 3.3277 | 30.04 | 5.9 | 11.3 | 2021-08-03
2021-08-04 | Click Here |  | 6.29 | 5.04 | 5.01 | 5.19 | 5.23 | 7.54 | 7.69 | 1.77 | 2.04 | 2.2 | 2.41 | 42 | 34 | 19 | 1 | 0 | 0 | 0.592 | 0.514 | 1.32 | 0.144 | 0.392 | 0.417 | 14.3 | 37.2 | 35.8 | 35.4 | 46.7 | 28.6 | 74.4 | 71.6 | 70.8 | 93.4 | 3.27 | 3.61 | 2.9 | 6 | 0.024 | 20.2 | 18.4 | 128.29 | 0.73855 | 62.9 | 90.4 | 0.2017 | 0.0429 | 19.1 | 18.44 | 19.04 | 0.6 | 1.373 | 2.17 | 14.9 | 3.1585 | 30.38 | 5.9 | 11.3 | 2021-08-04
2021-08-05 | Click Here |  | 6.16 | 5.04 | 4.99 | 5.2 | 5.24 | 7.37 | 7.45 | 1.7 | 1.91 | 2.2 | 2.45 | 36 | 29 | 17 | 1 | 0 | 0 | 0.441 | 0.496 | 1.24 | 0.126 | 0.376 | 0.407 | 14.6 | 36.8 | 34.4 | 34 | 45.3 | 29.2 | 73.6 | 65.8 | 68 | 90.6 | 3.23 | 3.46 | 3 | 5.9 | 0.019 | 19.9 | 18 | 103.64 | 0.87608 | 62.4 | 90 | 0.208 | 0.0454 | 18.47 | 14.54 | 16.49 | 1.95 | 1.373 | 2.17 | 15.972 | 3.2361 | 30.75 | 5.9 | 11.3 | 2021-08-05
2021-08-06 | Click Here |  | 5.84 | 4.69 | 4.95 | 4.84 | 4.93 | 7.36 | 7.48 | 1.77 | 1.83 | 2.2 | 2.37 | 35 | 29 | 5 | 0 | 0 | 0 | 0.65 | 0.5 | 0.3 | 0.09 | 0.18 | 0.23 | 15 | 40.2 | 37.4 | 36.1 | 47 | 30 | 80.4 | 74.8 | 72.2 | 94 | 3.27 | 3.6 | 3 | 6.1 | 0.19 | 21.1 | 19 | 94.28 | 0.8243 | 61.7 | 89 | 0.2093 | 0.0503 | 15.18 | 14.2 | 15.27 | 1.07 | 1.373 | 2.17 | 15.972 | 3.0143 | 30.63 | 5.9 | 11 | 2021-08-06
2021-08-07 | Click Here |  | 6.45 | 5 | 5.19 | 4.95 | 5.02 | 7.14 | 7.512 | 1.56 | 1.7 | 2.03 | 2.28 | 39 | 31 | 7 | 0 | 0 | 0 | 0.694 | 0.643 | 0.587 | 0.09 | 0.261 | 0.321 | 14.8 | 37.2 | 37.8 | 35.5 | 44.4 | 29.6 | 74.4 | 75.6 | 71 | 88.8 | 3.23 | 3.58 | 3 | 6.1 | 0.052 | 22.2 | 19.6 | 89.09 | 0.60451 | 64 | 91.3 | 0.1935 | 0.0391 | 15.17 | 14.12 | 15.16 | 1.04 | 0 | 0 | 0 | 2.8645 | 30.6 | 5.5 | 11 | 2021-08-07
2021-08-08 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 89.32 | 0.81439 | 0 | 0 | 0 | 0 | 13.43 | 13.32 | 13.32 | 0 | 1.235 | 2.653 | 7.332 | 3.0444 | 0 | 5.5 | 11 | 2021-08-08
2021-08-09 | Click Here |  | 6.29 | 5.06 | 5.01 | 5.09 | 5.12 | 7.4 | 7.5 | 1.62 | 1.84 | 2.01 | 2.29 | 40 | 33 | 10 | 0 | 0 | 0 | 0.512 | 0.575 | 0.412 | 0.087 | 0.299 | 0.387 | 13.9 | 35.1 | 35.3 | 36.4 | 44.3 | 27.8 | 70.2 | 70.6 | 72.8 | 88.6 | 3.29 | 3.61 | 2.9 | 6 | 0.041 | 21.1 | 19.9 | 95.59 | 0.87096 | 64.1 | 91.8 | 0.1929 | 0.037 | 15 | 13.95 | 15 | 1.05 | 1.423 | 2.639 | 8.841 | 3.111 | 30.23 | 5.5 | 11 | 2021-08-09
2021-08-10 | Click Here |  | 6.58 | 5.04 | 5.05 | 5.01 | 5.1 | 7.45 | 7.51 | 1.34 | 1.57 | 2.01 | 2.25 | 37 | 30 | 6 | 0 | 0 | 0 | 0.476 | 0.573 | 0.541 | 0.092 | 0.393 | 0.324 | 14.3 | 37.2 | 36.4 | 36.1 | 47 | 28.6 | 74.4 | 72.8 | 72.2 | 94 | 3.16 | 3.58 | 2.9 | 6 | 0.041 | 21 | 19.7 | 0 |  | 64.8 | 90.1 | 0.1883 | 0.0452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 31.64 | 5.5 | 11 | 2021-08-10
2021-08-11 | Click Here |  | 6.57 | 5.05 | 5.01 | 5.07 | 5.1 | 7.01 | 7.34 | 2.2 | 2.2 | 2.2 | 1.58 | 30 | 26 | 20 | 3 | 1 | 0 | 0.6 | 0.5 | 1.2 | 0.179 | 0.46 | 0.34 | 14.3 | 37.4 | 35 | 35.1 | 45.9 | 28.6 | 74.8 | 70 | 70.2 | 91.8 | 3.25 | 3.65 | 3 | 6 | 0.02 | 21.1 | 19.6 | 109.83 | 1.3895 | 62.1 | 87.4 | 0.2063 | 0.0585 | 13.66 | 12.53 | 13.57 | 1.04 | 1.493 | 2.724 | 10.197 | 3.9795 | 31.41 | 5.5 | 11 | 2021-08-11
2021-08-12 | Click Here |  | 6.58 | 5.1 | 5.11 | 5.09 | 5.14 | 7.03 | 7.5 | 1.66 | 1.76 | 2.04 | 1.94 | 37 | 31 | 27 | 2 | 0 | 0 | 0.61 | 0.53 | 1.52 | 0.149 | 0.336 | 0.213 | 14.6 | 36 | 34.2 | 34.3 | 43.8 | 29.2 | 72 | 68.4 | 68.6 | 87.6 |  |  | 3.1 | 5.9 | 0.167 | 20.7 | 19.4 | 94.82 | 1.0102 | 60.9 | 89.3 | 0.2152 | 0.049 | 14.52 | 13.41 | 14.48 | 1.07 | 1.323 | 2.745 | 8.559 | 3.2102 | 30.1 | 5.3 | 11 | 2021-08-12
2021-08-13 | Click Here |  | 5.96 | 5.08 | 5.05 | 5.09 | 5.14 | 7.16 | 7.22 | 1.7 | 1.84 | 2.15 | 2.05 | 35 | 28 | 14 | 0 | 0 | 0 | 0.67 | 0.51 | 0.722 | 0.075 | 0.241 | 0.17 | 14.2 | 36.2 | 33 | 32.9 | 45.1 | 28.4 | 72.4 | 66 | 65.8 | 90.2 | 3 | 3.51 | 3.1 | 5.9 | 0.138 | 21 | 19.3 | 92.61 | 0.64226 | 63.5 | 90.9 | 0.1951 | 0.0412 | 14.39 | 14.29 | 14.29 | 0 | 1.37 | 2.791 | 9.666 | 2.9423 | 30.04 | 5.2 | 11 | 2021-08-13
2021-08-14 | Click Here |  | 6.4 | 5.09 | 5.11 | 5.11 | 5.12 | 7.2 | 7.16 | 1.51 | 1.76 | 2.13 | 2.25 | 38 | 30 | 11 | 0 | 0 | 0 | 0.633 | 0.56 | 0.114 | 0.076 | 0.204 | 0.186 | 14.6 | 35.6 | 34.7 | 34.4 | 45.9 | 29.2 | 71.2 | 69.4 | 68.8 | 91.8 | 2.84 | 2.16 | 3.1 | 6 | 0.112 | 21.6 | 19.5 | 99.22 | 0.93562 | 63.1 | 90.3 | 0.2004 | 0.0421 | 14.78 | 13.71 | 14.73 | 1.02 | 0 | 0 | 0 | 3.2856 | 29.81 | 5.2 | 11 | 2021-08-14
2021-08-15 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2021-08-15
2021-08-16 | Click Here |  | 6.6 | 5.12 | 5.02 | 5.01 | 5.33 | 7.06 | 7.52 | 1.56 | 1.74 | 2.16 | 1.75 | 39 | 31 | 25 | 2 | 1 | 0 | 0.614 | 0.538 | 1.55 | 0.09 | 0.168 | 0.265 | 15.1 | 37.8 | 35.5 | 33.8 | 48.1 | 30.2 | 75.6 | 71 | 67.6 | 96.2 | 2.88 | 2.68 | 3 | 5.9 | 0.081 | 23.1 | 20.6 | 103.63 | 1.144 | 63.4 | 89.7 | 0.1976 | 0.0469 | 15.65 | 14.37 | 15.67 | 1.3 | 1.37 | 2.791 | 9.666 | 3.274 | 30.55 | 5.2 | 11 | 2021-08-16
2021-08-17 | Click Here |  | 6.54 | 5.07 | 5.16 | 5.04 | 5.14 | 7.34 | 7.32 | 1.58 | 1.79 | 1.99 | 1.91 | 35 | 29 | 7 | 0 | 0 | 0 | 0.569 | 0.484 | 0.622 | 0.079 | 0.209 | 0.185 | 15.3 | 37.3 | 35.7 | 35.4 | 47.2 | 30.6 | 74.6 | 71.4 | 70.8 | 94.4 | 2.83 | 2.4 | 3.1 | 6.1 | 0.171 | 22.1 | 20.6 | 97.02 | 1.0988 | 61.2 | 90.6 | 0.2129 | 0.0428 | 14.56 | 13.6 | 14.64 | 1.04 | 1.37 | 2.791 | 9.666 | 3.2388 | 30.42 | 5 | 11 | 2021-08-17
2021-08-18 | Click Here |  | 6.16 | 4.94 | 5.02 | 5.03 | 5.06 | 5.52 | 4.78 | 1.77 | 1.88 | 2.13 | 2.26 | 34 | 26 | 17 | 1 | 0 | 0 | 0.555 | 0.491 | 1.58 | 0.093 | 0.295 | 0.247 | 14.9 | 36.9 | 35.7 | 35.1 | 36.2 | 29.8 | 73.8 | 71.4 | 70.2 | 72.4 | 3.01 | 2.81 | 3.1 | 5.8 | 0.147 | 21.7 | 20.6 | 99.22 | 0.6574 | 63.6 | 89 | 0.1966 | 0.0502 | 16.79 | 15.82 | 16.87 | 1.05 | 1.37 | 2.791 | 9.666 | 2.8474 | 29.81 | 5 | 11 | 2021-08-18
2021-08-19 | Click Here |  | 6.52 | 5.07 | 5.01 | 5.13 | 5.09 | 7.12 | 7.61 | 1.39 | 1.57 | 2.11 | 2.5 | 31 | 24 | 13 | 0 | 0 | 0 | 0.577 | 0.47 | 1.23 | 0.113 | 0.435 | 0.534 | 15.2 | 38 | 35.9 | 37 | 46.9 | 30.4 | 76 | 71.8 | 74 | 93.8 | 3 | 2.97 | 3.1 | 5.9 | 0.172 | 22.6 | 20.2 | 116.8 | 0.97865 | 64.9 | 89.4 | 0.1878 | 0.0437 | 17.49 | 16.63 | 17.62 | 0.99 | 1.37 | 2.791 | 9.666 | 3.1886 | 30.51 | 5 | 11 | 2021-08-19
2021-08-20 | Click Here |  | 6.61 | 5.06 | 5.13 | 5.04 | 5.08 | 7.1 | 7.24 | 1.59 | 1.71 | 1.99 | 2.36 | 32 | 27 | 11 | 1 | 0 | 0 | 0.417 | 0.156 | 1.19 | 0.103 | 0.314 | 0.297 | 15.7 | 36.1 | 36.6 | 37.1 | 47.4 | 31.4 | 72.2 | 73.2 | 74.2 | 94.8 |  |  | 3 | 6 | 0.141 | 23.5 | 21 | 94.22 | 1.7416 | 65.1 | 89.7 | 0.1876 | 0.0435 | 14.67 | 13.53 | 14.64 | 1.11 | 1.37 | 2.791 | 9.666 | 3.1616 | 30.51 | 5 | 10.5 | 2021-08-20
2021-08-21 | Click Here |  | 6.51 | 5.06 | 5.1 | 5.08 | 5.14 | 6.86 | 6.98 | 1.61 | 1.79 | 1.99 | 0.96 | 46 | 39 | 6 | 0 | 0 | 0 | 0.571 | 0.216 | 0.474 | 0.103 | 0.268 | 0.224 | 14.7 | 34.5 | 34.1 | 34.7 | 42.1 | 29.4 | 69 | 68.2 | 69.4 | 84.2 |  |  | 3.1 | 6 | 0.136 | 21.7 | 21.7 | 92.61 | 2.0732 | 68.5 | 89.4 | 0.1895 | 0.0485 | 13.83 | 12.69 | 13.69 | 1 | N/a | 0 | 0 | 3.3132 | 31.07 | 5 | 10.5 | 2021-08-21
2021-08-22 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2021-08-22
2021-08-23 | Click Here |  | 6.14 | 5.13 | 5.08 | 5.05 | 5.07 | 6.72 | 6.87 | 1.64 | 1.93 | 2.1 | 1.57 | 33 | 26 | 32 | 1 | 0 | 0 | 0.537 | 0.486 | 0.587 | 0.093 | 0.28 | 0.221 | 13.6 | 33.9 | 33.7 | 31.8 | 43.2 | 27.2 | 67.8 | 67.4 | 63.6 | 86.4 |  |  | 3.1 | 5.8 | 0.111 | 22 | 20.7 | 94.82 | 1.0414 | 64.6 | 90.9 | 0.1898 | 0.0413 | 14.33 | 13.24 | 14.28 | 1.04 | N/A | 0 | 0 | 3.2514 | 30.98 | 4.9 | 10.8 | 2021-08-23
2021-08-24 | Click Here |  | 6.23 | 5.1 | 5.06 | 5.05 | 5.12 | 7.13 | 6.96 | 1.8 | 1.91 | 2.22 | 1.8 | 32 | 26 | 10 | 0 | 0 | 0 | 0.563 | 0.429 | 1.03 | 0.159 | 0.263 | 0.231 | 13.5 | 33.7 | 32.12 | 31.2 | 44.7 | 27 | 67.4 | 64.2 | 62.4 | 89.4 |  |  | 3.1 | 6 | 0.046 | 21.8 | 21 | 95.5 | 0.72318 | 65.1 | 91 | 0.1861 | 0.041 | 14.43 | 13.41 | 14.46 | 1.05 | 1.695 | 2.439 | 8.99 | 3.2332 | 31.92 | 4.9 | 11 | 2021-08-24
2021-08-25 | Click Here |  | 6.19 | 5.02 | 4.99 | 5 | 5.04 | 5.69 | 5.57 | 1.65 | 1.94 | 2.01 | 1.13 | 33 | 26 | 12 | 0 | 0 | 0 | 0.463 | 0.414 | 0.986 | 0.124 | 0.088 | 0.071 | 13.8 | 32.3 | 31.7 | 33 | 34.2 | 27.6 | 64.6 | 63.4 | 66 | 68.4 |  |  | 3 | 5.8 | 0.057 | 21.2 | 21 | 99.16 | 0.96332 | 68.4 | 92.3 | 0.1644 | 0.0346 | 14.99 | 14.01 | 15.09 | 1.08 | 1.752 | 2.453 | 9.167 | 3.2133 | 31.25 | 4.9 | 11 | 2021-08-25
2021-08-26 | Click Here |  | 6.21 | 4.94 | 4.96 | 4.89 | 4.96 | 5.39 | 5.15 | 1.83 | 1.99 | 2.2 | 3.29 | 40 | 32 | 15 | 0 | 0 | 0 | 0.468 | 0.393 | 0.991 | 0.127 | 0.176 | 0.119 | 14.1 | 35.3 | 34.1 | 32.9 | 34.4 | 28.2 | 70.6 | 68.2 | 65.8 | 68.8 |  |  | 2.9 | 6 | 0.031 | 21.4 | 21 | 108.44 | 1.4393 | 69 | 88.6 | 0.1607 | 0.0525 | 14.91 | 13.91 | 14.98 | 1.07 | 1.747 | 2.405 | 9.433 | 3.5393 | 32.27 | 4.9 | 11 | 2021-08-26
2021-08-27 | Click Here |  | 6.19 | 5.07 | 5.16 | 4.94 | 4.98 | 6.01 | 6.24 | 1.74 | 1.88 | 2.2 | 4.9 | 39 | 33 | 14 | 0 | 0 | 0 | 0.346 | 0.394 | 1.14 | 0.141 | 0.104 | 0.091 | 14.4 | 34.9 | 33.6 | 33.1 | 37.1 | 28.8 | 69.8 | 67.2 | 66.2 | 74.2 |  |  | 3 | 5.8 | 0.062 | 21.2 | 20.8 | 95.38 | 1.0137 | 68.8 | 90.6 | 0.1617 | 0.0428 | 13.44 | 12.43 | 13.5 | 1.07 | 1.674 | 2.341 | 8.54 | 3.4837 | 30.5 | 4.9 | 11 | 2021-08-27
2021-08-28 | Click Here |  | 6.17 | 5.01 | 5.1 | 5.04 | 5.06 | 5.95 | 6.14 | 1.97 | 2.13 | 2.2 | 4.25 | 37 | 30 | 15 | 1 | 0 | 0 | 0.398 | 0.43 | 1.2 | 0.101 | 0.112 | 0.093 | 14.1 | 35.3 | 33 | 30.6 | 36 | 28.2 | 70.6 | 66 | 61.2 | 72 |  |  | 3.1 | 6 | 0.037 | 20.7 | 20.6 | 92.73 | 1.1838 | 67.8 | 91.2 | 0.1685 | 0.0396 | 12.75 | 11.78 | 12.84 | 1.06 | 0 | 0 | 0 | 3.5738 | 30.44 | 4.9 | 11 | 2021-08-28
2021-08-29 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 102.18 | 0.70437 | 0 | 0 | 0 | 0 | 14.31 | 13.2 | 14.26 | 1.06 | 1.641 | 2.341 | 8.589 | 3.5144 | 0 | 4.9 | 11 | 2021-08-29
2021-08-30 | Click Here |  | 6.51 | 4.99 | 5.18 | 5.04 | 5.14 | 7.01 | 7.66 | 1.79 | 1.94 | 2.09 | 1.59 | 41 | 34 | 17 | 1 | 0 | 0 | 0.396 | 0.454 | 1.29 | 0.128 | 0.246 | 0.271 | 14.2 | 35.3 | 32.9 | 33.5 | 46.6 | 28.4 | 70.6 | 65.8 | 67 | 93.2 |  |  | 3 | 5.9 | 0.029 | 3 | 5.9 | 91.81 | 1.3839 | 67.1 | 91.3 | 0.1939 | 0.0395 | 14.85 | 13.83 | 14.89 | 1.06 | 1.797 | 2.221 | 9.376 | 3.0139 | 30.7 | 4.9 | 11 | 2021-08-30
2021-08-31 | Click Here |  | 6.29 | 5.04 | 4.99 | 5.18 | 5.24 | 7.39 | 7.27 | 1.83 | 1.96 | 2.19 | 1.58 | 42 | 37 | 19 | 0 | 0 | 0 | 0.398 | 0.048 | 1.47 | 0.133 | 0.396 | 0.315 | 14.4 | 38.9 | 39.1 | 38.1 | 50.9 | 28.8 | 77.8 | 78.2 | 76.2 | 101.8 |  |  | 3 | 6 | 0.039 | 20 | 18.8 | 72.77 | 1.0071 | 67.4 | 92.1 | 0.1713 | 0.0354 | 13.98 | 12.92 | 13.96 | 1.04 | 1.698 | 2.12 | 8.951 | 2.5571 | 30.71 | 4.9 | 11 | 2021-08-31
2021-09-01 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2021-09-01
2021-09-02 | Click Here |  | 6.39 | 5.12 | 5.21 | 5.17 | 5.2 | 7.04 | 7.54 | 1.89 | 1.99 | 2.2 | 1.53 | 39 | 32 | 19 | 0 | O | 0 | 0.377 | 0 | 1.48 | 0.126 | 0.291 | 0.337 | 14.4 | 35.3 | 30.2 | 30.8 | 48.7 | 28.8 | 70.6 | 60.4 | 61.6 | 97.4 |  |  | 3 | 5.9 | 0.044 | 19.7 | 18.6 | 0 |  | 67.4 | 90.9 | 0.1913 | 0.0414 | 15.54 | 14.37 | 15.5 | 1.13 | 1.798 | 2.236 | 9.206 |  | 30.35 | 4.9 | 10.7 | 2021-09-02
2021-09-03 | Click Here |  | 6.36 | 5.22 | 5.12 | 5.21 | 5.23 | 7.3 | 7.95 | 2.05 | 2.29 | 2.56 | 1.19 | 30 | 24 | 4 | 0 | 0 | 0 | 0.538 | 0.364 | 0.604 | 0.123 | 0.419 | 0.253 | 15 | 37.1 | 35.8 | 36.6 | 53.7 | 30 | 74.2 | 71.6 | 73.2 | 107.4 |  |  | 3.1 | 5.9 | 0.142 | 18.2 | 18.2 | 0 |  | 67.5 | 92.6 | 0.1707 | 0.0334 | 13.18 | 12.03 | 13.1 | 1.07 | 1.829 | 2.244 | 8.838 |  | 30.98 | 4.9 | 10.7 | 2021-09-03
2021-09-04 | Click Here |  | 6.26 | 5.25 | 5.05 | 5.29 | 5.31 | 7.23 | 7.37 | 1.87 | 2.03 | 2.44 | 3.35 | 31 | 25 | 8 | 0 | 0 | 0 | 0.647 | 0.288 | 1.14 | 0.099 | 0.253 | 0.218 | 14.3 | 36.9 | 35 | 35.2 | 47.3 | 28.6 | 73.8 | 70 | 70.4 | 94.6 |  |  | 3 | 6 | 0.101 | 18 | 18.1 | 0 |  | 67.1 | 92.2 | 0.1726 | 0.0345 | 13.36 | 12.06 | 13.1 | 1.04 | 1.627 | 2.25 | 7.398 |  | 30.51 | 4.9 | 10.7 | 2021-09-04
2021-09-05 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2021-09-05
2021-09-06 | Click Here |  | 6.29 | 5.21 | 5.13 | 5.21 | 5.22 | 6.93 | 7.26 | 1.89 | 2 | 2.16 | 2.15 | 36 | 29 | 24 | 2 | 1 | 0 | 0.935 | 0.359 | 1.44 | 0.125 | 0.262 | 0.219 | 16.7 | 37.9 | 34.8 | 35.2 | 49.4 | 33.4 | 75.8 | 75.6 | 70.4 | 98.8 |  |  | 3 | 5.9 | 0.208 | 16.8 | 17.4 | 100.88 | 1.5894 | 65 | 91.2 | 0.1869 | 0.0398 | 14.65 | 12.55 | 14.66 | 2.11 | 1.62 | 2.189 | 8.11 | 3.6494 | 30.99 | 4.9 | 10 | 2021-09-06
2021-09-07 | Click Here |  | 6.37 | 5.3 | 5.06 | 5.23 | 5.3 | 6.98 | 7.49 | 1.73 | 1.9 | 1.96 | 1.99 | 37 | 28 | 29 | 3 | 1 | 0 | 0.863 | 0.305 | 1.65 | 0.114 | 0.306 | 0.149 | 16.2 | 36.5 | 34.3 | 35 | 51.2 | 32.4 | 73 | 68.6 | 70 | 102.4 |  |  | 3.1 | 5.9 | 0.141 | 17.9 | 17.4 | 97.02 | 1.8193 | 60.3 | 89 | 0.219 | 0.0505 | 15.5 | 12.41 | 13.47 | 1.06 | 1.67 | 1.689 | 8.269 | 3.5493 | 31.06 | 4.9 | 10 | 2021-09-07
2021-09-08 | Click Here |  | 6.33 | 5.17 | 5.19 | 5.18 | 5 | 7.49 | 7.14 | 1.6 | 1.79 | 2.18 | 1.75 | 34 | 26 | 30 | 4 | 0 | 0 | 0.68 | 0.287 | 2.64 | 0.093 | 0.168 | 0.163 | 14.5 | 34.2 | 33.5 | 34.6 | 50.2 | 29 | 68.4 | 67 | 69.2 | 100.4 |  |  | 3.1 | 5.8 | 0.11 | 16.8 | 17.2 | 88.2 | 1.5735 | 61.4 | 90.2 | 0.2011 | 0.0486 | 13.99 | 11.8 | 12.85 | 1.05 | 1.693 | 1.406 | 8.333 | 3.3935 | 31.92 | 4.3 | 10 | 2021-09-08
2021-09-09 | Click Here |  | 6.34 | 5.21 | 5.2 | 5.1 | 5.26 | 7.49 | 7.39 | 1.69 | 1.76 | 2.22 | 0.77 | 31 | 24 | 3 | 0 | 0 | 0 | 0.642 | 0.326 | 0.416 | 0.083 | 0.259 | 0.212 | 15 | 37.4 | 36 | 38.2 | 48.6 | 30 | 74.8 | 72 | 76.4 | 97.2 |  |  | 3 | 6 | 0.127 | 18 | 17.5 | 0 |  | 63 | 91.4 | 0.2001 | 0.0386 | 12.77 | 12.63 | 12.63 | 0 | 1.688 | 1.752 | 8.22 |  | 30.98 | 4.3 | 10 | 2021-09-09
2021-09-10 | Click Here |  | 6.62 | 5.2 | 5.14 | 5.15 | 5.26 | 7.82 | 7.31 | 1.68 | 1.92 | 1.99 | 1.33 | 36 | 29 | 9 | 0 | 0 | 0 | 0.413 | 0.527 | 0.505 | 0.087 | 0.218 | 0.189 | 15.4 | 40.6 | 36.6 | 36.8 | 50.9 | 30.8 | 81.2 | 73.2 | 73.6 | 101.8 |  |  | 3.1 | 6 | 0.096 | 18.7 | 17.9 | 90.4 | 1.8095 | 63.7 | 91.3 | 0.1953 | 0.0394 | 12.64 | 11.53 | 12.59 | 1.06 | 1.709 | 1.979 | 8.106 | 3.5595 | 31.04 | 4.3 | 10 | 2021-09-10
2021-09-11 | Click Here |  | 6.33 | 4.99 | 5.15 | 4.98 | 5.08 | 6.9 | 7.14 | 1.73 | 1.9 | 2.11 | 2.14 | 40 | 32 | 7 | 0 | 0 | 0 | 0.693 | 0.621 | 0.497 | 0.083 | 0.269 | 0.264 | 15.8 | 39.1 | 37.4 | 37.3 | 50.1 | 31.6 | 78.2 | 74.8 | 74.6 | 100.2 |  |  | 3 | 6 | 0.063 | 19.1 | 18.1 | 88.2 | 1.4099 | 63.5 | 91.5 | 0.1955 | 0.0392 | 12.68 | 11.54 | 12.6 | 1.06 | 0 | 0 | 0 | 3.4699 | 30.35 | 4.1 | 10 | 2021-09-11
2021-09-12 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2021-09-12
2021-09-13 | Click Here |  | 6.24 | 5.09 | 5.13 | 5.08 | 5.13 | 7 | 7.37 | 1.58 | 1.81 | 2.18 | 1.99 | 42 | 36 | 8 | 0 | 0 | 0 | 0.827 | 0.68 | 0.687 | 0.085 | 0.462 | 0.41 | 15.4 | 39.9 | 37 | 36.3 | 51.3 | 30.8 | 79.8 | 74 | 72.6 | 102.6 |  |  | 3.1 | 5.9 | 0.063 | 18.5 | 17.9 | 92.61 | 1.2949 | 58.5 | 89.3 | 0.2328 | 0.0491 | 13.63 | 12.57 | 13.62 | 1.05 | 1.69 | 2.376 | 8.316 | 3.3449 | 30.98 | 4.2 | 10.2 | 2021-09-13
2021-09-14 | Click Here |  | 6.26 | 5.12 | 5.12 | 5.16 | 5.16 | 7.46 | 7.11 | 1.32 | 1.76 | 1.98 | 2.02 | 40 | 33 | 14 | 0 | 0 | 0 | 0.731 | 0.632 | 0.707 | 0.113 | 0.316 | 0.21 | 15.2 | 39.7 | 36.6 | 37.1 | 50.9 | 30.4 | 79.4 | 73.2 | 74.2 | 101.8 |  |  | 3.1 | 5.9 | 0.051 | 17.9 | 17.8 | 94.81 | 1.3197 | 60.8 | 90.7 | 0.2158 | 0.042 | 13.94 | 12.85 | 13.9 | 1.05 | 1.585 | 2.911 | 8.15 | 3.3497 | 30.5 | 4.2 | 10.5 | 2021-09-14
2021-09-15 | Click Here |  | 6.14 | 5.09 | 5.15 | 5.28 | 5.52 | 7.63 | 7.45 | 1.64 | 1.74 | 1.98 | 2.01 | 38 | 30 | 9 | 0 | 0 | 0 | 0.596 | 0.645 | 0.695 | 0.107 | 0.298 | 0.257 | 14.9 | 39.3 | 36.1 | 36.6 | 50 | 29.8 | 78.6 | 72.2 | 73.2 | 100 |  |  | 3 | 6.1 | 0.048 | 16.6 | 17.7 | 97.88 | 1.3641 | 58.9 | 89.8 | 0.2294 | 0.0465 | 14.25 | 13.17 | 14.21 | 1.04 | 1.611 | 2.155 | 8.187 | 3.3741 | 30.23 | 4.2 | 10.3 | 2021-09-15
2021-09-16 | Click Here |  | 6.11 | 5.12 | 5.1 | 5.3 | 5.32 | 7.89 | 7.63 | 1.59 | 1.78 | 1.97 | 1.98 | 49 | 41 | 14 | 0 | 0 | 0 | 0.706 | 0.59 | 0.676 | 0.093 | 0.282 | 0.229 | 15.2 | 39.5 | 37.2 | 37.1 | 50.4 | 30.4 | 79 | 74.4 | 74.2 | 100.8 |  |  | 2.9 | 17.7 | 0.041 | 17 | 17.7 | 88.2 | 1.1306 | 59.4 | 89.2 | 0.2259 | 0.0493 | 13.85 | 12.75 | 13.83 | 1.08 | 1.53 | 2.517 | 8.215 | 3.1406 | 30.2 | 4.2 | 10 | 2021-09-16
2021-09-17 | Click Here |  | 6.21 | 5.2 | 5.1 | 5.06 | 5.12 | 6.89 | 7.47 | 1.77 | 1.92 | 2.09 | 2.12 | 47 | 40 | 12 | 1 | 0 | 0 | 0.691 | 0.563 | 0.634 | 0.089 | 0.301 | 0.287 | 14.9 | 36.9 | 37 | 36.3 | 49 | 29.8 | 73.8 | 74 | 72.6 | 98 |  |  | 3 | 6 | 0.048 | 17.1 | 17.3 | 0 |  | 59.2 | 89.6 | 0.226 | 0.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 31.65 | 4.2 | 10 | 2021-09-17
2021-09-18 | Click Here |  | 6.17 | 5.16 | 5.21 | 5.1 | 5.19 | 7.41 | 7.5 | 1.69 | 1.78 | 1.99 | 2.02 | 47 | 40 | 13 | 0 | 0 | 0 | 0.623 | 0.591 | 0.684 | 0.091 | 0.308 | 0.277 | 15.1 | 37.1 | 35.8 | 35.3 | 49.4 | 30.2 | 74.2 | 71.6 | 70.6 | 98.8 |  |  | 3 | 6.1 | 0.044 | 17 | 17.2 | 79.68 | 1.2657 | 59.9 | 90.4 | 0.2231 | 0.0433 | 12.04 | 10.91 | 11.96 | 1.05 | 0 | 0 | 0 | 3.3157 | 30.94 | 4.2 | 10 | 2021-09-18
2021-09-19 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 87.83 | 1.3421 | 0 | 0 | 0 | 0 | 12.86 | 11.79 | 12.82 | 1.06 | 1.592 | 1.818 | 6.346 | 3.3821 | 0 | 4.2 | 10 | 2021-09-19
2021-09-20 | Click Here |  | 6.19 | 5.05 | 5.17 | 5.15 | 5.13 | 6.47 | 7.29 | 1.69 | 1.76 | 1.98 | 2 | 51 | 42 | 19 | 0 | 0 | 0 | 0.512 | 0.556 | 0.799 | 0.094 | 0.326 | 0.258 | 14.8 | 37.6 | 37.8 | 36.5 | 39.4 | 29.6 | 75.2 | 75.6 | 73 | 78.8 |  |  | 3 | 6 | 0.056 | 16.6 | 17.1 | 95.83 | 1.3205 | 60.7 | 89.7 | 0.2165 | 0.0472 | 13.98 | 12.87 | 13.94 | 1.07 | 1.708 | 2.264 | 6.558 | 3.3805 | 30.58 | 4.2 | 10 | 2021-09-20
2021-09-21 | Click Here |  | 6.54 | 5.17 | 5.27 | 5.23 | 5.42 | 7.42 | 7.27 | 1.68 | 1.71 | 2.12 | 2.13 | 40 | 34 | 17 | 0 | 1 | 0 | 0.496 | 0.256 | 0.933 | 0.148 | 0.31 | 0.26 | 14.6 | 36.4 | 34.4 | 35.5 | 49.1 | 29.2 | 72.8 | 68.8 | 71 | 98.2 | 5.49 | 4.37 | 2.9 | 6 | 0.117 | 15.7 | 16.9 | 92.61 | 1.1545 | 61.2 | 89.5 | 0.2127 | 0.0481 | 13.94 | 12.84 | 13.88 | 1.04 | 1.745 | 2.559 | 6.652 | 3.2745 | 29.95 | 4.2 | 10.3 | 2021-09-21
2021-09-22 | Click Here |  | 6.23 | 5.08 | 5.16 | 5.05 | 5.13 | 6.94 | 7.46 | 1.66 | 1.88 | 2.06 | 2.08 | 41 | 33 | 14 | 1 | 0 | 0 | 0.508 | 0.493 | 0.811 | 0.106 | 0.271 | 0.236 | 14.2 | 37 | 34.3 | 35.3 | 49 | 28.4 | 74 | 68.6 | 70.6 | 98 | 5.2 | 4.34 | 3 | 5.9 | 0.055 | 16 | 16.9 | 90.07 | 1.2311 | 61.5 | 89.9 | 0.2123 | 0.0478 | 13.42 | 12.35 | 13.39 | 1.04 | 1.727 | 2.567 | 6.601 | 3.3111 | 31.45 | 4.2 | 10.3 | 2021-09-22
2021-09-23 | Click Here |  | 6.28 | 4.99 | 5.02 | 5.03 | 5.1 | 6.91 | 7.15 | 1.73 | 1.87 | 1.95 | 2.06 | 40 | 34 | 17 | 2 | 0 | 0 | 0.604 | 0.486 | 0.936 | 0.109 | 0.294 | 0.25 | 14.6 | 37.8 | 34.8 | 35.8 | 48.9 | 29.2 | 75.6 | 69.6 | 71.6 | 97.8 | 7.3 | 5.21 | 3 | 5.8 | 0.136 | 16.4 | 16.8 | 97.02 | 1.2847 | 56.1 | 87.7 | 0.2509 | 0.0567 | 14.28 | 13.13 | 14.2 | 1.07 | 1.754 | 2.589 | 6.888 | 3.3547 | 30.83 | 4.2 | 10.3 | 2021-09-23
2021-09-24 | Click Here |  | 6.19 | 5.09 | 5.03 | 5.06 | 5.07 | 7.29 | 6.99 | 1.63 | 1.82 | 1.9 | 1.98 | 39 | 32 | 1 | 0 | 0 | 0 | 0.544 | 0.47 | 0.995 | 0.089 | 0.28 | 0.216 | 14.8 | 37.5 | 35.2 | 34.6 | 49.4 | 29.6 | 75 | 70.4 | 69.2 | 98.8 | 3.28 | 2.9 | 3.1 | 5.9 | 0.13 | 17 | 16.9 | 81.58 | 0.59862 | 59.8 | 89.4 | 0.2232 | 0.0485 | 14.14 | 14.09 | 14.09 | 0 | 1.737 | 2.257 | 9.163 | 2.6286 | 30.98 | 4.1 | 10.4 | 2021-09-24
2021-09-25 | Click Here |  | 6.16 | 5.05 | 5.01 | 5.08 | 5.12 | 7.31 | 7.24 | 1.74 | 1.9 | 1.97 | 2.01 | 38 | 31 | 3 | 0 | 0 | 0 | 0.561 | 0.455 | 0.982 | 0.085 | 0.276 | 0.235 | 14.6 | 36.4 | 35.1 | 34.4 | 48.8 | 29.2 | 72.8 | 70.2 | 68.8 | 97.6 | 3.27 | 2.81 | 3 | 6 | 0.113 | 16.9 | 16.8 | 90.4 | 1.9118 | 59.2 | 89.5 | 0.2241 | 0.0481 | 11.74 | 10.6 | 11.62 | 1.02 | 0 | 0 | 0 | 3.8718 | 30.51 | 4.1 | 10.4 | 2021-09-25
2021-09-26 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2021-09-26
2021-09-27 | Click Here |  | 6.21 | 5.09 | 4.97 | 5.11 | 5.15 | 6.93 | 7.32 | 1.65 | 1.82 | 1.9 | 1.92 | 39 | 33 | 10 | 0 | 0 | 0 | 0.481 | 0.443 | 0.963 | 0.092 | 0.257 | 0.234 | 14.9 | 37.8 | 34.8 | 35.2 | 48 | 29.8 | 75.6 | 69.6 | 70.4 | 96 | 3.35 | 3.02 | 3 | 5.9 | 0.081 | 16.2 | 16.5 | 86 | 1.1999 | 59.6 | 89.8 | 0.2239 | 0.0438 | 13.28 | 12.24 | 13.26 | 1.02 | 1.716 | 2.102 | 8.578 | 3.1899 | 30.58 | 4.3 | 10.2 | 2021-09-27
2021-09-28 | Click Here |  | 6.39 | 5.06 | 5.08 | 5.08 | 5.13 | 6.89 | 7.19 | 1.73 | 1.92 | 2.07 | 2.12 | 37 | 32 | 22 | 1 | 0 | 0 | 0.539 | 0.457 | 1.22 | 0.127 | 0.293 | 0.234 | 14.6 | 38.9 | 34.7 | 35.3 | 49.2 | 29.2 | 77.8 | 69.4 | 70.6 | 98.4 | 3.28 | 7.61 | 3 | 5.9 | 0.121 | 16.1 | 16.6 | 88.64 | 1.2367 | 61.9 | 86.1 | 0.2077 | 0.0646 | 13.29 | 12.17 | 13.21 | 1.04 | 1.644 | 1.916 | 8.459 | 3.3067 | 30.3 | 4.3 | 10.2 | 2021-09-28
2021-09-29 | Click Here |  | 6.28 | 5.05 | 5.01 | 5.09 | 5.17 | 7.38 | 7.44 | 1.77 | 1.98 | 2 | 2.03 | 39 | 33 | 20 | 0 | 0 | 0 | 0.494 | 0.446 | 1.17 | 0.112 | 0.216 | 0.209 | 14.4 | 37.8 | 34.2 | 35 | 49.5 | 28.8 | 77.6 | 68.4 | 70 | 99 | 3.34 | 7.45 | 3 | 6.1 | 0.114 | 16 | 16.4 | 101.43 | 1.5634 | 62.1 | 88.6 | 0.2019 | 0.0501 | 13.66 | 12.57 | 13.62 | 1.05 | 1.905 | 1.626 | 9.276 | 3.6634 | 29.85 | 4.3 | 10.2 | 2021-09-29
2021-09-30 | Click Here |  | 6.04 | 5.02 | 4.97 | 5.04 | 5.15 | 7.22 | 7.24 | 1.64 | 1.78 | 1.86 | 1.9 | 38 | 31 | 37 | 15 | 6 | 0 | 0.53 | 0.435 | 2.29 | 0.387 | 0.486 | 0.309 | 14.2 | 37 | 34.2 | 34.8 | 48.8 | 28.4 | 74 | 68.4 | 69.6 | 97.6 |  |  | 3.1 | 5.9 | 0.312 | 15.4 | 16.2 | 112.45 | 0.93412 | 62.6 | 91.8 | 0.2929 | 0.0372 | 18.48 | 17.64 | 18.66 | 1.02 | 1.654 | 1.862 | 14.78 | 2.8941 | 30.98 | 4.3 | 10.2 | 2021-09-30
2021-10-01 | Click Here |  | 6.19 | 5.1 | 5.16 | 5.13 | 5.19 | 7.21 | 7.12 | 1.69 | 1.87 | 1.98 | 2.01 | 39 | 34 | 21 | 0 | 0 | 0 | 0.486 | 0.429 | 1.47 | 0.146 | 0.371 | 0.277 | 14.1 | 37.1 | 34.6 | 34.1 | 46.5 | 28.2 | 74.2 | 69.2 | 68.2 | 93 | 3.43 | 6.08 | 3 | 5.9 | 0.207 | 15.4 | 16.3 | 90.96 | 1.2074 | 62.1 | 92.1 | 0.2094 | 0.0349 | 13.66 | 12.6 | 13.67 | 1.07 | 1.66 | 1.912 | 8.284 | 3.2774 | 30.21 | 4.3 | 10.2 | 2021-10-01
2021-10-02 | Click Here |  | 6.29 | 5 | 4.77 | 5.19 | 5.23 | 7.01 | 7.11 | 1.7 | 1.96 | 2.05 | 2.08 | 37 | 30 | 24 | 1 | 0 | 0 | 0.514 | 0.422 | 1.4 | 0.141 | 0.326 | 0.297 | 14.4 | 37.2 | 34.5 | 33.9 | 47.2 | 28.8 | 74.4 | 69 | 67.9 | 94.4 | 4.05 | 5.32 | 2.9 | 6 | 0.101 | 15.4 | 16.4 | 86.48 | 1.2871 | 61.8 | 92 | 0.2146 | 0.0354 | 12.79 | 11.73 | 12.78 | 1.05 | 1.548 | 1.87 | 7.144 | 3.3471 | 30.17 | 4.3 | 10.2 | 2021-10-02
2021-10-03 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2021-10-03
2021-10-04 | Click Here |  | 6.11 | 5.09 | 4.91 | 5.13 | 5.2 | 7.04 | 7.06 | 1.63 | 1.8 | 1.9 | 1.92 | 42 | 35 | 38 | 3 | 0 | 0 | 0.512 | 0.435 | 1.45 | 0.294 | 0.382 | 0.3 | 14.6 | 37.6 | 35.2 | 35.5 | 48.9 | 29.2 | 75.2 | 70.4 | 71 | 97.8 |  |  | 3.1 | 6 | 0.3 | 14.9 | 15.8 | 79.38 | 1.0158 | 58.5 | 89.1 | 0.2327 | 0.0497 | 13.14 | 12.07 | 13.05 | 0.98 | 1.64 | 1.869 | 7.693 | 2.9858 | 30.28 | 4.3 | 10.2 | 2021-10-04
2021-10-05 | Click Here |  | 6.02 | 5.14 | 5.4 | 5.06 | 5.15 | 7.04 | 7.09 | 1.67 | 1.82 | 1.95 | 1.92 | 39 | 32 | 24 | 2 | 0 | 0 | 0.51 | 0.436 | 1.33 | 0.271 | 0.415 | 0.364 | 14.7 | 37.5 | 36.4 | 35.7 | 48.7 | 29.4 | 75 | 72.8 | 71.4 | 97.4 |  |  | 3 | 5.8 | 0.286 | 14.7 | 15.6 | 92.61 | 1.4605 | 58.7 | 90.2 | 0.2331 | 0.0479 | 13.09 | 12.15 | 13.12 | 0.97 | 1.614 | 1.864 | 8.053 | 3.4605 | 30.98 | 4.3 | 10.2 | 2021-10-05
2021-10-06 | Click Here |  | 6.55 | 5.19 | 5.05 | 5.17 | 5.28 | 7.41 | 7.16 | 1.65 | 1.91 | 1.94 | 1.98 | 41 | 35 | 20 | 1 | 0 | 0 | 0.491 | 0.427 | 1.39 | 0.16 | 0.323 | 0.312 | 13.8 | 37.1 | 33.6 | 32.9 | 48.2 | 27.6 | 74.2 | 67.2 | 65.8 | 96.4 |  |  | 3 | 6 | 0.167 | 13.6 | 15.7 | 89.96 | 1.229 | 62.1 | 88.8 | 0.2067 | 0.0514 | 13.49 | 12.38 | 13.42 | 1.04 | 1.639 | 1.87 | 8.268 | 3.299 | 30.66 | 4.4 | 10.2 | 2021-10-06
2021-10-07 | Click Here |  | 6.39 | 5.15 | 5.08 | 5.17 | 5.26 | 7.39 | 7.31 | 1.72 | 1.84 | 2.09 | 2.11 | 36 | 28 | 14 | 0 | 0 | 0 | 0.496 | 0.399 | 1.14 | 0.117 | 0.344 | 0.331 | 14 | 37.2 | 33.4 | 33.1 | 47.1 | 28 | 74.4 | 66.8 | 66.2 | 94.2 |  |  | 3 | 5.9 | 0.147 | 14.1 | 16 | 90.41 | 1.2355 | 62.1 | 90.5 | 0.2067 | 0.0432 | 13.46 | 12.38 | 13.44 | 1.06 | 1.634 | 1.866 | 9.729 | 3.3155 | 31.06 | 4.4 | 10.2 | 2021-10-07
2021-10-08 | Click Here |  | 6.48 | 5.1 | 5.21 | 5.11 | 5.16 | 6.94 | 7.24 | 1.72 | 1.93 | 2.01 | 2.04 | 38 | 30 | 16 | 1 | 0 | 0 | 0.471 | 0.356 | 1.28 | 0.12 | 0.366 | 0.314 | 13.8 | 35.1 | 32.6 | 33.5 | 47.2 | 27.6 | 70.2 | 65.2 | 67 | 94.4 |  |  | 3.1 | 5.8 | 0.127 | 13.4 | 14.8 | 86.21 | 1.2229 | 54.2 | 90.2 | 0.2654 | 0.0446 | 12.96 | 11.85 | 12.89 | 1.04 | 1.663 | 1.862 | 7.688 | 3.3029 | 31.77 | 4.4 | 10.2 | 2021-10-08
2021-10-09 | Click Here |  | 6.44 | 5.2 | 5.18 | 5.19 | 5.23 | 6.73 | 7.37 | 1.72 | 1.94 | 2.15 | 2.13 | 37 | 29 | 14 | 0 | 0 | 0 | ,493 | 0.426 | 1.19 | 0.11 | 0.336 | 0.321 | 13.3 | 34.9 | 31.3 | 31.8 | 47.2 | 26.6 | 69.8 | 62.6 | 63.6 | 94.4 |  |  | 3 | 5.9 | 0.136 | 12.3 | 14.4 | 81.89 | 1.3174 | 54.4 | 90 | 0.2562 | 0.0448 | 12.2 | 11.85 | 12.89 | 1.04 | 0 | 0 | 0 | 3.1374 | 31.8 | 4.4 | 10.2 | 2021-10-09
2021-10-10 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 84.09 | 1.287 | 0 | 0 | 0 | 0 | 12.51 | 11.14 | 12.09 | 0.95 | 1.498 | 1.87 | 7.522 | 3.427 | 0 | 4.3 | 10.2 | 2021-10-10
2021-10-11 | Click Here |  | 6.37 | 5.12 | 5.07 | 5.16 | 5.19 | 7.29 | 7.58 | 1.76 | 2.01 | 2.09 | 2.05 | 36 | 30 | 15 | 0 | 0 | 0 | 0.412 | 0.396 | 1.09 | 0.124 | 0.391 | 0.317 | 13.7 | 35.2 | 30.9 | 31.5 | 47.7 | 37.4 | 70.4 | 61.8 | 63 | 95.4 |  |  | 3 | 6 | 0.121 | 12.2 | 14.4 | 92.06 | 1.1574 | 55.6 | 90.4 | 0.2569 | 0.0419 | 14.01 | 12.95 | 14.01 | 1.06 | 1.537 | 1.873 | 8.556 | 3.2274 | 31.11 | 4.3 | 10.2 | 2021-10-11
2021-10-12 | Click Here |  | 6.52 | 5.1 | 5.08 | 5.24 | 5.26 | 7.51 | 7.51 | 1.66 | 1.82 | 1.98 | 2.02 | 39 | 33 | 12 | 0 | 0 | 0 | 0.673 | 0.385 | 0.985 | 0.22 | 0.717 | 0.643 | 13.3 | 35.9 | 31.3 | 32.1 | 46.1 | 26.6 | 71.8 | 62.6 | 64.2 | 92.2 |  |  | 2.9 | 6.1 | 0.163 | 12.3 | 14.5 | 86 | 1.2056 | 62.2 | 90.3 | 0.2062 | 0.0442 | 13.08 | 12.03 | 13.08 | 0 | 1.59 | 1.88 | 8.23 | 3.2456 | 30.23 | 4.3 | 10.4 | 2021-10-12
2021-10-13 | Click Here |  | 6.43 | 5.1 | 5.06 | 5.2 | 5.25 | 7.59 | 7.65 | 1.69 | 1.86 | 1.99 | 1.95 | 37 | 29 | 15 | 1 | 0 | 0 | 0.593 | 0.374 | 1.19 | 0.196 | 0.412 | 0.395 | 13.5 | 36.2 | 31.6 | 32.4 | 47.3 | 27 | 72.4 | 63.2 | 64.8 | 94.6 |  |  | 3 | 6.1 | 0.196 | 12.2 | 14.4 | 82.71 | 1.3013 | 62.5 | 90 | 0.2026 | 0.0476 | 12.4 | 11.34 | 12.38 | 1.04 | 1.635 | 1.863 | 8.124 | 3.3113 | 30 | 4.3 | 10.4 | 2021-10-13
2021-10-14 | Click Here |  | 7.12 | 5.29 | 5.03 | 5.27 | 5.3 | 7.18 | 7.66 | 1.74 | 1.88 | 1.94 | 1.96 | 39 | 31 | 18 | 2 | 0 | 0 | 0.498 | 0.376 | 1.3 | 0.199 | 0.682 | 0.601 | 13.1 | 37.4 | 31.1 | 31 | 45.2 | 26.2 | 74.8 | 62.2 | 62 | 90.4 |  |  | 3.1 | 6 | 0.181 | 12.7 | 13.6 | 88.2 | 1.3139 | 62.1 | 90.2 | 0.2029 | 0.0474 | 13.3 | 12.12 | 13.15 | 1.03 | 1.644 | 1.847 | 8.094 | 3.3039 | 31.95 | 4.3 | 10.4 | 2021-10-14
2021-10-15 | Click Here |  | 6.34 | 5.2 | 5.06 | 5.21 | 5.29 | 7.29 | 7.57 | 1.68 | 1.84 | 1.96 | 1.99 | 36 | 30 | 16 | 1 | 0 | 0 | 0.512 | 0.486 | 1.16 | 0.182 | 0.445 | 0.375 | 13.4 | 37.1 | 32.2 | 34.3 | 44.8 | 26.8 | 74.2 | 64.4 | 68.6 | 89.6 |  |  | 3 | 5.9 | 0.146 | 12.6 | 13.6 | 70.56 | 0.61718 | 62.2 | 89.8 | 0.2025 | 0.0481 | 12.36 | 12.24 | 12.24 | 0 | 1.637 | 1.844 | 7.796 | 2.6172 | 30.98 | 4.1 | 10.4 | 2021-10-15
2021-10-16 | Click Here |  | 6.16 | 5.22 | 5.2 | 5.19 | 5.26 | 7.31 | 7.32 | 1.71 | 1.9 | 2.02 | 1.99 | 35 | 28 | 17 | 2 | 0 | 0 | 0.456 | 0.423 | 1.22 | 0.176 | 0.481 | 0.44 | 13.2 | 36.7 | 33.1 | 35 | 44.3 | 26.4 | 73.4 | 66.2 | 70 | 88.6 |  |  | 3.1 | 6 | 0.129 | 12.5 | 13.4 | 70.56 | 0.95432 | 62 | 89.5 | 0.0229 | 0.0487 | 12.04 | 10.88 | 11.91 | 1.03 | 0 | 0 | 0 | 2.9443 | 30.51 | 4.1 | 10.4 | 2021-10-16
2021-10-17 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2021-10-17
2021-10-18 | Click Here |  | 6.45 | 5.13 | 5 | 5.18 | 5.27 | 7.13 | 7.6 | 1.51 | 1.75 | 1.91 | 1.95 | 37 | 29 | 24 | 2 | 1 | 0 | 0.48 | 0.33 | 1.19 | 0.16 | 0.51 | 0.42 | 12.6 | 34.1 | 29.2 | 29.9 | 44.7 | 25.2 | 68.2 | 58.4 | 59.8 | 89.4 |  |  | 3 | 6 | 0.186 | 11 | 13.1 | 94.61 | 1.3928 | 60.7 | 90.5 | 0.2165 | 0.0434 | 13.75 | 12.66 | 13.68 | 1.02 | 1.693 | 1.917 | 7.792 | 3.3928 | 31.23 | 4.1 | 10.4 | 2021-10-18
2021-10-19 | Click Here |  | 6.37 | 5.34 | 5.09 | 5.28 | 5.35 | 7.5 | 7.2 | 1.79 | 1.95 | 2.01 | 2.05 | 39 | 32 | 30 | 3 | 1 | 0 | 0.502 | 0.374 | 1.48 | 0.173 | 0.383 | 0.206 | 12.7 | 30.4 | 28.1 | 28.5 | 45 | 25.4 | 60.8 | 56.2 | 57 | 90 |  |  | 3 | 5.9 | 0.147 | 11.7 | 12.8 | 79.38 | 0.92952 | 60.4 | 90.2 | 0.2168 | 0.0437 | 15.44 | 12.26 | 13.84 | 1.58 | 1.706 | 1.842 | 8.048 | 2.9395 | 27.3 | 4 | 10.4 | 2021-10-19
2021-10-20 | Click Here |  | 6.42 | 5.31 | 5.13 | 5.28 | 5.32 | 7.54 | 7.37 | 1.79 | 2.04 | 2.03 | 2.02 | 36 | 29 | 28 | 3 | 0 | 0 | 0.486 | 0.35 | 1.44 | 0.166 | 0.331 | 0.175 | 12.8 | 30.5 | 28.2 | 30.1 | 45.1 | 25.6 | 61 | 56.4 | 60.2 | 90.2 |  |  | 3.1 | 6 | 0.134 | 11.7 | 12.7 | 85.99 | 0.99591 | 60.6 | 89.9 | 0.2159 | 0.0445 | 14.8 | 12.61 | 13.1 | 0.49 | 1.736 | 1.836 | 7.828 | 3.0959 | 30.28 | 4 | 10.4 | 2021-10-20
2021-10-21 | Click Here |  | 6.33 | 5.16 | 5.28 | 5.21 | 5.27 | 7.4 | 7.29 | 1.79 | 1.98 | 2.12 | 2.11 | 34 | 27 | 16 | 1 | 0 | 0 | 0.471 | 0.362 | 1.03 | 0.092 | 0.344 | 0.229 | 13 | 32.2 | 29.5 | 31.3 | 44.8 | 26 | 64.4 | 59 | 62.6 | 89.6 |  |  | 3 | 5.9 | 0.121 | 11.6 | 12.6 | 81.58 | 1.1156 | 61.1 | 90.3 | 0.2079 | 0.0435 | 12.82 | 11.59 | 12.65 | 1.06 | 1.695 | 1.841 | 7.803 | 3.1956 | 29.81 | 4 | 10.2 | 2021-10-21
2021-10-22 | Click Here |  | 6.29 | 5.36 | 5.49 | 5.19 | 5.24 | 7.19 | 7.33 | 1.73 | 1.9 | 2.01 | 2.04 | 37 | 28 | 14 | 0 | 0 | 0 | 0.409 | 0.312 | 0.891 | 0.088 | 0.321 | 0.288 | 13.2 | 32.4 | 28.6 | 29 | 43.3 | 26.4 | 64.8 | 57.2 | 58 | 86.6 |  |  | 3.1 | 6 | 0.106 | 12.3 | 13.5 | 90.96 | 1.2447 | 61.9 | 90.9 | 0.2042 | 0.0414 | 13.39 | 12.31 | 13.36 | 1.05 | 1.719 | 1.847 | 7.717 | 3.3547 | 29.96 | 4 | 10.2 | 2021-10-22
2021-10-23 | Click Here |  | 6.29 | 5.31 | 5.39 | 5.11 | 5.17 | 7.36 | 7.58 | 1.8 | 2 | 2.14 | 2.13 | 35 | 27 | 9 | 0 | 0 | 0 | 0.314 | 0.301 | 0.791 | 0.086 | 0.295 | 0.234 | 13.4 | 32.8 | 29.1 | 29.7 | 44.1 | 26.8 | 65.6 | 58.2 | 59.4 | 88.2 |  |  | 3 | 6 | 0.098 | 12.2 | 13.5 | 86 | 1.2304 | 62.4 | 92.4 | 0.1987 | 0.0341 | 12.9 | 11.83 | 12.87 | 1.04 | 0 | 0 | 0 | 3.3004 | 30.26 | 4 | 10.2 | 2021-10-23
2021-10-24 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2021-10-24
2021-10-25 | Click Here |  | 6.28 | 5.15 | 5.28 | 5.21 | 5.24 | 7.27 | 7.25 | 1.69 | 1.89 | 2.15 | 1.98 | 50 | 42 | 10 | 0 | 0 | 0 | 0.68 | 0.477 | 0.768 | 0.097 | 0.328 | 0.26 | 14.6 | 37.9 | 30.3 | 30.4 | 43.6 | 29.2 | 75.8 | 60.6 | 60.8 | 87.2 |  |  | 3.1 | 5.8 | 0.298 | 14 | 13.2 | 88.2 | 1.3506 | 52.5 | 88.4 | 0.2796 | 0.0536 | 12.92 | 11.81 | 12.86 | 1.05 | 1.689 | 1.84 | 7.877 | 3.3906 | 30.28 | 4 | 10.2 | 2021-10-25
2021-10-26 | Click Here |  | 6.24 | 5.21 | 5.17 | 5.23 | 5.27 | 7.26 | 7.33 | 1.7 | 1.91 | 1.99 | 2.02 | 48 | 40 | 10 | 0 | 0 | 0 | 0.51 | 0.318 | 0.969 | 0.117 | 0.342 | 0.27 | 14.5 | 37.8 | 31.1 | 30.6 | 44.2 | 29 | 75.6 | 62.2 | 61.2 | 88.4 |  |  | 3 | 5.9 | 0.306 | 14 | 13.1 | 81.58 | 1.002 | 57.8 | 96.5 | 0.2377 | 0.0153 | 13.16 | 11.94 | 12.99 | 1.05 | 1.742 | 1.837 | 7.815 | 3.102 | 30.75 | 4 | 10.2 | 2021-10-26
2021-10-27 | Click Here |  | 6.19 | 5.17 | 5.14 | 5.2 | 5.25 | 7.34 | 7.49 | 1.72 | 1.97 | 2.01 | 1.99 | 45 | 39 | 11 | 0 | 0 | 0 | 0.498 | 0.367 | 0.829 | 0.104 | 0.213 | 0.144 | 14.7 | 38.1 | 29.7 | 29.2 | 44.7 | 29.4 | 76.2 | 59.4 | 58.4 | 89.4 |  |  | 3 | 6.1 | 0.244 | 13.8 | 1`2.9 | 86.79 | 1.3223 | 58.1 | 96.7 | 0.2304 | 0.014 | 12.91 | 11.86 | 12.89 | 1.03 | 1.703 | 1.854 | 7.736 | 3.3223 | 30.37 | 4 | 10.2 | 2021-10-27
2021-10-28 | Click Here |  | 6.26 | 5.21 | 5.14 | 5.38 | 5.42 | 7.75 | 7.54 | 1.66 | 1.78 | 1.97 | 2 | 49 | 43 | 16 | 0 | 0 | 0 | 0.462 | 0.329 | 0.917 | 0.107 | 0.299 | 0.226 | 12.8 | 35.8 | 28.5 | 28.8 | 44.5 | 25.6 | 71.6 | 57 | 57.6 | 89 |  |  | 2.8 | 6 | 0.164 | 11.2 | 13 | 88.2 | 1.2703 | 55.7 | 90.3 | 0.2579 | 0.0439 | 13.32 | 12.17 | 13.22 | 1.05 | 1.673 | 1.886 | 8.208 | 3.2903 | 30.18 | 4 | 0 | 2021-10-28
2021-10-29 | Click Here |  | 6.45 | 5.26 | 5.23 | 5.24 | 5.29 | 7.51 | 7.86 | 1.64 | 1.79 | 1.96 | 1.98 | 48 | 41 | 14 | 1 | 0 | 0 | 0.455 | 0.347 | 0.893 | 0.106 | 0.203 | 0.164 | 12.4 | 45.4 | 28.3 | 28.9 | 45.5 | 24.8 | 90.8 | 56.6 | 57.8 | 91 |  |  | 2.9 | 5.9 | 0.171 | 11 | 12 | 68.36 | 0.67646 | 55.5 | 90.6 | 0.2577 | 0.0436 | 12.54 | 12.14 | 12.14 | 0 | 1.596 | 1.902 | 7.895 | 2.5565 | 30.27 | 4 | 10.2 | 2021-10-29
2021-10-30 | Click Here |  | 6.39 | 5.16 | 5.21 | 5.2 | 5.27 | 7.14 | 6.99 | 1.66 | 1.83 | 1.97 | 1.98 | 47 | 40 | 15 | 1 | 0 | 0 | 0.461 | 0.356 | 0.903 | 0.114 | 0.714 | 0.551 | 14.3 | 35.5 | 28.2 | 29 | 44.2 | 28.6 | 71 | 56.4 | 58 | 88.4 |  |  | 3 | 6.1 | 0.155 | 9.8 | 11.9 | 82.64 | 1.3801 | 55.9 | 90.2 | 0.2574 | 0.0439 | 12.04 | 10.97 | 11.99 | 1.02 | 1.486 | 1.946 | 7.449 | 3.4201 | 30.01 | 4 | 10.2 | 2021-10-30
2021-10-31 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 89.3 | 1.2996 | 0 | 0 | 0 | 0 | 13.34 | 12.14 | 13.23 | 1.09 | 0 | 0 | 0 | 3.3396 | 0 | 4 | 10.2 | 2021-10-31
2021-11-01 | Click Here |  | 6.32 | 5.14 | 5.17 | 5.17 | 5.2 | 7.11 | 7.38 | 1.68 | 1.79 | 1.99 | 1.99 | 49 | 41 | 14 | 0 | 0 | 0 | 0.416 | 0.347 | 0.912 | 0.124 | 0.447 | 0.416 | 14.4 | 35.7 | 28.4 | 28.9 | 44.8 | 28.8 | 71.4 | 56.8 | 57.8 | 89.6 |  |  | 3.1 | 6 | 0.149 | 9.7 | 11.8 | 87.16 | 1.283 | 56.1 | 90.6 | 0.2549 | 0.0409 | 13.16 | 12.09 | 13.13 | 1.04 | 1.644 | 1.957 | 7.82 | 3.273 | 30.46 | 4 | 10.2 | 2021-11-01
2021-11-02 | Click Here |  | 6.55 | 5.27 | 5.09 | 5.27 | 5.36 | 7.86 | 7.3 | 1.65 | 1.77 | 2.01 | 2.02 | 50 | 43 | 16 | 0 | 0 | 0 | 0.525 | 0.348 | 0.905 | 0.154 | 0.415 | 0.436 | 13.8 | 35,2 | 29.6 | 30.5 | 44.7 | 27.6 | 70.4 | 59.2 | 61 | 89.4 |  |  | 3 | 5.9 | 0.176 | 10.9 | 12 | 90.4 | 1.255 | 56.1 | 88.7 | 0.2504 | 0.0519 | 13.6 | 12.57 | 12.6 | 1.03 | 1.645 | 2.191 | 8.04 | 3.265 | 29.79 | 4 | 10.2 | 2021-11-02
2021-11-03 | Click Here |  | 6.35 | 5.08 | 5.27 | 5.21 | 5.24 | 6.93 | 7.52 | 1.63 | 1.78 | 1.96 | 1.99 | 49 | 41 | 18 | 1 | 0 | 0 | 0.496 | 0.337 | 0.963 | 0.158 | 0.501 | 0.527 | 13.2 | 35.9 | 29.4 | 30.1 | 39.7 | 26.4 | 71.8 | 58.8 | 60.2 | 79.4 |  |  | 3 | 6 | 0.169 | 10.4 | 11.3 | 86.81 | 1.3415 | 56.4 | 89 | 0.2501 | 0.0516 | 12.86 | 11.83 | 12.08 | 1.05 | 1.625 | 1.981 | 7.74 | 3.3315 | 30.7 | 4 | 10 | 2021-11-03
2021-11-04 | Click Here |  | 6.41 | 5.33 | 5.31 | 5.19 | 5.3 | 6.84 | 7.41 | 1.76 | 1.87 | 1.97 | 2.01 | 49 | 42 | 35 | 5 | 2 | 0 | 0.496 | 0.334 | 1.9 | 0.34 | 0.545 | 0.485 | 12.9 | 32.6 | 27.7 | 27.9 | 41.4 | 25.8 | 65.2 | 55.4 | 55.8 | 82.8 |  |  | 3 | 5.8 | 0.199 | 10.3 | 11 | 83.79 | 1.3375 | 54.7 | 85.9 | 0.2616 | 0.0657 | 12.44 | 11.33 | 12.39 | 1.06 | 1.616 | 1.554 | 7.663 | 3.3575 | 30.86 | 4 | 10 | 2021-11-04
2021-11-05 | Click Here |  | 6.3 | 5.1 | 4.98 | 5.19 | 5.25 | 6.86 | 6.67 | 1.68 | 1.85 | 2.12 | 2.05 | 43 | 37 | 36 | 3 | 0 | 0 | 0.497 | 0.324 | 1.31 | 0.165 | 0.652 | 0.544 | 12.3 | 33.7 | 27.8 | 27.9 | 39.5 | 24.6 | 67.4 | 55.6 | 55.8 | 79 |  |  | 3.1 | 5.9 | 0.34 | 9.4 | 11.7 | 83.79 | 1.1174 | 56.7 | 87.2 | 0.2464 | 0.0595 | 12.17 | 12.01 | 12.01 | 0 | 1.638 | 1.445 | 7.748 | 3.1674 | 30.98 | 3.9 | 10 | 2021-11-05
2021-11-06 | Click Here |  | 6.27 | 5.08 | 5 | 5.12 | 5.19 | 7.08 | 7.12 | 1.71 | 1.87 | 2.1 | 2.05 | 42 | 36 | 31 | 2 | 0 | 0 | 0.476 | 0.318 | 1.19 | 0.157 | 0.612 | 0.517 | 12.4 | 33.5 | 28.1 | 27.7 | 40.2 | 24.8 | 67 | 56.2 | 55.4 | 80.4 |  |  | 3 | 6 | 0.311 | 9.3 | 11.6 | 90.4 | 1.6179 | 56.6 | 88 | 0.2469 | 0.0584 | 12.37 | 11.22 | 12.29 | 1.07 | 0 | 0 | 0 | 3.6579 | 30.51 | 4.2 | 10.3 | 2021-11-06
2021-11-07 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2021-11-07
2021-11-08 | Click Here |  | 6.21 | 5 | 5.05 | 5.12 | 5.2 | 6.86 | 7.07 | 1.68 | 1.86 | 2.05 | 2.09 | 44 | 37 | 22 | 3 | 1 | 0 | 0.47 | 0.331 | 1.2 | 0.216 | 0.786 | 0.489 | 13.3 | 37 | 28.3 | 29.3 | 42.5 | 26.6 | 74 | 56.6 | 58.6 | 85 |  |  | 3 | 5.8 | 0.256 | 10.6 | 10.7 | 95.5 | 1.3246 | 56.7 | 85.5 | 0.3463 | 0.0677 | 13.9 | 12.81 | 13.86 | 1.05 | 1.684 | 1.955 | 8.634 | 3.3846 | 32.83 | 4.2 | 10.3 | 2021-11-08
2021-11-09 | Click Here |  | 6.41 | 5.03 | 5 | 5.11 | 5.18 | 6.47 | 6.52 | 1.53 | 1.75 | 2.13 | 2.16 | 45 | 38 | 36 | 3 | 1 | 0 | 0.49 | 0.335 | 1.714 | 0.183 | 1.413 | 1.008 | 13.5 | 36.9 | 28.1 | 28.6 | 39.1 | 27 | 73.8 | 56.2 | 57.2 | 78.2 | 3.41 | 3.48 | 3 | 5.7 | 0.154 | 11.1 | 11 | 92.61 | 1.4017 | 52.6 | 85.2 | 0.2789 | 0.0653 | 13.45 | 12.36 | 13.39 | 1.03 | 1.683 | 2.471 | 8.391 | 3.4017 | 32.3 | 4.2 | 10.5 | 2021-11-09
2021-11-10 | Click Here |  | 6.33 | 5.14 | 5.05 | 5.25 | 5.34 | 7.13 | 7.38 | 1.5 | 1.77 | 2.05 | 1.86 | 43 | 36 | 32 | 2 | 0 | 0 | 0.501 | 0.317 | 1.62 | 0.151 | 0.567 | 0.425 | 13.1 | 31.5 | 27.7 | 28.6 | 41.7 | 26.2 | 63 | 55.4 | 57.2 | 83.4 | 3.36 | 3.43 | 3.1 | 5.8 | 0.294 | 10.6 | 11.1 | 83.79 | 0.95432 | 52.8 | 86.6 | 0.2782 | 0.0583 | 13.96 | 12.92 | 13.95 | 1.03 | 1.69 | 2.601 | 8.835 | 2.9443 | 30.28 | 4.4 | 10.7 | 2021-11-10
2021-11-11 | Click Here |  | 6.31 | 5.26 | 5.33 | 5.11 | 5.2 | 7.32 | 7.51 | 1.58 | 1.84 | 1.98 | 2.02 | 40 | 34 | 30 | 2 | 0 | 0 | 0.456 | 0.331 | 1.38 | 0.389 | 0.602 | 0.448 | 12.2 | 30.4 | 28.3 | 29.1 | 41.3 | 24.4 | 60.8 | 56.6 | 58.2 | 82.6 | 3.38 | 3.59 | 3.1 | 5.9 | 0.271 | 10.1 | 10.9 | 83.46 | 1.0059 | 56.7 | 85.5 | 0.2464 | 0.0676 | 12.59 | 12.44 | 12.44 | 0 | 1.51 | 2.151 | 7.878 | 3.0459 | 30.75 | 4.4 | 10.7 | 2021-11-11
2021-11-12 | Click Here |  | 6.2 | 5.14 | 5.2 | 5.09 | 5.17 | 7.28 | 7.34 | 1.62 | 1.89 | 2.21 | 2.24 | 54 | 48 | 129 | 1 | 0 | 0 | 0.394 | 0.341 | 1.41 | 0.219 | 0.448 | 0.359 | 13.4 | 35.2 | 27.5 | 28 | 43.8 | 26.8 | 70.4 | 55 | 56 | 87.6 | 3.34 | 3.64 | 3.1 | 6 | 0.217 | 9.2 | 10.9 | 87.03 | 1.2584 | 56.6 | 87.8 | 0.2469 | 0.056 | 12.86 | 11.8 | 12.86 | 1.06 | 1.57 | 2.439 | 7.949 | 3.3484 | 31.22 | 4.4 | 10.7 | 2021-11-12
2021-11-13 | Click Here |  | 6.29 | 5.17 | 5.29 | 5.14 | 5.25 | 7.34 | 7.29 | 1.74 | 1.93 | 2.11 | 2.14 | 48 | 39 | 21 | 1 | 0 | 0 | 0.412 | 0.317 | 1.86 | 0.241 | 0.609 | 0.541 | 13.3 | 34.8 | 28.1 | 28.6 | 44.7 | 26.6 | 69.6 | 56.2 | 57.2 | 89.4 | 3.33 | 3.56 | 3 | 5.9 | 0.192 | 9.1 | 10.7 | 86 | 1.2863 | 56.9 | 89.8 | 0.2413 | 0.0482 | 12.6 | 11.53 | 12.56 | 1.03 | 0 | 0 | 0 | 3.3863 | 30.57 | 4.4 | 10.7 | 2021-11-13
2021-11-14 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2021-11-14
2021-11-15 | Click Here |  | 6.12 | 5.13 | 5.19 | 5.29 | 5.31 | 7.28 | 7.26 | 1.59 | 1.73 | 2.16 | 2.07 | 44 | 36 | 29 | 5 | 0 | 0 | 0.717 | 0.32 | 1.06 | 0.165 | 0.563 | 0.353 | 13.2 | 34.7 | 27 | 27.8 | 42.6 | 26.4 | 69.4 | 54 | 55.6 | 85.2 | 2.63 | 2.52 | 3.1 | 5.9 | 0.314 | 10 | 11.2 | 83.79 | 0.9803 | 55.8 | 88.9 | 0.2533 | 0.0509 | 13.33 | 12.27 | 13.33 | 1.06 | 1.721 | 1.87 | 8.354 | 3.1003 | 30.75 | 4.4 | 10.7 | 2021-11-15
2021-11-16 | Click Here |  | 6.21 | 5.14 | 5.11 | 5.26 | 5.33 | 6.96 | 6.82 | 1.6 | 1.79 | 2.09 | 2.05 | 42 | 35 | 26 | 3 | 0 | 0 | 0.689 | 0.332 | 1.12 | 0.158 | 0.692 | 0.539 | 13.1 | 33.6 | 27.2 | 28.1 | 40.3 | 26.2 | 67.2 | 54.4 | 56.2 | 80.6 | 2.96 | 3.38 | 3 | 6.1 | 0.284 | 10 | 11 | 97.02 | 1.2768 | 56.2 | 89.3 | 0.2492 | 0.049 | 14.33 | 13.32 | 14.3 | 0.98 | 1.835 | 2.723 | 8.344 | 3.3068 | 30.51 | 4.4 | 10.7 | 2021-11-16
2021-11-17 | Click Here |  | 6.55 | 5.05 | 5.07 | 5.23 | 5.3 | 7.66 | 7.33 | 1.46 | 1.69 | 1.99 | 2.02 | 49 | 40 | 24 | 5 | 1 | 0 | 0.967 | 0.727 | 1.54 | 0.305 | 0.668 | 0.467 | 12.6 | 35.8 | 28 | 28.6 | 42.3 | 25.2 | 71.6 | 56 | 57.2 | 84.6 | 3.01 | 3.39 | 2.9 | 5.8 | 0.278 | 9 | 10.2 | 99.89 | 1.1426 | 58.8 | 88.9 | 0.2306 | 0.051 | 14.89 | 13.9 | 14.97 | 1.07 | 1.691 | 3.042 | 8.193 | 3.2626 | 32.31 | 4.7 | 10.7 | 2021-11-17
2021-11-18 | Click Here |  | 6.47 | 5.21 | 5.24 | 5.36 | 5.4 | 7.54 | 7.61 | 1.52 | 1.69 | 2.16 | 2.19 | 51 | 43 | 26 | 4 | 2 | 0 | 0.924 | 0.736 | 1.77 | 0.368 | 0.286 | 0.247 | 13.1 | 36 | 27.9 | 28.4 | 47.8 | 26.2 | 72 | 55.8 | 56.8 | 85.6 | 3.08 | 3.47 | 2.8 | 5.9 | 0.049 | 8.9 | 10 | 93.89 | 1.4083 | 54 | 89.2 | 0.2673 | 0.0494 | 13.61 | 12.15 | 13.64 | 1.49 | 1.669 | 2.354 | 8.512 | 3.5083 | 30.52 | 4.7 | 10.7 | 2021-11-18
2021-11-19 | Click Here |  | 6.39 | 5.1 | 5.06 | 5.24 | 5.26 | 7.59 | 7.76 | 1.57 | 1.7 | 2.08 | 2.09 | 54 | 47 | 22 | 1 | 0 | 0 | 0.496 | 0.554 | 1.24 | 0.187 | 0.594 | 0.637 | 13.6 | 35.8 | 28.1 | 28.5 | 46.4 | 27.2 | 71.6 | 56.2 | 57 | 92.8 | 2.98 | 3.36 | 3 | 5.9 | 0.062 | 9 | 9.9 | 90.69 | 1.3256 | 54.2 | 89.9 | 0.2659 | 0.0448 | 13.72 | 12.27 | 13.74 | 1.47 | 1.675 | 2.043 | 8.292 | 3.3556 | 29.59 | 4.7 | 10.7 | 2021-11-19
2021-11-20 | Click Here |  | 6.32 | 5.2 | 5.17 | 5.26 | 5.31 | 7.48 | 7.62 | 1.64 | 1.82 | 2.06 | 2.04 | 59 | 51 | 29 | 3 | 1 | 0 | 0.612 | 0.604 | 1.29 | 0.139 | 0.314 | 0.296 | 13 | 34.9 | 27.7 | 28.3 | 44.8 | 26 | 69.8 | 55.4 | 56.6 | 89.6 | 3.05 | 3.46 | 2.9 | 6 | 0.042 | 8.8 | 9.8 | 90.2 | 1.1921 | 53.2 | 90.1 | 0.2779 | 0.0442 | 13.18 | 12.18 | 13.2 | 1.02 | 0 | 0 | 0 | 3.3621 | 30.63 | 4.8 | 10.7 | 2021-11-20
2021-11-21 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 90.93 | 1.2931 | 0 | 0 | 0 | 0 | 13.14 | 12.06 | 13.09 | 1.03 | 1.453 | 1.867 | 8.245 | 3.4231 | 0 | 4.8 | 10.7 | 2021-11-21
2021-11-22 | Click Here |  | 6.49 | 5.11 | 4.94 | 5.17 | 5.23 | 6.65 | 7.07 | 1.44 | 1.69 | 2.18 | 2.2 | 50 | 42 | 22 | 2 | 1 | 0 | 0.496 | 0.445 | 1.37 | 0.214 | 0.861 | 1.201 | 12.6 | 34.9 | 26.5 | 27.9 | 41.6 | 25.2 | 69.8 | 53 | 55.8 | 83.2 | 2.96 | 3.31 | 2.9 | 6 | 0.205 | 8.5 | 9.4 | 86 | 1.1501 | 60.2 | 89 | 0.2202 | 0.0503 | 12.68 | 11.62 | 12.63 | 1.01 | 1.511 | 1.821 | 8.467 | 3.3601 | 30.48 | 4.8 | 10.7 | 2021-11-22
2021-11-23 | Click Here |  | 6.33 | 5.13 | 5.11 | 5.2 | 5.26 | 7.1 | 7.04 | 1.56 | 1.74 | 2.12 | 2.18 | 48 | 34 | 31 | 3 | 0 | 0 | 0.557 | 0.49 | 1.41 | 0.189 | 0.864 | 0.718 | 12.5 | 33.7 | 27.1 | 28 | 42.2 | 25 | 67.4 | 54.2 | 56 | 84.4 | 3.09 | 3.33 | 3 | 5.9 | 0.194 | 9.6 | 10.9 | 92.61 | 1.2635 | 60.4 | 90.1 | 0.22 | 0.0488 | 13.29 | 12.21 | 13.23 | 1.02 | 1.538 | 2.05 | 8.342 | 3.4435 | 30.51 | 4.9 | 10.8 | 2021-11-23
2021-11-24 | Click Here |  | 6.28 | 4.97 | 5.16 | 5.11 | 5.21 | 5.73 | 5.88 | 1.54 | 1.85 | 2.07 | 2.16 | 57 | 49 | 51 | 6 | 2 | 0 | 0.722 | 0.507 | 2.01 | 0.301 | 0.425 | 0.318 | 13.1 | 35.4 | 27.1 | 27.8 | 34.9 | 26.2 | 70.8 | 54.2 | 55.6 | 69.8 | 4.07 | 3.18 | 3 | 5.6 | 0.319 | 8.8 | 9 | 90.16 | 1.1216 | 54.6 | 85.7 | 0.2627 | 0.067 | 13.52 | 12.55 | 13.6 | 1.05 | 1.632 | 1.897 | 8.238 | 3.2616 | 30.31 | 4.9 | 10.8 | 2021-11-24
2021-11-25 | Click Here |  | 6.19 | 5 | 5.12 | 5.07 | 5.1 | 6.13 | 7.05 | 1.46 | 1.6 | 2.15 | 2.12 | 51 | 43 | 36 | 8 | 4 | 1 | 0.665 | 0.47 | 1.67 | 0.414 | 1.45 | 0.927 | 13.9 | 34.5 | 29.1 | 30.5 | 38.7 | 27.8 | 69 | 58.2 | 61 | 77.4 | 4.03 | 3.22 | 3.1 | 5.7 | 0.173 | 8.7 | 9 | 90.41 | 1.1706 | 51.8 | 85 | 0.2857 | 0.0704 | 13.13 | 12.55 | 13.08 | 0.53 | 1.668 | 1.977 | 8.308 | 3.2706 | 30.67 | 5 | 10.8 | 2021-11-25
2021-11-26 | Click Here |  | 6.27 | 5.27 | 5.06 | 5.24 | 5.22 | 7.28 | 7.74 | 1.55 | 1.74 | 2.1 | 2.15 | 48 | 40 | 31 | 2 | 0 | 0 | 0.632 | 0.449 | 1.52 | 0.229 | 2.2 | 1.037 | 16.2 | 36.2 | 29.5 | 29.7 | 45 | 32.4 | 72.4 | 59 | 59.4 | 90 | 3.79 | 3.26 | 3 | 6 | 0.162 | 10.9 | 10.1 | 88.2 | 1.1108 | 51.7 | 88.1 | 0.286 | 0.0564 | 12.9 | 12.28 | 12.78 | 0.5 | 1.582 | 1.937 | 7.846 | 3.2608 | 30.51 | 5.2 | 10.8 | 2021-11-26
2021-11-27 | Click Here |  | 6.21 | 5.08 | 5.26 | 5.17 | 5.2 | 7.34 | 8.21 | 1.6 | 1.82 | 2.11 | 2.15 | 46 | 38 | 28 | 1 | 0 | 0 | 0.628 | 0.456 | 1.39 | 0.189 | 0.405 | 0.296 | 15.4 | 35.2 | 30.1 | 29.9 | 44.6 | 30.8 | 70.4 | 60.2 | 59.8 | 89.2 | 3.52 | 3.21 | 3.1 | 5.9 | 0.144 | 10.9 | 10.1 | 83.79 | 1.2156 | 52 | 88.4 | 0.2771 | 0.0541 | 12.27 | 11.17 | 12.22 | 1.05 | 0 | 0 | 0 | 3.4056 | 31.45 | 5.2 | 10.5 | 2021-11-27
2021-11-28 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2021-11-28
2021-11-29 | Click Here |  | 5.98 | 5.28 | 4.93 | 5.2 | 5.3 | 7.44 | 7.96 | 1.8 | 1.91 | 2.17 | 2.16 | 57 | 48 | 36 | 4 | 0 | 0 | 0.749 | 0.527 | 1.42 | 0.181 | 0.387 | 0.386 | 13.6 | 37.3 | 29 | 29.8 | 46.1 | 27.2 | 74.6 | 58 | 59.6 | 92.2 | 3.01 | 2.75 | 3.1 | 5.9 | 0.299 | 9.7 | 9.5 | 92.61 | 1.245 | 57.4 | 92.9 | 0.2411 | 0.0319 | 13.3 | 12.24 | 13.3 | 1.06 | 1.448 | 1.955 | 8.22 | 3.435 | 30.98 | 5.4 | 10.8 | 2021-11-29
2021-11-30 | Click Here |  | 6.16 | 5.32 | 5.28 | 5.1 | 5.35 | 7.85 | 7.58 | 1.64 | 1.91 | 2.16 | 2.14 | 54 | 46 | 61 | 17 | 1 | 0 | 0.816 | 0.591 | 2.76 | 0.351 | 0.369 | 0.228 | 14.1 | 36.9 | 29.2 | 29.6 | 44.6 | 28.2 | 73.8 | 58.4 | 59.2 | 89.2 | 2.64 | 2.39 | 3 | 5.8 | 0.288 | 10.1 | 9.6 | 86 | 1.2343 | 54.2 | 89.2 | 0.2656 | 0.0496 | 15.06 | 11.64 | 12.66 | 1.02 | 1.433 | 1.938 | 7.859 | 3.3543 | 30.75 | 5.4 | 10.8 | 2021-11-30
2021-12-01 | Click Here |  | 6.21 | 5.2 | 5.41 | 5.25 | 5.3 | 7.57 | 7.45 | 1.78 | 1.92 | 2.18 | 2.06 | 65 | 57 | 63 | 4 | 0 | 0 | 2.02 | 0.965 | 2.46 | 0.147 | 0.219 | 0.147 | 13.7 | 30.4 | 28.4 | 28.7 | 41.7 | 27.4 | 60.8 | 56.8 | 57.4 | 83.4 | 2.79 | 2.68 | 3.1 | 5.9 | 0.233 | 10.2 | 9.5 | 92.61 | 1.3579 | 57.1 | 88.8 | 0.2427 | 0.0516 | 15.02 | 12.02 | 13.1 | 1.08 | 1.466 | 1.951 | 7.63 | 3.4979 | 30.51 | 5 | 10 | 2021-12-01
2021-12-02 | Click Here |  | 6.11 | 5.17 | 4.84 | 5.25 | 5.48 | 7.4 | 7.54 | 1.55 | 1.74 | 1.87 | 1.78 | 55 | 47 | 12 | 5 | 0 | 0 | 0.854 | 0.654 | 0.625 | 0.121 | 0.34 | 0.11 | 13.6 | 36 | 28.1 | 27.8 | 42.4 | 27.2 | 72 | 56.2 | 55.6 | 84.8 | 2.58 | 2.66 | 3.1 | 6 | 0.261 | 9.3 | 9.1 | 88.2 | 1.1632 | 58 | 89.6 | 0.2364 | 0.0475 | 12.63 | 12.54 | 12.54 | 0 | 1.49 | 1.976 | 8.169 | 3.1932 | 30.98 | 4.8 | 9.8 | 2021-12-02
2021-12-03 | Click Here |  | 6.07 | 5.2 | 5.22 | 5.24 | 5.53 | 7.23 | 7.12 | 1.64 | 1.9 | 2.05 | 1.97 | 54 | 46 | 11 | 2 | 0 | 0 | 0.829 | 0.663 | 0.595 | 0.112 | 0.292 | 0.158 | 13.4 | 35.7 | 29 | 28.6 | 41.8 | 26.8 | 71.4 | 58 | 57.2 | 83.6 | 2.74 | 2.8 | 3 | 5.8 | 0.14 | 9.3 | 9 | 88.2 | 1.4469 | 58.2 | 90.1 | 0.2358 | 0.0464 | 12.63 | 11.55 | 12.61 | 1.06 | 1.479 | 1.95 | 8.182 | 3.4669 | 30.51 | 4.8 | 9.8 | 2021-12-03
2021-12-04 | Click Here |  | 6.01 | 5.08 | 5.01 | 5.19 | 5.31 | 6.97 | 7.05 | 1.65 | 1.9 | 2.09 | 2.16 | 85 | 74 | 4 | 0 | 0 | 0 | 3.96 | 2.3 | 0.556 | 0.134 | 0.403 | 0.217 | 13.1 | 35.9 | 28.3 | 28.8 | 41.9 | 26.2 | 71.8 | 56.6 | 57.6 | 83.4 | 2.75 | 2.85 | 3 | 5.9 | 0.155 | 8.5 | 8 | 81.6 | 1.1711 | 59.6 | 88 | 0.2248 | 0.0555 | 12.41 | 11.36 | 12.35 | 0.99 | 0 | 0 | 0 | 3.2611 | 30.55 | 4.8 | 9.8 | 2021-12-04
2021-12-05 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2021-12-05
2021-12-06 | Click Here |  | 5.98 | 4.97 | 5.1 | 5.16 | 5.2 | 7.25 | 7.49 | 1.83 | 1.92 | 2.28 | 2.05 | 59 | 52 | 23 | 0 | 0 | 0 | 1.18 | 0.78 | 1.24 | 0.166 | 0.212 | 0.118 | 12.4 | 35.5 | 26.2 | 27 | 42.4 | 24.8 | 71 | 52.4 | 54 | 84.8 | 2.13 | 2.12 | 3.1 | 5.9 | 0.05 | 7.1 | 5.9 | 79.38 | 0.94822 | 54.5 | 89.1 | 0.2634 | 0.0499 | 13.05 | 11.98 | 13.05 | 1.07 | 1.525 | 1.912 | 8.383 | 3.0082 | 29.57 | 4.9 | 9.8 | 2021-12-06
2021-12-07 | Click Here |  | 6.06 | 5.22 | 4.97 | 5.27 | 5.25 | 7.36 | 7.26 | 1.81 | 1.92 | 2.02 | 2.05 | 65 | 58 | 24 | 5 | 0 | 0 | 1.43 | 0.762 | 1.22 | 0.144 | 0.286 | 0.141 | 12.5 | 35.6 | 26.3 | 26.2 | 42.7 | 25 | 71.2 | 52.6 | 52.4 | 85.4 | 2.71 | 2.47 | 3 | 5.8 | 0.258 | 8 | 5.8 | 77.17 | 1.3191 | 51.2 | 88.4 | 0.2901 | 0.0533 | 11.88 | 10.75 | 11.8 | 1.05 | 1.512 | 2.023 | 6.508 | 3.2591 | 30.75 | 4.9 | 9.8 | 2021-12-07
2021-12-08 | Click Here |  | 6.34 | 5.23 | 5.15 | 5.27 | 5.28 | 7.94 | 7.3 | 1.79 | 1.9 | 1.94 | 1.88 | 61 | 54 | 23 | 2 | 0 | 0 | 0.941 | 1.23 | 1.12 | 0.124 | 0.237 | 0.201 | 12.3 | 36.2 | 26.4 | 26.2 | 40 | 24.6 | 72.4 | 52.8 | 52.4 | 80 | 2.73 | 2.51 | 3 | 5.9 | 0.046 | 7.5 | 8.1 | 83.11 | 1.227 | 57.1 | 87.3 | 0.2432 | 0.0586 | 13.37 | 13.3 | 13.3 | 0 | 1.482 | 1.916 | 8.988 | 2.837 | 30.06 | 4.8 | 9.8 | 2021-12-08
2021-12-09 | Click Here |  | 6.41 | 5.29 | 5.43 | 5.33 | 5.3 | 7.44 | 7.37 | 1.81 | 1.94 | 1.99 | 2.01 | 59 | 52 | 19 | 1 | 0 | 0 | 1.06 | 0.994 | 1.19 | 0.103 | 0.286 | 0.277 | 12.7 | 36.4 | 26.5 | 26.1 | 39.8 | 25.4 | 72.8 | 53 | 52.2 | 79.6 | 2.88 | 2.65 | 3 | 6.1 | 0.041 | 7.4 | 8.1 | 79.38 | 1.5015 | 57.4 | 88.8 | 0.2352 | 0.0506 | 12.9 | 11.81 | 12.87 | 1.06 | 1.479 | 1.92 | 7.905 | 3.0515 | 30.5 | 4.8 | 9.8 | 2021-12-09
2021-12-10 | Click Here |  | 6.21 | 5.18 | 5.44 | 5.25 | 5.27 | 6.96 | 7.31 | 1.47 | 1.67 | 1.95 | 2 | 58 | 50 | 31 | 0 | 0 | 0 | 0.993 | 0.846 | 1.21 | 0.261 | 0.326 | 0.307 | 11.9 | 33.7 | 26 | 26.5 | 40.9 | 23.8 | 67.4 | 52 | 53 | 81.8 | 2.81 | 2.77 | 3.1 | 6 | 0.171 | 6.5 | 7.5 | 79.38 | 1.662 | 48.2 | 83.5 | 0.3167 | 0.078 | 12.28 | 11.22 | 12.26 | 1.04 | 1.477 | 1.904 | 7.466 | 3.212 | 30.76 | 4.8 | 9.8 | 2021-12-10
2021-12-11 | Click Here |  | 6.05 | 5.04 | 4.96 | 5.12 | 5.16 | 6.47 | 6.58 | 1.44 | 1.66 | 1.99 | 2.13 | 59 | 52 | 19 | 1 | 0 | 0 | 0.896 | 0.753 | 0.994 | 0.132 | 0.286 | 0.124 | 11.8 | 33.2 | 26.2 | 26.4 | 40.3 | 23.6 | 66.4 | 52.4 | 52.8 | 80.6 | 2.8 | 2.86 | 3 | 5.8 | 0.088 | 6.5 | 7.5 | 80.09 | 0.9681 | 48.4 | 84.2 | 0.3165 | 0.0745 | 12.94 | 11.89 | 12.92 | 1.03 | 0 | 0 | 0 | 3.0581 | 30.96 | 4.8 | 9.8 | 2021-12-11
2021-12-12 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 78.39 | 0.84169 | 0 | 0 | 0 | 0 | 12.63 | 12.48 | 12.48 | 0 | 1.361 | 1.916 | 8.013 | 2.8517 | 0 | 5 | 9.8 | 2021-12-12
2021-12-13 | Click Here |  | 6.12 | 5.2 | 5.18 | 5.22 | 5.28 | 7.41 | 7.33 | 1.59 | 1.81 | 1.96 | 2.01 | 60 | 54 | 20 | 0 | 0 | 0 | 0.886 | 0.741 | 1.19 | 0.147 | 0.311 | 0.256 | 12.2 | 33.7 | 26.5 | 26.9 | 40.7 | 24.4 | 67.4 | 53 | 53.8 | 81.4 | 2.81 | 2.93 | 3 | 6 | 0.074 | 7.2 | 8.3 | 86.06 | 1.3409 | 53.2 | 88.9 | 0.2727 | 0.0507 | 13.83 | 11.73 | 13.87 | 2.14 | 1.498 | 1.929 | 8.101 | 3.3309 | 30.14 | 5 | 9.8 | 2021-12-13
2021-12-14 | Click Here |  | 6.09 | 5.16 | 5.12 | 5.2 | 5.24 | 7.2 | 7.13 | 1.64 | 1.83 | 2.01 | 1.97 | 69 | 61 | 20 | 1 | 0 | 0 | 0.717 | 0.633 | 1.14 | 0.161 | 0.268 | 0.247 | 12.6 | 36.2 | 26.5 | 26.4 | 37.8 | 25.2 | 72.4 | 53 | 52.8 | 75.6 | 2.73 | 2.89 | 2.9 | 5.8 | 0.061 | 7.1 | 8.3 | 77.17 | 0.69786 | 54.2 | 89.4 | 0.2647 | 0.0496 | 12.85 | 12.75 | 12.75 | 0 | 1.482 | 1.91 | 7.96 | 2.7479 | 30.38 | 5 | 9.8 | 2021-12-14
2021-12-15 | Click Here |  | 6.03 | 4.95 | 5.04 | 5.08 | 5.12 | 6.79 | 7.16 | 1.4 | 1.61 | 1.96 | 2.01 | 67 | 56 | 28 | 0 | 0 | 0.263 | 0.694 | 0.556 | 1.51 | 0.164 | 0.336 | 0.263 | 11.7 | 35.6 | 25.7 | 26.5 | 36.7 | 23.4 | 69.2 | 51.4 | 53 | 73.4 | 2.8 | 2.88 | 3 | 5.9 | 0.126 | 6.7 | 7.2 | 85.58 | 1.2411 | 54.4 | 84.8 | 0.2646 | 0.0712 | 13.36 | 12.33 | 13.35 | 1.02 | 1.496 | 1.95 | 8.15 | 3.1511 | 30.22 | 4.8 | 9.8 | 2021-12-15
2021-12-16 | Click Here |  | 6.14 | 5.17 | 5.09 | 5.22 | 5.23 | 6.81 | 7.35 | 1.43 | 1.64 | 1.91 | 1.94 | 78 | 67 | 39 | 4 | 1 | 0 | 0.84 | 0.536 | 2.29 | 0.263 | 1.206 | 1.11 | 12 | 33.7 | 25.6 | 26.6 | 39.4 | 24 | 67.4 | 51.2 | 53.2 | 78.8 | 2.76 | 2.82 | 3 | 5.8 | 0.137 | 7.3 | 6.9 | 83.79 | 1.3594 | 54.2 | 81.6 | 0.2648 | 0.0882 | 12.66 | 11.6 | 12.63 | 1.03 | 1.497 | 1.952 | 7.773 | 3.2794 | 30.26 | 5 | 10 | 2021-12-16
2021-12-17 | Click Here |  | 5.82 | 5.17 | 5.3 | 5.24 | 5.25 | 6.91 | 7.39 | 1.41 | 1.51 | 1.91 | 1.88 | 71 | 64 | 41 | 7 | 0 | 0 | 1.04 | 0.556 | 2.17 | 0.27 | 0.493 | 0.396 | 13.4 | 35 | 27.4 | 27.8 | 39.7 | 26.8 | 70 | 54.8 | 55.6 | 79.4 | 3.09 | 3.2 | 3.1 | 6 | 0.072 | 6.5 | 7 | 77.17 | 0.95303 | 44.6 | 85.7 | 0.3505 | 0.0668 | 13.25 | 12.28 | 13.27 | 0.99 | 1.546 | 1.947 | 8.062 | 2.853 | 30.51 | 5.3 | 10.2 | 2021-12-17
2021-12-18 | Click Here |  | 5.96 | 5.12 | 5.09 | 5.26 | 5.3 | 6.93 | 7.07 | 1.38 | 1.49 | 1.96 | 1.87 | 58 | 50 | 24 | 2 | 0 | 0 | 0.858 | 0.521 | 1.28 | 0.265 | 0.576 | 0.439 | 11.3 | 32.2 | 27.1 | 25.1 | 37.5 | 22.6 | 64.4 | 54.2 | 50.2 | 75 | 2.9 | 3.01 | 3 | 6 | 0.055 | 6.7 | 7.5 | 83.79 | 1.1979 | 46.9 | 85.5 | 0.3284 | 0.0677 | 13.36 | 12.24 | 13.33 | 1.09 | 0 | 0 | 0 | 3.1079 | 30.75 | 5 | 10.4 | 2021-12-18
2021-12-19 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2021-12-19
2021-12-20 | Click Here |  | 5.9 | 5 | 5.02 | 5.16 | 5.19 | 6.7 | 6.75 | 1.28 | 1.43 | 1.82 | 1.89 | 59 | 51 | 21 | 1 | 0 | 0 | 0.761 | 0.497 | 1.25 | 0.193 | 0.618 | 0.524 | 11.6 | 33.2 | 24.7 | 25.6 | 37.5 | 23.2 | 66.4 | 49.4 | 51.2 | 75 | 2.95 | 2.97 | 3 | 5.9 | 0.194 | 6.6 | 6.7 | 0 |  | 49.3 | 82.8 | 0.3069 | 0.0817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30.06 | 5 | 10.6 | 2021-12-20
2021-12-21 | Click Here |  | 6.36 | 5.14 | 5.2 | 5.2 | 5.26 | 6.8 | 6.88 | 1.38 | 1.53 | 1.96 | 2 | 65 | 59 | 23 | 3 | 1 | 0 | 0.77 | 0.496 | 1.21 | 0.269 | 0.65 | 0.664 | 11.3 | 31.2 | 24.9 | 24.8 | 38.7 | 22.6 | 62.4 | 49.8 | 49.6 | 79.4 | 2.98 | 3.01 | 3 | 5.8 | 0.052 | 7.1 | 6.8 | 90.41 | 1.3475 | 46 | 84.8 | 0.3369 | 0.0716 | 13.48 | 12.41 | 13.46 | 1.05 | 1.464 | 1.938 | 8.282 | 3.3075 | 31.97 | 5.3 | 10.9 | 2021-12-21
2021-12-22 | Click Here |  | 6.23 | 5.24 | 5.09 | 5.32 | 5.31 | 6.96 | 6.84 | 1.42 | 1.56 | 1.93 | 1.9 | 62 | 54 | 21 | 2 | 0 | 0 | 0.761 | 0.471 | 1.18 | 0.27 | 0.542 | 0.521 | 11.6 | 31.2 | 25 | 24.9 | 40.1 | 23.2 | 62.4 | 50 | 49.8 | 80.2 | 3.03 | 3.01 | 3.1 | 6.1 | 0.054 | 7 | 6.8 | 81.58 | 0.86297 | 46.3 | 85.1 | 0.3348 | 0.0689 | 14.14 | 13.12 | 14.16 | 1.04 | 1.447 | 1.93 | 8.205 | 2.823 | 29.57 | 5.5 | 11.1 | 2021-12-22
2021-12-23 | Click Here |  | 6.19 | 5.12 | 5.27 | 5.21 | 5.23 | 6.4 | 7.12 | 1.53 | 1.64 | 1.97 | 1.92 | 64 | 58 | 35 | 10 | 2 | 0 | 0.747 | 0.463 | 2.9 | 0.405 | 1.6 | 0.675 | 11.9 | 31.2 | 24.9 | 24.5 | 37.1 | 23.8 | 62.4 | 49.8 | 49 | 74.2 | 3.05 | 3.36 | 3 | 3.36 | 0.048 | 6.8 | 6.8 | 86.55 | 1.3272 | 47.4 | 85.2 | 0.3242 | 0.0696 | 13.33 | 12.29 | 13.33 | 1.04 | 1.406 | 1.966 | 8.676 | 3.1972 | 32.39 | 5.2 | 11.1 | 2021-12-23
2021-12-24 | Click Here |  | 6.1 | 5.17 | 5.13 | 5.26 | 5.3 | 7.44 | 7.59 | 1.47 | 1.61 | 1.92 | 1.88 | 61 | 54 | 30 | 4 | 0 | 0 | 0.627 | 0.469 | 1.76 | 0.214 | 0.694 | 0.544 | 12.2 | 31.6 | 25.1 | 24.9 | 38.2 | 24.4 | 63.2 | 50.2 | 49.8 | 76.4 | 3.11 | 3.48 | 3 | 5.9 | 0.039 | 6.5 | 6.7 | 90.45 | 1.3868 | 47.5 | 87.4 | 0.3237 | 0.0596 | 13.54 | 12.57 | 13.6 | 1.03 | 1.367 | 1.968 | 8.592 | 3.2668 | 30.38 | 5.2 | 12 | 2021-12-24
2021-12-25 | Click Here |  | 6.07 | 5.11 | 5.04 | 5.33 | 5.38 | 7.79 | 8.01 | 1.54 | 1.7 | 2.01 | 1.96 | 59 | 52 | 25 | 2 | 0 | 0 | 0.612 | 0.456 | 1.54 | 0.204 | 0.614 | 0.546 | 11.7 | 32.1 | 26.4 | 26.1 | 39.4 | 23.4 | 64.2 | 54.8 | 54.2 | 78.8 | 3.03 | 3.41 | 3 | 6.1 | 0.042 | 6.4 | 6.6 | 88.2 | 1.1959 | 47.9 | 89.2 | 0.3201 | 0.0494 | 13.87 | 12.81 | 13.83 | 1.02 | 0 | 0 | 0 | 3.1259 | 31.05 | 5.2 | 11.8 | 2021-12-25
2021-12-26 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2021-12-26
2021-12-27 | Click Here |  | 6.06 | 5.17 | 4.96 | 5.29 | 5.31 | 7.38 | 7.84 | 1.62 | 1.74 | 2.02 | 1.81 | 59 | 51 | 54 | 11 | 2 | 0 | 0.752 | 0.437 | 2.22 | 0.43 | 0.889 | 0.966 | 13.3 | 35.9 | 26.9 | 27.3 | 41.5 | 26.6 | 71.8 | 53.8 | 54.6 | 83 | 3.05 | 3.32 | 3.1 | 5.9 | 0.115 | 7 | 8 | 0 |  | 48.8 | 87 | 0.3112 | 0.0601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30.98 | 5.2 | 11.8 | 2021-12-27
2021-12-28 | Click Here |  | 6.13 | 5.18 | 5.14 | 5.31 | 5.35 | 7.18 | 7.33 | 1.67 | 1.83 | 2.09 | 1.98 | 61 | 51 | 25 | 3 | 0 | 0 | 0.663 | 0.422 | 1.4 | 0.26 | 1.69 | 0.506 | 13.7 | 36.3 | 27.6 | 28.3 | 42.3 | 27.4 | 72.6 | 55.2 | 56.6 | 84.6 | 3.22 | 3.21 | 3.1 | 6 | 0.127 | 6.1 | 6.5 | 64.03 | 0.48191 | 57.6 | 90.4 | 0.2391 | 0.0436 | 12.84 | 11.76 | 12.79 | 1.03 | 1.382 | 1.703 | 8.519 | 2.4719 | 31.22 | 5.2 | 11.8 | 2021-12-28
2021-12-29 | Click Here |  | 6.09 | 5.17 | 5.15 | 5.24 | 5.29 | 6.95 | 6.77 | 1.76 | 1.91 | 1.99 | 1.98 | 59 | 50 | 22 | 2 | 0 | 0 | 0.548 | 0.409 | 1.29 | 0.312 | 0.499 | 0.336 | 12.4 | 35.7 | 26.9 | 27.2 | 38.7 | 24.8 | 71.4 | 53.8 | 54.4 | 77.4 | 3.11 | 3.23 | 3 | 5.8 | 0.094 | 6.5 | 7.6 | 91.11 | 1.3497 | 57.9 | 90.9 | 0.2357 | 0.0409 | 13.5 | 12.46 | 13.49 | 1.03 | 1.364 | 1.715 | 8.602 | 3.3197 | 30.57 | 5.2 | 11.8 | 2021-12-29
2021-12-30 | Click Here |  | 6.17 | 5.26 | 5.14 | 5.6 | 6.04 | 7.77 | 6.6 | 1.56 | 1.79 | 1.98 | 1.94 | 62 | 55 | 19 | 2 | 0 | 0 | 0.498 | 0.376 | 1.33 | 0.217 | 0.654 | 0.458 | 13.5 | 35.8 | 27.2 | 28 | 39.6 | 27 | 71.6 | 54.4 | 56 | 79.2 | 3.42 | 3.18 | 3 | 5.9 | 0.019 | 5.7 | 7.1 | 88.2 | 1.2967 | 50.2 | 87.1 | 0.299 | 0.0595 | 13.44 | 12.41 | 13.48 | 1.07 | 1.36 | 1.719 | 8.915 | 3.2267 | 30.86 | 5.2 | 11.8 | 2021-12-30
2021-12-31 | Click Here |  | 6.16 | 5.12 | 5.21 | 5.24 | 5.26 | 7.11 | 7.65 | 1.58 | 1.79 | 1.96 | 1.92 | 61 | 57 | 20 | 1 | 0 | 0 | 0.499 | 0.384 | 1.29 | 0.206 | 0.591 | 0.457 | 13.4 | 36.1 | 26.9 | 27.2 | 38.5 | 26.8 | 72.2 | 53.8 | 54.4 | 79 | 3.38 | 3.15 | 3 | 6 | 0.033 | 6.8 | 6.1 | 90.4 | 1.4775 | 50.4 | 87.3 | 0.2989 | 0.0592 | 13.13 | 12.08 | 13.15 | 1.07 | 1.341 | 1.737 | 8.311 | 3.3975 | 30.31 | 5.2 | 11.6 | 2021-12-31
|  |  | pH | [6 empty] | Chlorine |  |  |  | Colour | [5 empty] | Turbidity | [5 empty] | Total Dissolved Solids |  |  |  |  | Conductivity |  |  |  |  | Hardness |  | Alkalinity |  | Aluminum | Temperature |  | CI Used | Cl Demand | UVT |  | UVA |  | Flows withinin plant |  |  |  | Flows from plant |  |  | Chemical Dosages
|  |  | Raw | PTC | PTC (OL) | SWC | Filter | Finish (OL) | Finish | Free | Total | Sample | Analyzer | Raw A | Raw T | SWC A | Filter A | Finish A | Finish T | Raw | Raw (OL) | SWC | Filter | Finish | Finish (OL) | Raw | PTC | SWC | Filter | Finish | Raw | PTC | SWC | Filter | Finish | Raw | Finish | Raw | Finish | Finish (Free) | Raw | Finish |  |  | Raw | Filter | Raw | Filter | Raw | Finish | Filter | Backwash | Bishop's | Botwood | GFW | Chlorine | Alum | Lime (Pre) | Lime (Post)
January 2021 Average |  |  | 6.06 | 5.24 | 5.26 | 5.36 | 5.41 | 7.12 | 7.19 | 1.62 | 1.8 | 1.97 | 2 | 46.69 | 39.46 | 15.04 | 2.73 | 1.67 | #DIV/0! | 0.45 | 0.38 | 1.05 | 0.13 | 0.49 | 0.54 | 13.88 | 35.36 | 27.92 | 28.41 | 38.05 | 27.75 | 70.72 | 55.85 | 57.52 | 76.11 | 3.06 | 3.33 | 3.03 | 5.9 | 0.04 | 7.04 | 5.86 | 77.36 | 0.67 | 54.31 | 90.8 | 0.26 | 0.04 | 13.94 | 12.88 | 13.71 | 0.97 | 1.57 | 2.74 | 8.27 | 2.73 | 29.95 | 4.8 | 9.56
February 2021 Average |  |  | 6.07 | 5.27 | 5.3 | 5.34 | 5.38 | 7.03 | 7.14 | 1.59 | 1.8 | 1.99 | 2.03 | 44.92 | 37.67 | 19.08 | 2.94 | 4.2 | #DIV/0! | 0.38 | 0.31 | 1.68 | 0.21 | 0.65 | 0.68 | 14.41 | 35.92 | 28.92 | 29.19 | 40.39 | 28.83 | 71.83 | 57.83 | 58.37 | 80.78 | 3.13 | 3.32 | 3.03 | 5.93 | 0.03 | 6.55 | 5.51 | 79.45 | 0.73 | 53.56 | 89.99 | 0.27 | 0.05 | 13.59 | 12.61 | 13.42 | 1.06 | 1.58 | 2.77 | 7.33 | 2.88 | 29.98 | 4.61 | 10.52
March 2021 Average |  |  | 5.99 | 5.24 | 5.25 | 5.31 | 5.37 | 7.04 | 7.11 | 1.62 | 1.83 | 2 | 2.03 | 49.07 | 42.44 | 22.41 | 2.96 | 1.33 | #DIV/0! | 0.35 | 0.26 | 1.6 | 0.27 | 0.72 | 0.78 | 15.2 | 35.3 | 28.2 | 28.85 | 40.87 | 30.41 | 70.56 | 56.35 | 57.7 | 81.73 | 3 | 3.37 | 3.03 | 5.91 | 0.04 | 7.37 | 5.01 | 86.9 | 0.79 | 54.29 | 89.34 | 0.27 | 0.05 | 14.98 | 14.09 | 14.95 | 0.96 | 1.61 | 2.81 | 9.16 | 2.81 | 30.15 | 3.93 | 11.75
April 2021 Average |  |  | 5.98 | 5.06 | 5.03 | 5.18 | 5.24 | 7.15 | 7.24 | 1.6 | 1.86 | 2.04 | 2.09 | 63.56 | 55.96 | 24.6 | 2.08 | 1 | #DIV/0! | 0.56 | 0.43 | 1.52 | 0.16 | 0.61 | 0.61 | 10.9 | 29.85 | 23.97 | 24.09 | 33.83 | 21.64 | 59.62 | 47.94 | 48.18 | 67.64 | 2.88 | 3.32 | 3.03 | 5.94 | 0.04 | 8.84 | 5.72 | 84.43 | 0.91 | 49.66 | 88.24 | 0.31 | 0.05 | 13.64 | 12.67 | 13.49 | 0.95 | 1.48 | 2.77 | 7.78 | 3.02 | 29.68 | 3.62 | 11.47
May 2021 Average |  |  | 6.03 | 5.05 | 5.05 | 5.13 | 5.16 | 6.99 | 7.04 | 1.65 | 1.83 | 2.12 | 2.24 | 62.5 | 55.42 | 25.77 | 2.17 | 1 | #DIV/0! | 0.63 | 0.5 | 1.56 | 0.1 | 0.76 | 0.74 | 9.53 | 30.2 | 25.7 | 25.66 | 32.12 | 19.07 | 60.39 | 51.39 | 51.32 | 64.25 | 3.4 | 3.22 | 3.02 | 5.89 | 0.03 | 13.32 | 9 | 89.13 | 0.94 | 50.07 | 86.48 | 0.29 | 0.06 | 13.43 | 12.46 | 13.4 | 0.94 | 1.46 | 2.72 | 7.68 | 3.25 | 30.82 | 4.36 | 10.88
June 2021 Average |  |  | 6.24 | 5.1 | 5.08 | 5.12 | 5.18 | 7.24 | 7.24 | 1.71 | 1.94 | 2.2 | 2.81 | 52.08 | 44.85 | 16.31 | 2.17 | 1 | #DIV/0! | 0.57 | 0.5 | 1.07 | 0.1 | 0.44 | 0.35 | 12.69 | 33.42 | 31.45 | 31.09 | 39.92 | 25.37 | 67.22 | 62.9 | 62.38 | 79.84 | 3.11 | 3.03 | 3.08 | 5.96 | 0.1 | 18.5 | 14.68 | 111.65 | 0.55 | 56.17 | 89.42 | 0.25 | 0.05 | 16.16 | 15 | 15.96 | 1.03 | 1.57 | 2.81 | 10.11 | 3.37 | 29.73 | 5.01 | 11.23
July 2021 Average |  |  | 6.23 | 5.04 | 5.07 | 5.05 | 5.1 | 6.93 | 7.02 | 1.82 | 2.05 | 2.18 | 2.32 | 43.89 | 36.67 | 16.41 | 1.43 | #DIV/0! | #DIV/0! | 1.04 | 0.91 | 0.91 | 0.09 | 0.43 | 0.41 | 13.8 | 35.88 | 34.12 | 34.19 | 42.93 | 27.55 | 71.76 | 68.24 | 68.38 | 84.39 | 3.01 | 3.54 | 3.04 | 5.9 | 0.09 | 19.49 | 17.41 | 114.42 | 1.17 | 60.26 | 89.58 | 0.22 | 0.05 | 16.03 | 15 | 16.04 | 1.09 | 1.46 | 2.74 | 9.53 | 3.48 | 29.89 | 5.27 | 10.17
August 2021 Average |  |  | 6.33 | 5.03 | 5.05 | 5.05 | 5.11 | 6.89 | 7 | 1.68 | 1.85 | 2.12 | 2.24 | 36.92 | 30.12 | 15.38 | 1.58 | 1 | #DIV/0! | 0.54 | 0.46 | 1.06 | 0.12 | 0.3 | 0.28 | 14.46 | 36.33 | 34.97 | 34.58 | 43.98 | 28.92 | 72.67 | 69.83 | 69.15 | 87.97 | 3.16 | 3.27 | 3.03 | 5.95 | 0.08 | 20.62 | 19.37 | 98.77 | 1.02 | 64.61 | 90.25 | 0.19 | 0.04 | 15.09 | 14.01 | 14.99 | 1.06 | 1.48 | 2.51 | 10.13 | 3.21 | 30.68 | 5.25 | 11
September 2021 Average |  |  | 6.28 | 5.12 | 5.11 | 5.14 | 5.19 | 7.21 | 7.35 | 1.71 | 1.87 | 2.07 | 1.94 | 39.16 | 32.16 | 14.52 | 3.63 | 2.25 | #DIV/0! | 0.61 | 0.47 | 1.02 | 0.11 | 0.3 | 0.24 | 14.95 | 37.66 | 35.31 | 35.63 | 49.25 | 29.9 | 75.41 | 70.86 | 71.26 | 98.5 | 4.31 | 4.71 | 3.02 | 6.42 | 0.1 | 17.18 | 17.32 | 92.46 | 1.35 | 61.61 | 90.05 | 0.21 | 0.05 | 13.8 | 12.62 | 13.63 | 1.1 | 1.69 | 2.15 | 8.3 | 3.35 | 30.75 | 4.35 | 10.22
October 2021 Average |  |  | 6.36 | 5.18 | 5.15 | 5.2 | 5.25 | 7.28 | 7.37 | 1.7 | 1.89 | 2.01 | 2.02 | 39.85 | 32.73 | 17.73 | 1.67 | 1 | #DIV/0! | 0.49 | 0.38 | 1.14 | 0.15 | 0.4 | 0.33 | 13.61 | 35.97 | 31.18 | 31.62 | 45.77 | 27.61 | 71.93 | 62.35 | 63.25 | 91.55 | 3.74 | 5.7 | 3.01 | 5.96 | 0.17 | 12.79 | 14.01 | 84.85 | 1.18 | 59.35 | 90.77 | 0.22 | 0.04 | 13.14 | 12 | 12.96 | 1.04 | 1.64 | 1.87 | 7.97 | 3.21 | 30.48 | 4.16 | 10.26
November 2021 Average |  |  | 6.3 | 5.14 | 5.13 | 5.19 | 5.26 | 7.12 | 7.29 | 1.61 | 1.79 | 2.09 | 2.09 | 48.69 | 40.92 | 33.54 | 3.63 | 1.6 | 1 | 0.59 | 0.43 | 1.46 | 0.23 | 0.68 | 0.53 | 13.38 | 34.88 | 28.17 | 28.77 | 42.51 | 26.75 | 69.79 | 56.35 | 57.55 | 84.64 | 3.24 | 3.26 | 3.02 | 5.89 | 0.21 | 9.75 | 10.55 | 89.15 | 1.23 | 55.52 | 88.25 | 0.26 | 0.05 | 13.27 | 12.2 | 13.09 | 1.03 | 1.62 | 2.1 | 8.17 | 3.32 | 30.82 | 4.57 | 10.56
December 2021 Average |  |  | 6.11 | 5.15 | 5.14 | 5.25 | 5.31 | 7.15 | 7.23 | 1.57 | 1.74 | 1.99 | 1.96 | 62.78 | 55.04 | 25.78 | 3.41 | 1.5 | 0.26 | 0.98 | 0.68 | 1.41 | 0.21 | 0.56 | 0.4 | 12.49 | 34.27 | 26.54 | 26.68 | 39.9 | 24.98 | 68.47 | 53.16 | 53.44 | 79.93 | 2.9 | 2.94 | 3.03 | 5.83 | 0.1 | 7.2 | 7.39 | 83.54 | 1.2 | 52.09 | 87.07 | 0.28 | 0.06 | 13.17 | 12.14 | 13.07 | 1.09 | 1.45 | 1.9 | 8.15 | 3.13 | 30.62 | 5.03 | 10.51
2021 Average |  |  | 6.16 | 5.13 | 5.13 | 5.19 | 5.25 | 7.1 | 7.18 | 1.66 | 1.86 | 2.07 | 2.15 | 49.22 | 41.99 | 20.57 | 2.67 | 1.84 | 0.63 | 0.6 | 0.48 | 1.29 | 0.16 | 0.53 | 0.49 | 13.28 | 34.59 | 29.71 | 29.9 | 40.8 | 26.56 | 69.2 | 59.44 | 59.88 | 81.44 | 3.13 | 3.32 | 3.03 | 5.96 | 0.09 | 12.41 | 11 | 90.77 | 0.97 | 55.97 | 89.18 | 0.25 | 0.05 | 14.17 | 13.13 | 14.05 | 1.02 | 1.55 | 2.49 | 8.54 | 3.14 | 30.3 | 4.58 | 10.69
2021 WTP Average Flow Assessment
| Month | Finish | BF | Botwood | GFW | Communuity Flow | Percent Diff (%) |  |  | Max Value | Min Value |  |  | cell# | cell# | # Days | Flow Total / Month
| January | 12.88 | 1.57 | 2.74 | 8.27 | 12.58 | 2.329% |  | Finish | 22.26 | 10.6 |  | January | 4 | 34 | 31 | 389.98
| February | 12.61 | 1.58 | 2.77 | 7.33 | 11.68 | 7.375% |  | GFW | 15.972 | 5.641 |  | February | 35 | 62 | 28 | 327.04
| March | 14.09 | 1.61 | 2.81 | 9.16 | 13.58 | 3.62% |  | Botwood | 3.1 | 1.406 |  | March | 63 | 93 | 31 | 420.98
| April | 12.67 | 1.48 | 2.77 | 7.78 | 12.03 | 5.051% |  | Bishops | 2.093 | 1.101 |  | April | 94 | 123 | 30 | 360.9
| May | 12.46 | 1.46 | 2.72 | 7.68 | 11.86 | 4.815% | [5 empty] | May | 124 | 154 | 31 | 367.66
| June | 15 | 1.57 | 2.81 | 10.11 | 14.49 | 3.4% | [5 empty] | June | 155 | 184 | 30 | 434.7
| July | 15 | 1.46 | 2.51 | 10.13 | 14.1 | 6% | [5 empty] | July | 185 | 215 | 31 | 437.1
| August | 14.01 | 1.48 | 2.74 | 9.51 | 13.73 | 1.999% | [5 empty] | August | 216 | 246 | 31 | 425.63
| September | 12.62 | 1.69 | 2.15 | 8.3 | 12.14 | 3.803% | [5 empty] | September | 247 | 276 | 30 | 364.2
| October | 12 | 1.64 | 1.87 | 7.97 | 11.48 | 4.333% | [5 empty] | October | 277 | 307 | 31 | 355.88
| November | 12.2 | 1.62 | 2.1 | 8.17 | 11.89 | 2.541% | [5 empty] | November | 308 | 337 | 30 | 356.7
| December | 12.14 | 1.45 | 1.9 | 8.15 | 11.5 | 5.272% | [5 empty] | December | 338 | 368 | 31 | 356.5
| Yr Average | 13.14 | 1.5508 | 2.4908 | 8.5467 | 12.5883 | 4.212% | [8 empty] | 365 | 4597.27
2021 WTP UV Averages
| Month | UVT RAW | UVT Filter | UVA RAW | UVA Filter |  |  | Max Value | Min Value
| January | 54.3115 | 90.8 | 0.2643 | 0.0425 |  | UVT Raw | 96 | 8
| February | 53.5583 | 89.9875 | 0.2713 | 0.0453 |  | UVT Filter | 120 | 81.6
| March | 54.5148 | 89.4222 | 0.2638 | 0.0483 |  | UVA Raw | 0.411 | 0.2061
| April | 49.252 | 88.16 | 0.3092 | 0.0547 |  | UVA Filter | 0.0882 | -0.079
| May | 50.2 | 86.5577 | 0.2858 | 0.0627
| June | 56.25 | 89.3 | 0.25 | 0.0488
| July | 60.5 | 89.69 | 0.217 | 0.0467
| August | 64.61 | 90.25 | 0.192 | 0.044
| September | 61.61 | 90.13 | 0.214 | 0.0451
| October | 59.35 | 90.72 | 0.22 | 0.0424
| November | 55.52 | 88.25 | 0.26 | 0.0542
| December | 52.09 | 87.07 | 0.284 | 0.0602
| Yr Average | 55.9806 | 89.1948 | 0.25262 | 0.049575
2021 WTP Averages
| Month | Temp. (RAW) | Temp. (Finish) | Alkalinity (RAW) | Alkalinity (Finish) | Aluminum (Finish) | Hardness (RAW) | Hardness (Finish) |  |  | Max Value | Min Value
| January | 7.04 | 5.86 | 3.03 | 5.9 | 0.037 | 3.06 | 3.33 |  | Temp. Raw | 23.5 | 3
| February | 6.55 | 5.49 | 3.03 | 5.93 | 0.031 | 3.13 | 3.32 |  | Temp. Finish | 21.7 | 1
| March | 7.42 | 5.01 | 3.03 | 5.91 | 0.042 | 3 | 3.37 |  | Alkalinity Raw | 5 | 2.8
| April | 9.02 | 5.84 | 3.03 | 5.94 | 0.038 | 2.88 | 3.32 |  | Alkalinity Finish | 17.7 | 3.36
| May | 13.48 | 9.13 | 3.02 | 5.9 | 0.034 | 3.41 | 3.22 |  | Hardness Raw | 7.3 | 2.13
| June | 18.6 | 14.9 | 3.08 | 5.96 | 0.095 | 3.1 | 3.03 |  | Hardness Finish | 7.61 | 1.59
| July | 19.5 | 17.42 | 3.04 | 5.9 | 0.09 | 3.01 | 3.55
| August | 20.62 | 19.37 | 3.03 | 5.95 | 0.081 | 3.16 | 3.27
| September | 17.18 | 17.28 | 3.02 | 6.4 | 0.102 | 4.22 | 4.87
| October | 12.79 | 14.01 | 3.01 | 5.96 | 0.175 | 4.05 | 5.32
| November | 9.75 | 10.55 | 3.02 | 5.89 | 0.213 | 3.24 | 3.26
| December | 7.2 | 7.39 | 3.03 | 5.83 | 0.103 | 2.9 | 2.94
| Average | 12.4292 | 11.0208 | 3.0308 | 5.9558 | 0.08675 | 3.2633 | 3.5667
2021 WTP Averages
| Month | TDS (RAW) | TDS (Finish) | Conduct. (RAW) | Conduct. (Finish) |  |  | Max Value | Min Value |  |  |  | cell# | cell# | # Days
| January | 13.88 | 38.05 | 27.75 | 76.11 |  | TDS (RAW) | 17 | 7.9 |  |  | January | 4 | 34 | 31
| February | 14.41 | 40.39 | 28.83 | 80.78 |  | TDS (Finish) | 53.7 | 26.8 |  |  | February | 35 | 62 | 28
| March | 15.2 | 40.87 | 30.41 | 81.73 |  | Conduct. (RAW) | 37.4 | 15.8 |  |  | March | 63 | 93 | 31
| April | 10.9 | 33.83 | 21.64 | 67.64 |  | Conduct. (Finish) | 107.4 | 47 |  |  | April | 94 | 123 | 30
| May | 9.53 | 32.12 | 19.07 | 64.25 | [6 empty] | May | 124 | 154 | 31
| June | 12.69 | 39.92 | 25.37 | 79.84 | [6 empty] | June | 155 | 184 | 30
| July | 13.8 | 42.93 | 27.55 | 84.39 | [6 empty] | July | 185 | 215 | 31
| August | 14.46 | 43.98 | 28.92 | 87.97 | [6 empty] | August | 216 | 246 | 31
| September | 14.95 | 49.25 | 29.9 | 98.5 | [6 empty] | September | 247 | 276 | 30
| October | 13.61 | 45.77 | 27.61 | 91.55 | [6 empty] | October | 277 | 307 | 31
| November | 13.38 | 42.51 | 26.75 | 84.64 | [6 empty] | November | 308 | 337 | 30
| December | 12.45 | 39.9 | 24.98 | 79.93 | [6 empty] | December | 338 | 368 | 31
| Yr Average | 13.2717 | 40.7933 | 26.565 | 81.4442 | [9 empty] | 365
| 2021 WTP Averages | [8 empty] | 2021 WTP Averages
| Month | Color (Raw/Actual) | Color (Raw/True) |  |  | Max Value | Min Value |  |  | MONTHLY AVERAGES | Filter Turbidity | Finish Turbidity | Raw Turbidity
| January | 46.69 | 39.46 |  | Color (Raw/Actual) | 85 | 30 |  |  | January | 0.131 | 0.493 | 0.453 |  |  | >= 1 NTU Finish | 11
| February | 44.92 | 37.67 |  | Color (Raw/True) | 74 | 24 |  |  | February | 0.21 | 0.645 | 0.377
| March | 49.07 | 42.44 | [6 empty] | March | 0.274 | 0.724 | 0.351
| April | 63.56 | 55.96 | [6 empty] | April | 0.16 | 0.615 | 0.557
| May | 62.5 | 55.42 | [6 empty] | May | 0.101 | 0.759 | 0.625
| June | 52.08 | 44.85 | [6 empty] | June | 0.101 | 0.44 | 0.574
| July | 43.89 | 36.67 | [6 empty] | July | 0.09 | 0.43 | 1.04
| August | 36.92 | 30.12 | [6 empty] | August | 0.116 | 0.295 | 0.544
| September | 39.16 | 32.16 | [6 empty] | September | 0.114 | 0.297 | 0.609
| October | 39.85 | 32.73 | [6 empty] | October | 0.149 | 0.395 | 0.494
| November | 48.69 | 40.92 | [6 empty] | November | 0.226 | 0.68 | 0.588
| December | 62.78 | 55.04 | [6 empty] | December | 0.211 | 0.56 | 0.979
| Average | 49.1758 | 41.9533 | [6 empty] | Average | 0.15692 | 0.52775 | 0.59925
2021 Free Chlorine Assessment
| Month | Lab Free CL2 | Analyzer (Sample) | % Diff. | Residual Loss |  |  | Max Value | Min Value |  |  |  | cell# | cell# | # Days
| January | 1.62 | 2 | 19% | 0.38 |  | Free Chlorine | 2.2 | 1.25 |  |  | January | 4 | 34 | 31
| February | 1.59 | 2.03 | 21.67% | 0.44 |  | Analyzer Chlorine | 2.56 | 1.71 |  |  | February | 35 | 62 | 28
| March | 1.62 | 2.03 | 20.2% | 0.41 | [6 empty] | March | 63 | 93 | 31
| April | 1.6 | 2.09 | 23.44% | 0.49 | [6 empty] | April | 94 | 123 | 30
| May | 1.65 | 2.24 | 26.34% | 0.59 | [6 empty] | May | 124 | 154 | 31
| June | 1.71 | 2.81 | 39.15% | 1.1 | [6 empty] | June | 155 | 184 | 30
| July | 1.82 | 2.32 | 21.55% | 0.5 | [6 empty] | July | 185 | 215 | 31
| August | 1.68 | 2.24 | 25% | 0.56 | [6 empty] | August | 216 | 246 | 31
| September | 1.71 | 1.94 | 11.86% | 0.23 | [6 empty] | September | 247 | 276 | 30
| October | 1.7 | 2.02 | 15.84% | 0.32 | [6 empty] | October | 277 | 307 | 31
| November | 1.61 | 2.09 | 22.97% | 0.48 | [6 empty] | November | 308 | 337 | 30
| December | 1.57 | 1.96 | 19.9% | 0.39 | [6 empty] | December | 338 | 368 | 31
| Average | 1.6567 | 2.1475 | 22.86% | 0.49083 | [9 empty] | 365
*analyzer replaced in September 2021 as other one not operating
properly.

## 2020
Note: The password to unlock the sheets is "WTPLAB". Don't unlock any of them unless you plan on making permanent changes.
|  |  | pH | [6 empty] | Chlorine |  |  |  | Colour | [5 empty] | Turbidity | [5 empty] | Total Dissolved Solids |  |  |  |  | Conductivity |  |  |  |  | Hardness |  | Alkalinity |  | Aluminum | Temperature |  | Cl Demand | UVT |  | UVA |  | Flows withinin plant |  |  |  | Flows from plant |  |  | Chemical Dosages |  |  |  |  | Dennis Penney
Date | Shortcut | Start Time | Raw | PTC | PTC (OL) | SWC | Filter | Finish (OL) | Finish | Free | Total | Sample | Analyzer | Raw A | Raw T | SWC A | Filter A | Finish A | Finish T | Raw | Raw (OL) | SWC | Filter | Finish | Finish (OL) | Raw | PTC | SWC | Filter | Finish | Raw | PTC | SWC | Filter | Finish | Raw | Finish | Raw | Finish | Finish (Free) | Raw | Finish |  | Raw | Filter | Raw | Filter | Raw | Finish | Filter | Backwash | Bishop's | Botwood | GFW | Chlorine | Alum | Lime (Pre) | Lime (Post) | Date | Jerry Loveless
2020-01-01 | Click Here | #REF! | 6.16 | 5.11 | 5.2 | 5.26 | 5.3 | 6.71 | 7.14 | 1.96 | 2.14 | 2.2 | 2.32 | 50 | 44 | 15 | 0 | 0 | 0 | 0.281 | 0.326 | 0.633 | 0.104 | 0.442 | 0.56 | 12.5 | 35.2 | 26.7 | 27.1 | 34.5 | 25 | 70.4 | 53.4 | 54.2 | 69 | 3.15 | 4.03 | 3 | 5.8 | 0.088 | 6.6 | 0 | 0.43103 | 55.3 | 91.5 | 0.2569 | 0.0386 | 12.99 | 12.7 | 12.7 | 0 | 1.575 | 2.504 | 7.854 | 2.601 | 28.52 | 5.6 | 9.9 | 2020-01-01 | Nolan Simms
2020-01-02 | Click Here |  | 6.2 | 5.22 | 5.35 | 5.28 | 5.3 | 6.61 | 6.7 | 1.9 | 2.06 | 2.17 | 2.24 | 50 | 43 | 13 | 0 | 0 | 0 | 0.283 | 0.327 | 0.611 | 0.094 | 0.472 | 0.581 | 12.9 | 31.4 | 26.6 | 27.4 | 34.6 | 25.8 | 62.8 | 53.2 | 54.8 | 69.2 | 3.21 | 4.03 | 3.1 | 5.9 | 0.066 | 6.9 | 4.4 | 0.79285 | 55.6 | 91.7 | 0.2561 | 0.0383 | 13.6 | 12.63 | 13.61 | 0.98 | 1.575 | 2.504 | 8.551 | 2.9328 | 27.81 | 5.6 | 10.1 | 2020-01-02
2020-01-03 | Click Here |  | 5.85 | 5.29 | 5.25 | 5.32 | 5.36 | 6.94 | 6.87 | 1.97 | 2.14 | 2.17 | 2.29 | 46 | 39 | 21 | 0 | 0 | 0 | 0.427 | 0.299 | 1.16 | 0.145 | 0.423 | 0.427 | 13.3 | 29.8 | 26.7 | 57.4 | 36.5 | 26.6 | 59.6 | 53.4 | 54.8 | 73 | 3.35 | 3.55 | 2.6 | 6.1 | 0.009 | 7.1 | 4.4 | 0.78429 | 56.1 | 95.2 | 0.251 | 0.0214 | 14.56 | 13.49 | 14.48 | 0.99 | 0 | 0 | 0 | 2.8943 | 31.45 | 5.6 | 10.3 | 2020-01-03
2020-01-04 | Click Here |  | 5.89 | 5.31 | 5.27 | 5.34 | 5.36 | 7.08 | 7.01 | 1.91 | 2.11 | 2.12 | 2.18 | 45 | 38 | 20 | 0 | 0 | 0 | 0.419 | 0.294 | 1.04 | 0.141 | 0.589 | 0.603 | 13.2 | 29.9 | 27.1 | 27.6 | 37.1 | 26.4 | 59.8 | 54.2 | 55.2 | 74.2 | 3.2 | 3.5 | 2.8 | 5.9 | 0.012 | 7.1 | 4.4 |  | 55.8 | 95.3 | 0.2521 | 0.0211 | 14.17 | 13.2 | 14.16 | 0.96 | 0 | 0 | 0 |  | 30.98 | 5.6 | 10.3 | 2020-01-04 | Continuous
2020-01-05 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-01-05 | Grab
2020-01-06 | Click Here |  | 6.14 | 5.24 | 5.18 | 5.26 | 5.27 | 6.4 | 6.84 | 1.8 | 1.99 | 2.04 | 2.08 | 47 | 40 | 18 | 1 | 0 | 0 | 0.301 | 0.273 | 0.084 | 0.113 | 0.519 | 0.612 | 13.2 | 32.7 | 26.4 | 27.1 | 36.2 | 26.4 | 65.4 | 52.8 | 54.2 | 72.4 | 3.17 | 3.65 | 3 | 5.7 | 0.022 | 6.9 | 4.2 | 0.18786 | 55.6 | 91.9 | 0.2523 | 0.0381 | 13.66 | 12.49 | 13.48 | 0.99 | 0 | 0 | 0 | 2.1679 | 31.29 | 5.6 | 10.3 | 2020-01-06 | ^ Stuff for form dropdown menus
2020-01-07 | Click Here |  | 6.57 | 5.35 | 5.17 | 5.36 | 5.36 | 6.31 | 6.67 | 1.76 | 1.94 | 2.09 | 2.01 | 47 | 43 | 19 | 2 | 0 | 0 | 0.268 | 0.276 | 1.16 | 0.116 | 0.041 | 0.517 | 12.7 | 32.2 | 27.1 | 27 | 34.1 | 25.4 | 64.4 | 54.2 | 54 | 68.2 | 3.2 | 3.61 | 3 | 5.6 | 0.048 | 5.9 | 4.1 | 0.44607 | 53.7 | 90.1 | 0.2699 | 0.0449 | 14.12 | 12.99 | 13.95 | 0.96 | 1.575 | 2.504 | 8.911 | 2.4661 | 30.73 | 5.6 | 10.5 | 2020-01-07
2020-01-08 | Click Here |  | 6 | 5.23 | 5.13 | 5.3 | 5.34 | 6.69 | 6.61 | 1.94 | 2.15 | 2.2 | 2.19 | 43 | 36 | 15 | 0 | 0 | 0 | 0.402 | 0.278 | 1.17 | 0.137 | 2.3 | 1.332 | 13.2 | 34.7 | 27 | 27.4 | 34.5 | 26.4 | 69.4 | 54 | 54.8 | 69 | 3.47 | 2.24 | 0 | 0 | 0.013 | 7.1 | 4.2 | 0.67735 | 55.7 | 89.7 | 0.254 | 0.0468 | 14.08 | 13.07 | 14 | 0.93 | 0 | 0 | 0 | 2.7573 | 31.22 | 5.6 | 10.8 | 2020-01-08
2020-01-09 | Click Here |  | 6.03 | 5.31 | 5.34 | 5.32 | 5.33 | 6.62 | 6.7 | 2 | 2.09 | 2.2 | 2.02 | 42 | 35 | 14 | 0 | 0 | 0 | 0.397 | 0.278 | 1.04 | 0.116 | 0.658 | 0.641 | 13.3 | 34.1 | 27.4 | 28.1 | 34.4 | 26.6 | 68.2 | 54.8 | 56.2 | 68.8 | 3.4 | 2.96 | 0 | 0 | 0.012 | 7.1 | 4.2 | 0.69373 | 56.1 | 90.2 | 0.2533 | 0.0454 | 14.26 | 13.21 | 14.16 | 0.95 | 0 | 0 | 0 | 2.8037 | 30.98 | 5.6 | 10.8 | 2020-01-09
2020-01-10 | Click Here |  | 6.07 | 5.25 | 5.26 | 5.34 | 5.36 | 6.74 | 6.63 | 1.97 | 2.12 | 2.19 | 2.1 | 49 | 42 | 15 | 1 | 0 | 0 | 0.317 | 0.272 | 0.891 | 0.104 | 0.547 | 0.672 | 13.3 | 32.2 | 27.3 | 27.5 | 33.6 | 26.6 | 64.4 | 54.6 | 55 | 67.2 | 3.31 | 3.46 | 0 | 0 | 0.029 | 6.7 | 4.4 | 0.80209 | 56 | 90.5 | 0.2529 | 0.0439 | 14.61 | 13.6 | 14.57 | 0.97 | 0 | 0 | 0 | 3.0121 | 29.97 | 5.6 | 11.1 | 2020-01-10
2020-01-11 | Click Here |  | 6.02 | 5.31 | 5.24 | 5.36 | 5.4 | 6.79 | 6.7 | 1.94 | 2.09 | 2.07 | 2.13 | 47 | 40 | 13 | 0 | 0 | 0 | 0.274 | 0.261 | 0.914 | 0.109 | 0.476 | 0.71 | 13 | 32.6 | 26.9 | 27.4 | 34.2 | 26 | 65.2 | 53.8 | 54.8 | 68.4 | 3.08 | 3.53 | 0 | 0 | 0.097 | 6.6 | 4.4 | 0.77083 | 56.4 | 90.9 | 0.2509 | 0.0404 | 14.66 | 13.57 | 14.56 | 0.99 | 1.575 | 2.504 | 9.491 | 2.9508 | 30.67 | 5.6 | 11.1 | 2020-01-11
2020-01-12 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-01-12
2020-01-13 | Click Here |  | 5.62 | 5.23 | 5.25 | 5.32 | 5.35 | 6.97 | 6.94 | 1.96 | 2.15 | 2.2 | 2.28 | 42 | 35 | 24 | 0 | 0 | 0 | 0.374 | 0.257 | 1.46 | 0.178 | 0.478 | 0.513 | 13.8 | 34.3 | 28.1 | 27.4 | 36.4 | 27.6 | 68.6 | 56.2 | 54.8 | 72.8 | 3.35 | 3.21 | 0 | 0 | 0.031 | 7 | 4.3 | 0.57525 | 56.7 | 91.4 | 0.2426 | 0.0387 | 15.05 | 14.01 | 14.98 | 0.97 | 0 | 0 | 0 | 2.7153 | 30.04 | 5.6 | 11.1 | 2020-01-13
2020-01-14 | Click Here |  | 5.89 | 5.29 | 5.26 | 5.33 | 5.37 | 6.95 | 6.98 | 1.98 | 2.07 | 2.2 | 2.09 | 40 | 33 | 18 | 0 | 0 | 0 | 0.374 | 0.25 | 1.38 | 0.23 | 0.632 | 0.66 | 14.1 | 35 | 28.4 | 27.5 | 36.2 | 28.2 | 70 | 56.8 | 55 | 72.4 | 3.25 | 3.55 | 0 | 0 | 0 | 7.2 | 4.2 | 0.81091 | 56.8 | 91.2 | 0.2424 | 0.0395 | 15.26 | 14.2 | 15.19 | 0.99 | 0 | 0 | 0 | 2.9609 | 31.45 | 5.6 | 11.1 | 2020-01-14
2020-01-15 | Click Here |  | 5.95 | 5.27 | 5.31 | 5.34 | 5.41 | 7.04 | 6.97 | 1.91 | 2.11 | 2.19 | 1.9 | 42 | 34 | 19 | 0 | 0 | 0 | 0.392 | 0.294 | 1.51 | 0.117 | 0.547 | 0.655 | 13.7 | 34.7 | 28.1 | 27.5 | 36.2 | 27.4 | 69.4 | 56.2 | 55 | 72.4 | 3.25 | 3.73 | 0 | 0 | 0.126 | 7.1 | 4.5 | 0.85309 | 56.1 | 89.5 | 0.2511 | 0.0482 | 14.966 | 13.705 | 14.671 | 0.966 | 0 | 0 | 0 | 2.9231 | 31.3 | 5.6 | 11.1 | 2020-01-15
2020-01-16 | Click Here |  | 6.3 | 5.36 | 5.32 | 5.6 | 5.68 | 7.47 | 7.03 | 1.84 | 2.07 | 1.94 | 1.96 | 34 | 22 | 19 | 0 | 0 | 0 | 0.471 | 0.086 | 1.36 | 0.196 | 0.371 | 0.423 | 13.6 | 33.5 | 27.9 | 27.4 | 36.4 | 27.2 | 67 | 55.8 | 54.8 | 72.8 | 3.03 | 3.8 | 0 | 0 | 0.059 | 6.8 | 4.5 | 0.87521 | 55.6 | 90 | 0.2543 | 0.0457 | 14.92 | 14.08 | 15.02 | 0.94 | 0 | 0 | 0 | 2.9152 | 29.67 | 5.6 | 11.1 | 2020-01-16
2020-01-17 | Click Here |  | 6.17 | 5.22 | 5.31 | 5.31 | 5.34 | 6.68 | 7.49 | 1.71 | 1.93 | 1.89 | 1.87 | 35 | 24 | 20 | 1 | 0 | 0 | 0.468 | 0.053 | 1.41 | 0.183 | 0.386 | 0.454 | 13.9 | 34.1 | 28.3 | 27.7 | 38 | 27.8 | 68.2 | 56.6 | 55.4 | 76 | 3.09 | 3.91 | 0 | 0 | 0.066 | 7.2 | 4.3 | 0.97622 | 55.8 | 89.9 | 0.2541 | 0.0459 | 14.33 | 13.32 | 14.27 | 0.95 | 0 | 0 | 0 | 3.0062 | 29.32 | 5.6 | 11.1 | 2020-01-17
2020-01-18 | Click Here |  | 6.21 | 5.24 | 5.3 | 5.35 | 5.33 | 6.61 | 6.87 | 1.8 | 1.96 | 2.01 | 2 | 34 | 25 | 18 | 1 | 0 | 0 | 0.452 | 0.02 | 1.08 | 0.116 | 0.399 | 0.563 | 13.4 | 34.2 | 28.1 | 27.8 | 38.3 | 26.8 | 68.4 | 56.2 | 55.6 | 76.6 | 3.03 | 4.12 | 0 | 0 | 0.055 | 7.2 | 4.3 | 0.9438 | 55.9 | 90.2 | 0.254 | 0.0456 | 15.17 | 14.27 | 15.21 | 0.94 | 0 | 0 | 0 | 2.9238 | 30.57 | 5.6 | 11.1 | 2020-01-18
2020-01-19 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.93732 | 0 | 0 | 0 | 0 | 15.015 | 13.955 | 14.914 | 0.959 | 0 | 0 | 0 | 2.8873 | 0 | 5.6 | 11.3 | 2020-01-19
2020-01-20 | Click Here |  | 6.13 | 5.27 | 5.3 | 5.39 | 5.37 | 6.77 | 6.94 | 1.7 | 1.98 | 2.01 | 1.82 | 37 | 30 | 19 | 1 | 0 | 0 | 0.409 | 0.02 | 1.12 | 0.124 | 0.374 | 0.509 | 13.1 | 34.4 | 27.8 | 27.5 | 38 | 26.2 | 68.8 | 55.6 | 55 | 76 | 3.02 | 3.96 | 0 | 0 | 0.047 | 7.1 | 4.3 | 0.91633 | 56.1 | 90.4 | 0.2531 | 0.0438 | 15.659 | 14.685 | 15.655 | 0.97 | 0 | 0 | 0 | 2.8263 | 30.92 | 5.6 | 11.3 | 2020-01-20
2020-01-21 | Click Here |  | 6.07 | 5.27 | 5.31 | 5.36 | 5.4 | 6.77 | 6.76 | 1.96 | 2.13 | 2.2 | 2.12 | 33 | 24 | 18 | 0 | 0 | 0 | 0.403 | 0.079 | 1.18 | 0.198 | 0.511 | 0.488 | 14 | 34.3 | 29 | 27.5 | 35.6 | 28 | 68.6 | 58 | 55 | 71.2 | 3.01 | 3.86 | 0 | 0 | 0.046 | 7 | 4.3 | 1.0434 | 58.8 | 91.9 | 0.2301 | 0.0364 | 14.04 | 12.87 | 13.86 | 0.99 | 0 | 0 | 0 | 3.0334 | 31.54 | 5.6 | 11.3 | 2020-01-21
2020-01-22 | Click Here |  | 6.06 | 5.08 | 5.31 | 5.21 | 5.28 | 6.57 | 6.87 | 1.81 | 1.94 | 1.93 | 1.88 | 34 | 23 | 27 | 3 | 1 | 0 | 0.416 | 0.01 | 1.87 | 0.302 | 0.573 | 0.516 | 13.6 | 34.7 | 29.8 | 28.6 | 37.4 | 27.2 | 69.4 | 59.6 | 57.2 | 74.8 | 3.09 | 4.03 | 0 | 0 | 0.077 | 6.1 | 4.2 | 1.0065 | 58.6 | 90.5 | 0.2303 | 0.0439 | 14.86 | 13.16 | 14.15 | 0.99 | 0 | 0 | 0 | 2.9265 | 28.43 | 5.6 | 11.3 | 2020-01-22
2020-01-23 | Click Here |  | 6.14 | 5.23 | 5.21 | 5.27 | 5.29 | 6.43 | 6.91 | 1.84 | 1.99 | 1.96 | 1.9 | 33 | 25 | 21 | 1 | 0 | 0 | 0.412 | 0.06 | 1.22 | 0.133 | 0.561 | 0.557 | 14 | 31.8 | 24.6 | 26.8 | 37.3 | 28 | 63.6 | 49.2 | 53.6 | 74.6 | 2.99 | 3.89 | 0 | 0 | 0.058 | 7.1 | 4.1 | 0.98448 | 58.9 | 90.7 | 0.23 | 0.0437 | 16.21 | 14.62 | 15.57 | 0.95 | 1.575 | 2.504 | 10.541 | 2.9445 | 32.08 | 5.4 | 11.6 | 2020-01-23
2020-01-24 | Click Here |  | 5.9 | 5.21 | 5.09 | 5.24 | 5.33 | 6.82 | 6.75 | 2 | 2.14 | 2.17 | 1.94 | 36 | 29 | 11 | 0 | 0 | 0 | 0.484 | 0.025 | 0.824 | 0.197 | 0.593 | 0.441 | 13.8 | 34 | 26.4 | 26.6 | 34.2 | 27.6 | 68 | 52.8 | 53.2 | 68.4 | 3.13 | 3.64 | 0 | 0 | 0.008 | 6.2 | 4 | 0.56952 | 57.7 | 91.4 | 0.2388 | 0.0388 | 14.61 | 13.5 | 14.48 | 0.98 | 0 | 0 | 0 | 2.6695 | 29.57 | 5.4 | 11.8 | 2020-01-24
2020-01-25 | Click Here |  | 5.97 | 5.08 | 5.24 | 5.44 | 5.49 | 7.22 | 7.06 | 1.98 | 2.14 | 2.1 | 2.02 | 36 | 29 | 10 | 0 | 0 | 0 | 0.349 | 0.034 | 1.14 | 0.202 | 0.611 | 0.469 | 14.1 | 33.4 | 26.4 | 27.1 | 38.2 | 28.2 | 66.8 | 52.8 | 54.2 | 76.4 | 3.26 | 3.75 | 0 | 0 | 0.013 | 6.9 | 4 | 0.094371 | 57.4 | 91.3 | 0.2393 | 0.0391 | 14.75 | 13.71 | 14.68 | 0.97 | 0 | 0 | 0 | 2.2644 | 30.04 | 5.4 | 11.8 | 2020-01-25
2020-01-26 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-01-26
2020-01-27 | Click Here |  | 6.05 | 5.19 | 5.24 | 5.28 | 5.35 | 6.53 | 7.23 | 2.07 | 2.18 | 2.2 | 2.27 | 37 | 28 | 12 | 1 | 0 | 0 | 0.362 | 0.063 | 0.93 | 0.168 | 0.507 | 0.406 | 13.7 | 33.2 | 26.4 | 26.7 | 37.5 | 27.4 | 66.4 | 52.8 | 53.4 | 75 | 3.27 | 3.83 | 0 | 0 | 0.02 | 6 | 4 | 0.5809 | 55.9 | 90 | 0.2519 | 0.0454 | 14.583 | 13.477 | 14.583 | 0.97 | 0 | 0 | 0 | 2.7209 | 28.55 | 5.4 | 11.8 | 2020-01-27
2020-01-28 | Click Here |  | 6.05 | 5.24 | 5.15 | 5.31 | 5.29 | 6.34 | 6.58 | 1.78 | 1.97 | 2.04 | 2.18 | 36 | 29 | 13 | 1 | 0 | 0 | 0.347 | 0.091 | 0.891 | 0.143 | 0.499 | 0.524 | 13.9 | 32.3 | 26.4 | 26.8 | 36.5 | 27.8 | 64.6 | 52.8 | 53.6 | 73 | 3.14 | 3.96 | 0 | 0 | 0.037 | 6.4 | 4 | 0.55861 | 55 | 89.3 | 0.2589 | 0.049 | 14.84 | 13.74 | 14.72 | 0.98 | 1.575 | 2.504 | 9.661 | 2.7686 | 28.53 | 5.4 | 12 | 2020-01-28
2020-01-29 | Click Here |  | 5.96 | 5.26 | 5.11 | 5.33 | 5.36 | 6.9 | 6.78 | 1.88 | 1.98 | 2.03 | 2.08 | 39 | 32 | 11 | 0 | 0 | 0 | 0.347 | 0.013 | 1.01 | 0.133 | 0.463 | 0.539 | 14.5 | 32.5 | 27 | 27.3 | 37.4 | 29 | 65 | 54 | 54.6 | 74.8 | 3 | 3.31 | 0 | 0 | 0.008 | 6.9 | 4 | 0.41511 | 57.3 | 92 | 0.2418 | 0.0359 | 14.79 | 13.82 | 14.61 | 0.79 | 0 | 0 | 0 | 2.5351 | 30.51 | 5.4 | 12 | 2020-01-29
2020-01-30 | Click Here |  | 6.16 | 5.28 | 5.32 | 5.37 | 5.41 | 7.06 | 6.99 | 1.85 | 2 | 2.05 | 2.76 | 38 | 31 | 10 | 0 | 0 | 0 | 0.352 | 0.057 | 1.11 | 0.139 | 0.421 | 0.451 | 14.2 | 31.4 | 27 | 27.1 | 38.2 | 28.4 | 62.8 | 54 | 54.2 | 76.4 | 3.21 | 3.56 | 0 | 0 | 0.011 | 6.2 | 4.2 | 0.54327 | 57.4 | 92.2 | 0.2409 | 0.0348 | 14.32 | 14.03 | 14.03 | 0 | 0 | 0 | 0 | 2.2833 | 30.28 | 5.4 | 12 | 2020-01-30
2020-01-31 | Click Here |  | 6.09 | 5.22 | 5.27 | 5.32 | 5.39 | 7.01 | 6.97 | 1.51 | 1.79 | 1.85 | 1.44 | 40 | 33 | 10 | 0 | 0 | 0 | 0.304 | 0.247 | 0.677 | 0.098 | 0.316 | 0.38 | 13.9 | 32.7 | 26.8 | 27 | 38.1 | 27.8 | 65.4 | 53.6 | 54 | 76.2 | 3.11 | 3.49 | 3.2 | 5.6 | 0.013 | 6.8 | 4.1 | 0.33268 | 58.8 | 90.2 | 0.2303 | 0.448 | 15.221 | 14.125 | 15.09 | 0.965 | 0 | 0 | 0 | 1.8427 | 30.87 | 5.4 | 12 | 2020-01-31
2020-02-01 | Click Here |  | 6.07 | 5.19 | 5.25 | 5.37 | 5.41 | 7.12 | 7.09 | 1.71 | 2.06 | 1.9 | 1.47 | 37 | 30 | 14 | 0 | 0 | 0 | 0.367 | 0.245 | 0.741 | 0.012 | 0.301 | 0.366 | 14.6 | 33.4 | 26.9 | 27.2 | 38.8 | 29.2 | 66.8 | 53.8 | 54.4 | 77.6 | 3.04 | 3.81 | 3.2 | 5.9 | 0.019 | 7 | 4.2 | 0.86944 | 57.6 | 90.3 | 0.239 | 0.0443 | 14.35 | 13.45 | 14.29 | 0.84 | 1.575 | 2.504 | 9.371 | 2.6794 | 30.65 | 5.4 | 12 | 2020-02-01
2020-02-02 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-02-02
2020-02-03 | Click Here |  | 5.91 | 5.26 | 5.26 | 5.39 | 5.44 | 6.98 | 7.14 | 1.73 | 1.89 | 1.91 | 2.1 | 38 | 31 | 12 | 0 | 0 | 0 | 0.347 | 0.253 | 0.852 | 0.212 | 0.687 | 0.785 | 14.4 | 32.5 | 27.1 | 27.7 | 38.4 | 28.8 | 65 | 54.2 | 55.4 | 76.8 | 3.16 | 3.67 | 3.3 | 6.1 | 0.021 | 6.1 | 4.2 | 0.79575 | 57.3 | 91.7 | 0.2418 | 0.0376 | 15.14 | 13.44 | 15.27 | 1.83 | 1.575 | 2.504 | 7.854 | 2.7558 | 31.45 | 5.4 | 12 | 2020-02-03
2020-02-04 | Click Here |  | 6.01 | 5.21 | 5.27 | 5.42 | 5.44 | 7.19 | 7.21 | 1.74 | 1.88 | 2 | 2.02 | 44 | 37 | 15 | 0 | 0 | 0 | 0.348 | 0.246 | 1.09 | 0.131 | 0.403 | 0.378 | 14.9 | 33 | 27.1 | 27.2 | 39.4 | 29.8 | 66 | 54.2 | 54.4 | 78.8 | 3.23 | 3.36 | 3.6 | 6.4 | 0.011 | 6.9 | 4.4 | 0.47806 | 58 | 91.6 | 0.2364 | 0.0377 | 14.44 | 14.14 | 14.14 | 0 | 1.575 | 2.504 | 7.854 | 2.4781 | 30.51 | 5.4 | 12 | 2020-02-04
2020-02-05 | Click Here |  | 6.01 | 5.3 | 5.28 | 5.36 | 5.4 | 7 | 7.07 | 1.84 | 2.01 | 1.99 | 2.01 | 36 | 28 | 14 | 0 | 0 | 0 | 0.371 | 0.24 | 0.968 | 0.107 | 0.396 | 0.407 | 14.5 | 33.2 | 27.1 | 27.6 | 38.8 | 29 | 66.4 | 54.2 | 55.2 | 77.6 | 3.18 | 3.7 | 3.2 | 5.9 | 0.031 | 5.9 | 3.8 | 0.88872 | 58.4 | 91.4 | 0.2333 | 0.0388 | 14.129 | 11.983 | 13.846 | 1.863 | 0 | 0 | 0 | 2.8487 | 30.27 | 5.4 | 12 | 2020-02-05
2020-02-06 | Click Here |  | 6.01 | 5.29 | 5.24 | 5.33 | 5.37 | 6.95 | 7.06 | 1.8 | 1.94 | 2.01 | 1.97 | 39 | 33 | 17 | 1 | 0 | 0 | 0.296 | 0.24 | 0.747 | 0.137 | 0.331 | 0.437 | 15.1 | 33.4 | 27.3 | 27.9 | 38.5 | 30.2 | 66.8 | 54.6 | 55.8 | 77 | 2.97 | 3.64 | 2.9 | 5.7 | 0.034 | 6.9 | 4.1 | 0.71417 | 58.6 | 90 | 0.2319 | 0.0441 | 14.83 | 13.85 | 14.79 | 0.94 | 1.575 | 2.504 | 7.854 | 2.6742 | 30.29 | 5.4 | 12 | 2020-02-06
2020-02-07 | Click Here |  | 6.21 | 5.3 | 5.28 | 5.39 | 5.43 | 6.81 | 7.09 | 1.9 | 2.1 | 2.13 | 2.16 | 38 | 31 | 15 | 0 | 0 | 0 | 0.284 | 0.227 | 0.701 | 0.116 | 0.363 | 0.441 | 15.6 | 32.7 | 27.1 | 27.8 | 38.7 | 31.2 | 65.4 | 54.2 | 55.6 | 77.4 | 3.01 | 3.89 | 3 | 5.5 | 0.029 | 7.3 | 4 | 0.74147 | 58.8 | 90.4 | 0.2316 | 0.0438 | 14.48 | 13.51 | 14.5 | 0.99 | 1.575 | 2.504 | 7.854 | 2.7415 | 27.11 | 5.4 | 12 | 2020-02-07
2020-02-08 | Click Here |  | 6.07 | 5.16 | 5.29 | 5.32 | 5.34 | 6.42 | 6.9 | 1.83 | 1.99 | 2 | 2.02 | 39 | 30 | 12 | 0 | 0 | 0 | 0.316 | 0.257 | 0.689 | 0.106 | 0.338 | 0.417 | 15.9 | 33.2 | 27.2 | 27.8 | 38.6 | 31.8 | 66.4 | 54.4 | 55.6 | 77.2 | 2.98 | 3.9 | 2.8 | 5.7 | 0.047 | 7.5 | 4.1 | 0.64019 | 58.5 | 91.6 | 0.2318 | 0.0377 | 14.43 | 13.47 | 14.43 | 0.96 | 0 | 0 | 0 | 2.6502 | 28.73 | 5.4 | 12.3 | 2020-02-08
2020-02-09 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.67261 | 0 | 0 | 0 | 0 | 14.674 | 13.412 | 14.382 | 0.97 | 0 | 0 | 0 | 2.7026 | 0 | 5.4 | 12.6 | 2020-02-09
2020-02-10 | Click Here |  | 6.05 | 5.19 | 5.24 | 5.35 | 5.4 | 6.89 | 6.73 | 1.8 | 2.01 | 2 | 1.97 | 40 | 33 | 14 | 0 | 0 | 0 | 0.298 | 0.237 | 0.711 | 0.113 | 0.401 | 0.498 | 15.4 | 33.6 | 26.9 | 27.5 | 38.8 | 30.8 | 67.2 | 53.8 | 55 | 77.6 | 2.95 | 3.79 | 2.9 | 5.8 | 0.051 | 7.4 | 4 | 0.75708 | 58.3 | 91.4 | 0.2328 | 0.0395 | 14.813 | 13.912 | 14.794 | 0.882 | 0 | 0 | 0 | 2.7171 | 30.51 | 5.4 | 12.6 | 2020-02-10
2020-02-11 | Click Here |  | 5.98 | 5.17 | 5.24 | 5.37 | 5.39 | 7.24 | 6.79 | 1.68 | 1.94 | 1.95 | 1.97 | 39 | 32 | 14 | 0 | 0 | 0 | 0.317 | 0.252 | 0.719 | 0.121 | 0.417 | 0.519 | 15.9 | 34.9 | 27.9 | 28.4 | 41.8 | 31.8 | 69.8 | 55.8 | 56.8 | 83.6 | 2.86 | 3.63 | 3.1 | 5.6 | 0.071 | 7.3 | 4.2 | 0.77068 | 57.3 | 91.3 | 0.2418 | 0.0393 | 14.91 | 13.88 | 14.88 | 1 | 1.575 | 2.504 | 7.854 | 2.7407 | 29.76 | 5.4 | 12.6 | 2020-02-11
2020-02-12 | Click Here |  | 6.13 | 5.28 | 5.23 | 5.36 | 5.4 | 7.02 | 6.45 | 1.63 | 1.92 | 1.9 | 1.91 | 38 | 32 | 13 | 1 | 0 | 0 | 0.307 | 0.256 | 0.683 | 0.137 | 0.433 | 0.516 | 16.1 | 35.1 | 27.6 | 27.8 | 39.7 | 32.2 | 70.2 | 55.2 | 55.6 | 79.4 | 2.96 | 3.82 | 3 | 5.8 | 0.055 | 7.7 | 4.1 | 0.64931 | 57.5 | 91.6 | 0.2416 | 0.039 | 14.512 | 13.541 | 14.391 | 0.85 | 0 | 0 | 0 | 2.6393 | 29.85 | 5.4 | 12.6 | 2020-02-12
2020-02-13 | Click Here |  | 5.82 | 5.15 | 5.27 | 5.25 | 5.29 | 6.43 | 6.86 | 1.7 | 2.01 | 2 | 1.95 | 39 | 33 | 17 | 2 | 0 | 0 | 0.298 | 0.247 | 1.26 | 0.161 | 0.416 | 0.443 | 15.5 | 35.7 | 27.8 | 28.4 | 40.8 | 31 | 71.4 | 55.6 | 56.8 | 81.6 | 2.99 | 4.02 | 3.1 | 5.9 | 0.066 | 6.1 | 4.1 | 0.77458 | 59.3 | 89.4 | 0.2265 | 0.0487 | 14.78 | 13.76 | 14.74 | 0.98 | 1.575 | 2.504 | 9.681 | 2.7646 | 28.23 | 5.4 | 12.9 | 2020-02-13
2020-02-14 | Click Here |  | 5.86 | 5.35 | 5.44 | 5.37 | 5.41 | 6.98 | 6.73 | 1.69 | 1.88 | 1.83 | 1.89 | 38 | 31 | 14 | 1 | 0 | 0 | 0.335 | 0.256 | 1.2 | 0.132 | 0.483 | 0.467 | 15.8 | 33.7 | 27.7 | 28 | 38.4 | 31.6 | 67.4 | 55.4 | 56 | 76.8 | 3.1 | 3.6 | 3.2 | 6.1 | 0.011 | 6.5 | 4 | 0.80712 | 58.1 | 92.9 | 0.2357 | 0.0319 | 15.14 | 14.11 | 15.04 | 0.93 | 1.575 | 2.504 | 10.031 | 2.7671 | 30.98 | 5.2 | 13 | 2020-02-14
2020-02-15 | Click Here |  | 5.83 | 5.34 | 5.33 | 5.36 | 5.44 | 7.08 | 7.05 | 1.71 | 1.91 | 2.03 | 2.01 | 38 | 31 | 16 | 1 | 0 | 0 | 0.324 | 0.253 | 1.14 | 0.128 | 0.481 | 0.475 | 15.6 | 33.4 | 27.6 | 28.3 | 40.7 | 31.2 | 66.8 | 55.2 | 56.6 | 81.4 | 3.23 | 3.63 | 3.1 | 6 | 0.014 | 6.4 | 4 | 0.51927 | 58 | 92.5 | 0.2351 | 0.0325 | 15.02 | 14.02 | 14.95 | 0.93 | 0 | 0 | 0 | 2.4993 | 30.51 | 5.2 | 13 | 2020-02-15
2020-02-16 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-02-16
2020-02-17 | Click Here |  | 6.07 | 5.1 | 5.15 | 5.19 | 5.24 | 5.05 | 5.5 | 1.62 | 1.89 | 1.87 | 1.83 | 39 | 32 | 17 | 1 | 0 | 0 | 0.296 | 0.247 | 1.04 | 0.133 | 0.228 | 0.216 | 15.9 | 34.8 | 27.5 | 27.7 | 30.1 | 31.8 | 69.6 | 55 | 55.4 | 60.2 | 3.95 | 3.08 | 3 | 5.2 | 0.028 | 7.4 | 4 | 0.66955 | 58.2 | 92.3 | 0.235 | 0.0325 | 15.03 | 14.135 | 15.044 | 0.909 | 0 | 0 | 0 | 2.5596 | 31.04 | 5.2 | 12.8 | 2020-02-17
2020-02-18 | Click Here |  | 5.98 | 5.15 | 5.19 | 5.31 | 5.37 | 6.09 | 6.59 | 1.48 | 1.87 | 1.89 | 1.83 | 38 | 32 | 14 | 0 | 0 | 0 | 0.317 | 0.246 | 0.866 | 0.133 | 0 | 0.485 | 16 | 35.3 | 28 | 28.7 | 36.3 | 32 | 70.6 | 56 | 57.4 | 72.6 | 3.22 | 3.71 | 3 | 5.1 | 0.055 | 7.4 | 4 | 0.69289 | 54.5 | 90.3 | 0.2631 | 0.0443 | 14.73 | 13.74 | 14.69 | 0.95 | 1.575 | 2.504 | 9.661 | 2.6229 | 30.3 | 5.6 | 12.8 | 2020-02-18
2020-02-19 | Click Here |  | 5.87 | 5.32 | 5.25 | 5.43 | 5.45 | 7.01 | 6.94 | 1.57 | 1.69 | 1.8 | 1.81 | 38 | 31 | 15 | 0 | 0 | 0 | 0.362 | 0.264 | 1.34 | 0.225 | 0.523 | 0.544 | 16.3 | 35.5 | 28.5 | 28.6 | 41 | 32.6 | 71 | 57 | 57.2 | 82 | 3.76 | 4.52 | 3.5 | 6.8 | 0.008 | 7.6 | 4 | 0.28598 | 57.1 | 89.7 | 0.2431 | 0.047 | 14.49 | 14.26 | 14.26 | 0 | 1.575 | 2.504 | 7.854 | 2.146 | 30.28 | 5.7 | 12.8 | 2020-02-19
2020-02-20 | Click Here |  | 5.94 | 5.44 | 5.35 | 5.51 | 5.53 | 6.96 | 6.95 | 1.49 | 1.71 | 1.87 | 1.88 | 38 | 31 | 14 | 0 | 0 | 0 | 0.33 | 0.262 | 1.7 | 0.641 | 0.684 | 0.846 | 16.5 | 32.7 | 28.1 | 28.6 | 39.5 | 33 | 65.4 | 56.2 | 57.2 | 79 | 3.38 | 4.1 | 3.4 | 6.4 | 0.01 | 8.2 | 4.1 | 0.74774 | 56.8 | 90.2 | 0.2439 | 0.0461 | 14.97 | 14.09 | 15.03 | 0.94 | 0 | 0 | 0 | 2.5577 | 30.51 | 5.7 | 12.8 | 2020-02-20
2020-02-21 | Click Here |  | 6 | 5.36 | 5.42 | 5.46 | 5.49 | 7.01 | 7.08 | 1.54 | 1.72 | 1.9 | 1.78 | 41 | 34 | 16 | 1 | 0 | 0 | 0.291 | 0.269 | 1.54 | 0.317 | 0.312 | 0.477 | 15.9 | 33.1 | 28.4 | 28.9 | 38.3 | 31.8 | 66.2 | 56.8 | 57.8 | 76.6 | 3.37 | 4.04 | 3.2 | 5.9 | 0.071 | 7.9 | 4 | 0.81461 | 56.4 | 90.9 | 0.2451 | 0.043 | 14.729 | 13.815 | 14.789 | 0.974 | 0 | 0 | 0 | 2.6346 | 30.11 | 5.5 | 12.8 | 2020-02-21
2020-02-22 | Click Here |  | 6.01 | 5.44 | 5.37 | 5.46 | 5.5 | 7 | 6.92 | 1.5 | 1.69 | 1.9 | 1.84 | 42 | 36 | 17 | 1 | 0 | 0 | 0.301 | 0.27 | 1.45 | 0.109 | 0.341 | 0.466 | 16 | 34.6 | 28 | 28.3 | 37.6 | 32 | 69.2 | 56 | 56.6 | 75.2 | 3.01 | 3.95 | 3.1 | 6 | 0.027 | 7.2 | 4.7 | 0.59014 | 56.7 | 91.6 | 0.2426 | 0.039 | 14.977 | 14.03 | 14.921 | 0.891 | 1.575 | 2.504 | 9.957 | 2.5201 | 30.33 | 5.5 | 12.8 | 2020-02-22
2020-02-23 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-02-23
2020-02-24 | Click Here |  | 5.83 | 5.35 | 5.37 | 5.42 | 5.46 | 7.14 | 7.11 | 1.61 | 1.8 | 1.87 | 1.83 | 38 | 31 | 15 | 0 | 0 | 0 | 0.409 | 0.276 | 1.17 | 0.176 | 0.607 | 0.462 | 16.2 | 35.9 | 28.4 | 28.9 | 40.5 | 32.4 | 71.8 | 56.8 | 57.8 | 81 | 3.28 | 3.96 | 3.2 | 6.2 | 0.009 | 8 | 4 | 0.17172 | 56.5 | 91.5 | 0.248 | 0.0384 | 15.32 | 14.29 | 15.14 | 0.85 | 0 | 0 | 0 | 2.0317 | 32.39 | 5.5 | 12.8 | 2020-02-24
2020-02-25 | Click Here |  | 5.91 | 5.41 | 5.37 | 5.46 | 5.5 | 6.64 | 6.82 | 1.5 | 1.7 | 1.67 | 1.75 | 37 | 30 | 14 | 0 | 0 | 0 | 0.473 | 0.261 | 1.17 | 0.252 | 0.542 | 0.524 | 16.8 | 34.2 | 27.6 | 27.7 | 37.4 | 33.6 | 68.4 | 55.2 | 55.4 | 74.8 | 3.06 | 4.04 | 3.4 | 6.5 | 0.015 | 6.3 | 4 | 0.35182 | 56.9 | 91.9 | 0.2446 | 0.0365 | 15.22 | 14.15 | 15.12 | 0.97 | 0 | 0 | 0 | 2.0518 | 29.57 | 5.5 | 12.8 | 2020-02-25
2020-02-26 | Click Here |  | 6.04 | 5.32 | 5.38 | 5.5 | 5.54 | 7.54 | 7.6 | 1.58 | 1.79 | 1.91 | 1.95 | 42 | 35 | 19 | 0 | 0 | 0 | 0.367 | 0.288 | 1.19 | 0.114 | 0.467 | 0.429 | 16.1 | 34.6 | 28.2 | 29 | 40.6 | 32.2 | 69.2 | 56.4 | 58 | 81.2 | 3.23 | 4.1 | 3.1 | 5.9 | 0.104 | 7.1 | 4 | -0.17846 | 57.5 | 89.8 | 0.24 | 0.0463 | 15.61 | 15.39 | 15.39 | 0 | 0 | 0 | 0 | 1.7015 | 29.9 | 5.5 | 12.8 | 2020-02-26
2020-02-27 | Click Here |  | 6.04 | 5.32 | 5.35 | 5.5 | 5.54 | 7.29 | 7.55 | 1.57 | 1.77 | 1.77 | 1.69 | 43 | 37 | 15 | 0 | 0 | 0 | 0.446 | 0.321 | 1.29 | 0.16 | 0.41 | 0.492 | 16.3 | 36.1 | 27.8 | 28.8 | 40.6 | 21.6 | 72.2 | 55.6 | 57.6 | 81.2 | 3.26 | 4.25 | 3.1 | 6 | 0.051 | 7 | 3.8 | 0.71747 | 58.2 | 92.8 | 0.2348 | 0.0322 | 15.45 | 14.43 | 15.53 | 1.1 | 0 | 0 | 0 | 2.4975 | 30.23 | 5.3 | 12.8 | 2020-02-27
2020-02-28 | Click Here |  | 5.82 | 5.2 | 5.39 | 5.29 | 5.31 | 6.56 | 7.65 | 1.53 | 1.76 | 1.75 | 1.72 | 42 | 36 | 17 | 2 | 0 | 0 | 0.401 | 0.27 | 1.39 | 0.183 | 0.438 | 0.5 | 16.1 | 34.4 | 27.4 | 27.5 | 40.9 | 32.2 | 68.8 | 54.8 | 55 | 81.8 | 3.18 | 3.77 | 3 | 5.8 | 0.078 | 7.4 | 3.8 | 0.6742 | 55.5 | 89.2 | 0.2554 | 0.0494 | 14.66 | 13.61 | 14.6 | 0.99 | 0 | 0 | 0 | 2.5442 | 29.32 | 5.3 | 12.8 | 2020-02-28
2020-02-29 | Click Here |  | 5.97 | 5.23 | 5.2 | 5.37 | 5.41 | 6.76 | 6.37 | 1.64 | 1.84 | 1.87 | 1.83 | 43 | 37 | 15 | 1 | 0 | 0 | 0.414 | 0.257 | 1.26 | 0.113 | 0.342 | 0.357 | 15.7 | 34.2 | 27.1 | 27.7 | 32.8 | 31.4 | 68.4 | 54.2 | 55.4 | 65.6 | 3.25 | 3.96 | 3.1 | 5.6 | 0.063 | 6.6 | 4 | 0.69429 | 55.7 | 89.6 | 0.2552 | 0.0491 | 15.11 | 14.17 | 15.12 | 0.95 | 0 | 0 | 0 | 2.6343 | 28.56 | 5.3 | 12.8 | 2020-02-29
2020-03-01 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.71044 | 0 | 0 | 0 | 0 | 15.25 | 14.186 | 15.164 | 0.978 | 0 | 0 | 0 | 2.6604 | 0 | 5.3 | 12.8 | 2020-03-01
2020-03-02 | Click Here |  | 5.93 | 5.21 | 5.19 | 5.49 | 5.54 | 7.28 | 7.79 | 1.67 | 1.94 | 2.01 | 1.99 | 47 | 41 | 18 | 1 | 0 | 0 | 0.317 | 0.264 | 1.47 | 0.112 | 0.419 | 0.613 | 16 | 34.1 | 27.4 | 27.8 | 38.5 | 32 | 68.2 | 54.8 | 55.6 | 77 | 3.15 | 4.14 | 3.2 | 5.9 | 0.071 | 7.2 | 3.8 | 0.76941 | 55.9 | 93.4 | 0.254 | 0.0293 | 15.54 | 14.674 | 15.585 | 0.911 | 0 | 0 | 0 | 2.6394 | 29.4 | 5.3 | 12.8 | 2020-03-02
2020-03-03 | Click Here |  | 6 | 5.23 | 5.19 | 5.39 | 5.41 | 7.28 | 7.29 | 1.71 | 1.94 | 1.92 | 1.75 | 40 | 33 | 33 | 2 | 0 | 0 | 0.311 | 0.27 | 2.68 | 0.524 | 0.419 | 0.518 | 15.9 | 34.1 | 26.4 | 27.8 | 39 | 31.8 | 68.2 | 52.8 | 55.6 | 78 | 3.11 | 4.12 | 2.9 | 6 | 0.084 | 7.2 | 4.2 | 0.90391 | 56.1 | 92.8 | 0.2529 | 0.0322 | 17.03 | 14.28 | 15.24 | 0.96 | 0 | 0 | 0 | 2.6639 | 30.03 | 5.3 | 12.8 | 2020-03-03
2020-03-04 | Click Here |  | 6.02 | 5.37 | 5.22 | 5.39 | 5.44 | 7.01 | 7.22 | 1.74 | 1.96 | 1.87 | 1.8 | 39 | 32 | 29 | 4 | 1 | 0 | 0.306 | 0.251 | 2.41 | 0.432 | 0.461 | 0.574 | 16.6 | 30.4 | 26.8 | 27.7 | 37.7 | 33.2 | 60.8 | 53.6 | 55.4 | 75.4 | 3.09 | 4.24 | 3 | 5.8 | 0.076 | 9.2 | 4 | 0.8544 | 56.3 | 89.8 | 0.2527 | 0.0463 | 16.49 | 13.56 | 14.49 | 0.93 | 0 | 0 | 0 | 2.6644 | 28.34 | 5.3 | 12.8 | 2020-03-04
2020-03-05 | Click Here |  | 6.1 | 5.32 | 5.21 | 5.42 | 5.47 | 7.26 | 6.94 | 1.79 | 2.01 | 2.06 | 2.02 | 40 | 33 | 18 | 1 | 0 | 0 | 0.314 | 0.268 | 0.982 | 0.085 | 0.418 | 0.533 | 16.3 | 34.7 | 27.5 | 27.9 | 38.4 | 32.6 | 69.4 | 55 | 55.8 | 76.8 | 3.15 | 4.19 | 2.9 | 5.9 | 0.044 | 7.8 | 4 | 0.73952 | 56.1 | 91.5 | 0.2529 | 0.0384 | 15.28 | 14.25 | 15.24 | 0.99 | 1.575 | 2.504 | 10.171 | 2.6695 | 28.17 | 5.3 | 12.8 | 2020-03-05
2020-03-06 | Click Here |  | 5.77 | 5.38 | 5.25 | 5.39 | 5.45 | 6.77 | 7.22 | 1.55 | 1.83 | 1.82 | 1.84 | 44 | 37 | 13 | 0 | 0 | 0 | 0.41 | 0.265 | 0.97 | 0.099 | 0.451 | 0.448 | 16.4 | 34 | 27.4 | 27.3 | 39.2 | 32.8 | 68 | 54.8 | 54.6 | 78.4 | 3.18 | 3.58 | 3.1 | 5.8 | 0.036 | 7.5 | 3.9 | 0.53042 | 57.1 | 92 | 0.243 | 0.0362 | 14.94 | 13.89 | 14.86 | 0.97 | 1.575 | 2.504 | 7.854 | 2.4504 | 30.04 | 5 | 12.8 | 2020-03-06
2020-03-07 | Click Here |  | 5.79 | 5.36 | 5.38 | 5.37 | 5.44 | 6.79 | 6.74 | 1.57 | 1.86 | 1.87 | 1.89 | 41 | 35 | 12 | 0 | 0 | 0 | 0.394 | 0.249 | 0.906 | 0.087 | 0.363 | 0.354 | 16.6 | 34.1 | 26.9 | 27.6 | 39.3 | 33.2 | 68.2 | 53.8 | 55.2 | 78.6 | 3.1 | 3.76 | 3 | 6 | 0.034 | 7.5 | 4 |  | 57.3 | 91.6 | 0.2426 | 0.0375 | 14.98 | 14.75 | 14.75 | 0 | 0 | 0 | 0 |  | 30.28 | 5 | 12.8 | 2020-03-07
2020-03-08 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-03-08
2020-03-09 | Click Here |  | 6.18 | 5.42 | 5.34 | 5.41 | 5.48 | 6.84 | 6.91 | 1.59 | 1.89 | 1.9 | 1.91 | 40 | 35 | 14 | 0 | 0 | 0 | 0.381 | 0.264 | 0.963 | 0.078 | 0.399 | 0.403 | 16.7 | 34.8 | 27.3 | 27.9 | 40.3 | 33.4 | 69.6 | 54.6 | 55.8 | 80.6 | 3.19 | 3.96 | 2.9 | 6.2 | 0.044 | 7 | 3.9 | 0.81511 | 57.5 | 91.2 | 0.2424 | 0.0378 | 14.76 | 13.586 | 14.646 | 1.06 | 0 | 0 | 0 | 2.7151 | 28.97 | 5 | 12.8 | 2020-03-09
2020-03-10 | Click Here |  | 6.41 | 5.47 | 5.32 | 5.48 | 5.5 | 6.68 | 6.72 | 1.53 | 1.8 | 1.81 | 1.79 | 39 | 33 | 12 | 0 | 0 | 0 | 0.377 | 0.257 | 0.891 | 0.093 | 0.402 | 0.451 | 17 | 35.2 | 27.6 | 27.8 | 38.1 | 34 | 70.4 | 55.2 | 55.6 | 76.2 | 3.25 | 4.05 | 3 | 6 | 0.033 | 6.9 | 3.9 | 0.75608 | 57.9 | 91 | 0.2421 | 0.038 | 15.6 | 14.59 | 15.53 | 0.94 | 1.575 | 2.504 | 10.511 | 2.6761 | 27.4 | 4.7 | 12.8 | 2020-03-10
2020-03-11 | Click Here |  | 5.84 | 5.21 | 5.27 | 5.28 | 5.35 | 6.68 | 6.83 | 1.59 | 1.84 | 1.88 | 1.94 | 42 | 36 | 10 | 0 | 0 | 0 | 0.377 | 0.289 | 0.861 | 0.103 | 0.49 | 0.484 | 16.5 | 34 | 28.1 | 28.3 | 38.3 | 33 | 68 | 56.2 | 56.6 | 76.6 | 3.18 | 3.74 | 3.4 | 6.3 | 0.015 | 6.1 | 3.8 | 0.54766 | 52.9 | 87 | 0.2759 | 0.0601 | 14.76 | 13.72 | 14.63 | 0.91 | 1.575 | 2.504 | 7.854 | 2.4077 | 30.28 | 4.3 | 12.8 | 2020-03-11
2020-03-12 | Click Here |  | 5.91 | 5.28 | 5.25 | 5.36 | 5.44 | 6.63 | 6.71 | 1.64 | 1.88 | 1.82 | 1.86 | 41 | 34 | 14 | 3 | 0 | 0 | 0.366 | 0.353 | 1.04 | 0.125 | 0.476 | 0.49 | 16.8 | 33.9 | 28.2 | 28.2 | 37.7 | 33.6 | 67.8 | 56.4 | 56.4 | 75.4 | 2.95 | 3.69 | 3.3 | 6.2 | 0.018 | 6.8 | 4.1 | 0.81092 | 58.1 | 91.9 | 0.2353 | 0.0364 | 15.54 | 14.35 | 15.33 | 0.98 | 0 | 0 | 0 | 2.6509 | 30.98 | 4.3 | 13 | 2020-03-12
2020-03-13 | Click Here |  | 6 | 5.24 | 5.19 | 5.35 | 5.41 | 6.74 | 6.68 | 1.69 | 1.92 | 1.89 | 1.77 | 40 | 32 | 12 | 1 | 0 | 0 | 0.261 | 0.239 | 0.749 | 0.096 | 0.414 | 0.407 | 16.5 | 34.1 | 28.1 | 28.6 | 36.9 | 33 | 68.2 | 56.2 | 57.2 | 73.8 | 3.09 | 3.93 | 3.2 | 6 | 0.024 | 6.9 | 4.2 | 0.91273 | 58 | 92.4 | 0.2359 | 0.0341 | 14.732 | 13.525 | 14.479 | 0.954 | 0 | 0 | 0 | 2.7327 | 30.27 | 4.3 | 13 | 2020-03-13
2020-03-14 | Click Here |  | 6.04 | 5.2 | 5.14 | 5.34 | 5.37 | 6.89 | 6.8 | 1.74 | 1.96 | 1.93 | 1.84 | 40 | 34 | 10 | 0 | 0 | 0 | 0.34 | 0.269 | 0.674 | 0.091 | 0.368 | 0.406 | 16.5 | 36.6 | 28.4 | 28.5 | 40.3 | 33 | 73.2 | 56.8 | 57 | 80.6 | 3.11 | 3.61 | 3.1 | 6 | 0.068 | 6 | 4.3 | 0.89749 | 57.6 | 92.8 | 0.2394 | 0.0319 | 14.41 | 13.36 | 14.33 | 0.97 | 1.575 | 2.504 | 9.281 | 2.6975 | 30.7 | 4.3 | 13 | 2020-03-14
2020-03-15 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-03-15
2020-03-16 | Click Here |  | 5.63 | 5.23 | 5.16 | 5.32 | 5.36 | 6.7 | 6.79 | 1.57 | 1.87 | 1.93 | 1.81 | 40 | 33 | 9 | 0 | 0 | 0 | 0.358 | 0.268 | 1.07 | 0.124 | 0.45 | 0.449 | 16.5 | 35.5 | 28.4 | 28.5 | 39.2 | 33 | 71 | 56.8 | 57 | 78.4 | 3.03 | 3.83 | 3.2 | 6.1 | 0.051 | 6.6 | 3.8 | 0.5792 | 58.2 | 93.1 | 0.2351 | 0.0308 | 15.35 | 14.42 | 15.31 | 0.89 | 1.575 | 2.504 | 10.341 | 2.4992 | 30.51 | 4.3 | 13 | 2020-03-16
2020-03-17 | Click Here |  | 5.85 | 5.28 | 5.27 | 5.33 | 5.41 | 6.87 | 6.83 | 1.65 | 1.93 | 1.91 | 2 | 45 | 37 | 14 | 2 | 0 | 0 | 0.359 | 0.26 | 1.08 | 0.104 | 0.456 | 0.451 | 16.1 | 34.2 | 28.4 | 28.5 | 39.8 | 32.2 | 68.4 | 56.8 | 57 | 79.6 | 3.12 | 4.06 | 3.1 | 6 | 0.009 | 5.8 | 3.6 | 0.72386 | 57.9 | 91.6 | 0.2368 | 0.0378 | 14.89 | 13.8 | 14.77 | 0.97 | 0 | 0 | 0 | 2.6839 | 30.29 | 4.3 | 13 | 2020-03-17
2020-03-18 | Click Here |  | 5.94 | 5.22 | 5.17 | 5.27 | 5.29 | 5.49 | 5.66 | 1.67 | 1.99 | 1.96 | 2.04 | 44 | 37 | 14 | 1 | 0 | 0 | 0.291 | 0.254 | 0.894 | 0.146 | 0.176 | 0.149 | 17.4 | 35.8 | 28.4 | 28.1 | 29.9 | 34.8 | 71.6 | 56.8 | 56.2 | 59.8 | 3.22 | 4.03 | 2.9 | 5.6 | 0.01 | 7.3 | 3.7 | 0.53959 | 58 | 89.8 | 0.2362 | 0.0464 | 14.12 | 13.91 | 13.91 | 0 | 0 | 0 | 0 | 2.5396 | 30.06 | 4.3 | 13 | 2020-03-18
2020-03-19 | Click Here |  | 5.99 | 5.22 | 5.16 | 5.4 | 5.44 | 7.27 | 6.77 | 1.74 | 2.01 | 2.01 | 1.97 | 40 | 32 | 15 | 0 | 0 | 0 | 0.361 | 0.255 | 0.699 | 0.104 | 0.409 | 0.537 | 16.9 | 36.1 | 28.3 | 29 | 40.6 | 33.8 | 72.2 | 56.6 | 58 | 81.2 | 3.14 | 4.09 | 3 | 5.8 | 0.014 | 6.9 | 3.9 | 0.83686 | 59.1 | 91.7 | 0.2299 | 0.0375 | 14.37 | 13.29 | 14.27 | 0.98 | 0 | 0 | 0 | 2.7869 | 29.41 | 4.3 | 13 | 2020-03-19
2020-03-20 | Click Here |  | 5.81 | 5.06 | 5.22 | 5.18 | 5.19 | 6.25 | 7.44 | 1.71 | 1.92 | 1.94 | 1.88 | 39 | 33 | 14 | 1 | 0 | 0 | 0.342 | 0.253 | 0.683 | 0.112 | 0.401 | 0.417 | 17.1 | 36.8 | 28.4 | 29 | 41 | 34.2 | 73.6 | 56.8 | 58 | 82 | 3.11 | 4.15 | 3 | 6 | 0.021 | 7.2 | 3.6 | 0.81351 | 59.3 | 91.3 | 0.2297 | 0.0372 | 14.204 | 13.078 | 14.048 | 0.97 | 0 | 0 | 0 | 2.7435 | 29.34 | 4.3 | 13 | 2020-03-20
2020-03-21 | Click Here |  | 6.11 | 5.28 | 5.17 | 5.37 | 5.38 | 6.32 | 7.44 | 1.74 | 1.95 | 1.93 | 1.88 | 40 | 34 | 16 | 1 | 0 | 0 | 0.362 | 0.273 | 1.09 | 0.091 | 0.422 | 0.464 | 17.3 | 36.2 | 28.4 | 28.9 | 41 | 34.6 | 72.4 | 56.8 | 57.8 | 82 | 3.07 | 4.05 | 2.9 | 6.1 | 0.038 | 7.5 | 3.7 | 0.79288 | 55.6 | 89.7 | 0.2543 | 0.0468 | 14.85 | 13.81 | 14.8 | 0.99 | 0 | 0 | 0 | 2.7329 | 28.85 | 4.3 | 13 | 2020-03-21
2020-03-22 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.82055 | 0 | 0 | 0 | 0 | 14.58 | 13.419 | 14.389 | 0.97 | 0 | 0 | 0 | 2.7706 | 0 | 4.3 | 13.4 | 2020-03-22
2020-03-23 | Click Here |  | 6.01 | 5.22 | 5.16 | 5.34 | 5.37 | 7.19 | 7.47 | 1.74 | 1.96 | 2.01 | 1.98 | 40 | 34 | 10 | 0 | 0 | 0 | 0.296 | 0.217 | 0.541 | 0.098 | 0.399 | 0.386 | 16.9 | 36.4 | 28.5 | 28.8 | 40.9 | 33.8 | 72.8 | 57 | 57.6 | 81.8 | 3.13 | 3.86 | 3.1 | 5.5 | 0.031 | 7.1 | 3.7 | 0.81154 | 58.9 | 91.9 | 0.23 | 0.0306 | 15.025 | 13.915 | 14.826 | 0.911 | 0 | 0 | 0 | 2.7915 | 30.03 | 4.3 | 13.4 | 2020-03-23
2020-03-24 | Click Here |  | 6 | 5.12 | 5.16 | 5.42 | 5.49 | 7.07 | 7.2 | 1.78 | 2.01 | 2.04 | 1.99 | 39 | 32 | 14 | 0 | 0 | 0 | 0.374 | 0.242 | 0.599 | 0.102 | 0.311 | 0.364 | 16.8 | 36.7 | 28.5 | 28.8 | 41.4 | 33.6 | 73.4 | 57 | 57.6 | 82.8 | 3.13 | 3.81 | 3.1 | 5.9 | 0.031 | 5.9 | 3.5 | 0.8293 | 59.2 | 93.5 | 0.2289 | 0.029 | 14.28 | 13.28 | 14.17 | 0.89 | 0 | 0 | 0 | 2.7893 | 29.87 | 4.3 | 13.4 | 2020-03-24
2020-03-25 | Click Here |  | 5.99 | 5.22 | 5.16 | 5.32 | 5.37 | 6.87 | 7.08 | 1.74 | 1.95 | 1.97 | 1.93 | 39 | 31 | 15 | 1 | 0 | 0 | 0.379 | 0.257 | 0.714 | 0.093 | 0.406 | 0.421 | 17.2 | 37.2 | 29.2 | 29.3 | 41.8 | 34.4 | 74.4 | 58.4 | 58.6 | 83.6 | 3.12 | 4 | 3 | 6 | 0.043 | 6.6 | 3.7 | 0.64093 | 59.5 | 93.1 | 0.2286 | 0.0294 | 14.365 | 13.655 | 14.134 | 0.479 | 0 | 0 | 0 | 2.6209 | 30.1 | 4.3 | 13.4 | 2020-03-25
2020-03-26 | Click Here |  | 5.79 | 4.99 | 5.16 | 5.1 | 5.05 | 6.78 | 7.06 | 1.77 | 1.94 | 1.95 | 1.93 | 39 | 33 | 12 | 0 | 0 | 0 | 0.361 | 0.243 | 0.919 | 0.104 | 0.396 | 0.389 | 16.9 | 36.8 | 29.3 | 29.6 | 41.9 | 33.8 | 73.6 | 58.6 | 59.2 | 83.8 | 3.11 | 3.86 | 3 | 5.8 | 0.027 | 6 | 3.6 | 0.88411 | 58 | 91.2 | 0.2364 | 0.04 | 14.15 | 13.07 | 14.04 | 0.97 | 1.575 | 2.504 | 8.991 | 2.8341 | 31.14 | 4.3 | 13.6 | 2020-03-26
2020-03-27 | Click Here |  | 5.72 | 5.12 | 5.23 | 5.16 | 5.21 | 6.78 | 7.02 | 1.75 | 1.97 | 1.84 | 1.95 | 43 | 36 | 13 | 0 | 0 | 0 | 0.382 | 0.254 | 1.11 | 0.132 | 0.516 | 0.436 | 17 | 35.6 | 29.7 | 29.6 | 42.2 | 34 | 71.2 | 59.4 | 59.2 | 84.4 | 3 | 3.55 | 3.1 | 5.9 | 0.011 | 6.3 | 3.5 | 0.50689 | 57.2 | 91.4 | 0.2421 | 0.0387 | 14.6 | 13.5 | 14.45 | 0.95 | 0 | 0 | 0 | 2.4469 | 30.98 | 4.3 | 13.6 | 2020-03-27
2020-03-28 | Click Here |  | 5.77 | 5.18 | 5.24 | 5.21 | 5.25 | 7.01 | 7.15 | 1.73 | 1.92 | 1.88 | 1.93 | 42 | 35 | 12 | 0 | 0 | 0 | 0.393 | 0.277 | 0.98 | 0.127 | 0.531 | 0.506 | 16.9 | 35.4 | 29.6 | 30.1 | 42 | 33.8 | 70.8 | 59.2 | 60.2 | 84 | 3.06 | 3.75 | 3 | 6.1 | 0.014 | 6.3 | 3.5 |  | 57 | 91.1 | 0.2428 | 0.0392 | 14.67 | 13.72 | 14.57 | 0.95 | 0 | 0 | 0 |  | 30.51 | 4.3 | 13.6 | 2020-03-28
2020-03-29 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-03-29
2020-03-30 | Click Here |  | 6.12 | 5.27 | 5.22 | 5.35 | 5.36 | 7.18 | 6.84 | 1.75 | 1.94 | 1.9 | 1.91 | 40 | 34 | 14 | 0 | 0 | 0 | 0.361 | 0.216 | 0.894 | 0.113 | 0.399 | 0.387 | 16.4 | 34.8 | 29.3 | 29.4 | 42.4 | 32.8 | 69.6 | 58.6 | 58.8 | 84.8 | 3.06 | 3.81 | 3 | 6 | 0.022 | 5.4 | 3.4 | 0.77463 | 57.4 | 91.3 | 0.2426 | 0.039 | 14.143 | 13.069 | 14.041 | 0.972 | 0 | 0 | 0 | 2.7346 | 28.59 | 4.3 | 13.6 | 2020-03-30
2020-03-31 | Click Here |  | 6.08 | 5.19 | 5.24 | 5.31 | 5.35 | 6.71 | 7.16 | 1.77 | 1.96 | 1.93 | 1.88 | 42 | 35 | 13 | 0 | 0 | 0 | 0.344 | 0.217 | 0.914 | 0.113 | 0.499 | 0.481 | 16.3 | 34.4 | 29.3 | 28.9 | 42.4 | 23.6 | 68.8 | 58.6 | 57.8 | 84.8 | 3.1 | 3.88 | 3 | 6.1 | 0.019 | 5.3 | 3.5 | 0.76181 | 57.6 | 91.5 | 0.2464 | 0.0389 | 14.58 | 13.51 | 14.45 | 0.94 | 1.575 | 2.504 | 9.431 | 2.7418 | 30.17 | 4.3 | 13.8 | 2020-03-31
2020-04-01 | Click Here |  | 5.63 | 5.13 | 5.17 | 5.18 | 5.28 | 6.91 | 7.1 | 1.8 | 1.99 | 2.01 | 1.98 | 42 | 35 | 13 | 0 | 0 | 0 | 0.333 | 0.239 | 0.924 | 0.242 | 0.499 | 0.455 | 16.4 | 36.4 | 28.8 | 29 | 41.6 | 32.8 | 72.8 | 57.6 | 58 | 83.2 | 3.04 | 3.68 | 3.1 | 5.9 | 0.01 | 6 | 3.5 | 0.48965 | 58.2 | 92.4 | 0.235 | 0.34 | 14.46 | 13.43 | 14.38 | 0.95 | 0 | 0 | 0 | 2.4596 | 30.28 | 4.3 | 14 | 2020-04-01
2020-04-02 | Click Here |  | 5.75 | 5.2 | 5.15 | 5.29 | 5.34 | 6.91 | 7.17 | 1.8 | 1.98 | 1.99 | 1.98 | 41 | 34 | 11 | 0 | 0 | 0 | 0.325 | 0.231 | 1.07 | 0.128 | 0.429 | 0.447 | 15.9 | 36.3 | 28.8 | 29 | 41.1 | 31.8 | 72.6 | 57.6 | 58 | 82.2 | 3.02 | 3.74 | 3.2 | 6.1 | 0.013 | 5.5 | 3.3 | 0.76336 | 58.1 | 92.2 | 0.2354 | 0.0346 | 14.69 | 13.65 | 14.6 | 0.95 | 0 | 0 | 0 | 2.7134 | 30.51 | 4.3 | 14 | 2020-04-02
2020-04-03 | Click Here |  | 5.86 | 5.14 | 5.17 | 5.27 | 5.34 | 7.17 | 7.14 | 1.82 | 2.04 | 1.96 | 1.86 | 39 | 31 | 15 | 0 | 0 | 0 | 0.297 | 0.216 | 0.729 | 0.117 | 0.436 | 0.427 | 17.1 | 36.6 | 28.8 | 30.7 | 41.2 | 34.2 | 73.2 | 57.6 | 61.4 | 82.4 | 3.15 | 3.6 | 3 | 6.1 | 0.024 | 6.7 | 3.4 | 0.76987 | 57.4 | 92 | 0.2426 | 0.0377 | 14.884 | 13.794 | 14.769 | 0.975 | 0 | 0 | 0 | 2.7499 | 30.09 | 4.3 | 14 | 2020-04-03
2020-04-04 | Click Here |  | 5.77 | 5.2 | 5.16 | 5.26 | 5.33 | 7.19 | 7.13 | 1.77 | 1.98 | 1.99 | 1.94 | 39 | 34 | 11 | 0 | 0 | 0 | 0.317 | 0.211 | 0.746 | 0.107 | 0.461 | 0.427 | 17.8 | 36.8 | 29.3 | 29.6 | 41.9 | 35.6 | 73.6 | 58.6 | 59.2 | 83.8 | 3.18 | 3.69 | 2.9 | 5.7 | 0.03 | 6.7 | 3.3 | 0.64718 | 56.7 | 93 | 0.2426 | 0.0315 | 14.28 | 13.77 | 14.77 | 1 | 1.575 | 2.504 | 9.691 | 2.6172 | 30.89 | 4.3 | 14 | 2020-04-04
2020-04-05 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-04-05
2020-04-06 | Click Here |  | 5.83 | 5.18 | 5.15 | 5.24 | 5.36 | 7.18 | 7.2 | 1.73 | 1.96 | 1.95 | 1.94 | 38 | 32 | 12 | 0 | 0 | 0 | 0.286 | 0.229 | 0.841 | 0.101 | 0.521 | 0.492 | 17.1 | 34.4 | 28.2 | 29.1 | 42.9 | 34.2 | 68.8 | 56.4 | 58.2 | 85.8 | 3.03 | 3.7 | 3.1 | 6 | 0.021 | 6.4 | 3.2 | 0.57148 | 58.3 | 92.6 | 0.2352 | 0.0341 | 14.47 | 13.42 | 14.39 | 0.97 | 0 | 0 | 0 | 2.4615 | 30.28 | 4.3 | 14 | 2020-04-06
2020-04-07 | Click Here |  | 5.84 | 5.28 | 5.17 | 5.31 | 5.37 | 6.84 | 7.22 | 1.73 | 1.93 | 1.94 | 1.86 | 37 | 30 | 10 | 0 | 0 | 0 | 0.326 | 0.228 | 1.17 | 0.125 | 0.518 | 0.46 | 16.5 | 36.6 | 29.5 | 29.7 | 41.9 | 33 | 73.2 | 59 | 59.4 | 83.8 | 2.99 | 3.65 | 5.7 | 3.3 | 0.016 | 5.7 | 3.3 | 0.82351 | 54.2 | 91.6 | 0.2659 | 0.0381 | 14.56 | 13.5 | 14.46 | 0.96 | 0 | 0 | 0 | 2.7435 | 30.51 | 4.3 | 14 | 2020-04-07
2020-04-08 | Click Here |  | 6.01 | 5.2 | 5.27 | 5.37 | 5.4 | 7.29 | 7.37 | 1.7 | 1.92 | 1.9 | 1.85 | 39 | 34 | 14 | 0 | 0 | 0 | 0.198 | 0.237 | 0.747 | 0.103 | 0.382 | 0.436 | 16.6 | 38 | 29.6 | 30 | 43.6 | 33.2 | 76 | 59.2 | 60 | 87.2 | 3.03 | 3.54 | 3.1 | 5.9 | 0.034 | 5.7 | 3.3 | 0.78883 | 58.5 | 92.5 | 0.2348 | 0.0336 | 14.365 | 13.202 | 14.145 | 0.943 | 0 | 0 | 0 | 2.6988 | 30.78 | 4.3 | 14 | 2020-04-08
2020-04-09 | Click Here |  | 5.9 | 5.23 | 1.99 | 5.37 | 5.4 | 7.22 | 7.3 | 1.77 | 2.03 | 1.99 | 1.9 | 39 | 33 | 16 | 0 | 0 | 0 | 0.316 | 0.245 | 0.713 | 0.098 | 0.426 | 0.519 | 16.6 | 37.5 | 29.8 | 30.2 | 44 | 33.2 | 75 | 59.6 | 60.4 | 88 | 3.17 | 3.69 | 2.9 | 5.7 | 0.012 | 5.6 | 3.8 | 0.80557 | 55.7 | 93.4 | 0.2552 | 0.0291 | 14.59 | 13.52 | 14.46 | 0.94 | 0 | 0 | 0 | 2.6656 | 30.33 | 4.3 | 14 | 2020-04-09
2020-04-10 | Click Here |  | 5.79 | 5.07 | 1.84 | 5.22 | 5.27 | 7.26 | 6.71 | 1.68 | 1.89 | 1.84 | 1.81 | 40 | 34 | 15 | 1 | 0 | 0 | 0.299 | 0.237 | 0.699 | 0.114 | 0.453 | 0.474 | 16.5 | 36.9 | 29.8 | 30.1 | 42.9 | 33 | 73.8 | 59.6 | 60.2 | 85.8 | 3.13 | 3.73 | 3 | 5.9 | 0.022 | 5.6 | 3.4 | 0.84036 | 55.9 | 93 | 0.255 | 0.0294 | 13.777 | 12.675 | 13.645 | 0.97 | 0 | 0 | 0 | 2.7004 | 25.76 | 4.3 | 14 | 2020-04-10
2020-04-11 | Click Here |  | 5.8 | 5.13 | 5.16 | 5.22 | 5.28 | 7.11 | 6.82 | 1.73 | 1.97 | 1.91 | 1.85 | 39 | 32 | 18 | 1 | 0 | 0 | 0.301 | 0.236 | 0.814 | 0.112 | 0.471 | 0.487 | 16.3 | 37.5 | 30.1 | 30.2 | 42.5 | 32.6 | 75 | 60.2 | 60.4 | 85 | 3.17 | 3.81 | 2.9 | 5.6 | 0.044 | 5.5 | 3.5 | 0.77848 | 55.7 | 92.5 | 0.2532 | 0.0336 | 14.41 | 13.34 | 14.3 | 0.96 | 0 | 0 | 0 | 2.6985 | 30.17 | 4.3 | 14 | 2020-04-11
2020-04-12 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.81229 | 0 | 0 | 0 | 0 | 14.29 | 13.29 | 14.23 | 0.94 | 0 | 0 | 0 | 2.7223 | 0 | 4.3 | 14.4 | 2020-04-12
2020-04-13 | Click Here |  | 5.92 | 5.14 | 5.11 | 5.2 | 5.24 | 6.89 | 6.98 | 1.67 | 1.9 | 1.9 | 1.94 | 43 | 38 | 17 | 0 | 0 | 0 | 0.247 | 0.231 | 0.799 | 0.109 | 0.46 | 0.539 | 16.2 | 38.2 | 29.8 | 30.2 | 41.4 | 32.4 | 76.4 | 59.6 | 60.4 | 82.8 | 3.19 | 3.75 | 3 | 5.6 | 0.061 | 5.6 | 3.4 | 0.82302 | 56.1 | 90.1 | 0.2529 | 0.045 | 15.224 | 14.149 | 15.128 | 0.979 | 0 | 0 | 0 | 2.763 | 29.95 | 4.3 | 14.4 | 2020-04-13
2020-04-14 | Click Here |  | 6 | 5.12 | 5.09 | 5.37 | 5.46 | 7.01 | 6.99 | 1.65 | 1.84 | 0 | 0 | 45 | 38 | 19 | 1 | 0 | 0 | 0.317 | 0.228 | 0.968 | 0.217 | 0.398 | 0.557 | 16.6 | 39.6 | 30.9 | 30.7 | 42.2 | 33.2 | 79.2 | 61.8 | 61.4 | 84.4 | 3.17 | 3.76 | 3.1 | 5.7 | 0.068 | 6.1 | 3.4 |  | 55.6 | 89.2 | 0.2523 | 0.0494 | 14.36 | 14.76 | 15.75 | 0.99 | 0 | 0 | 0 |  | 30.73 | 4.3 | 14.6 | 2020-04-14
2020-04-15 | Click Here |  | 5.97 | 5.13 | 5.09 | 5.23 | 5.25 | 6.71 | 6.93 | 1.73 | 1.91 | 1.89 | 1.84 | 46 | 40 | 22 | 3 | 1 | 0 | 0.386 | 0.237 | 1.21 | 0.311 | 0.496 | 0.587 | 16.6 | 38.5 | 29.4 | 30.6 | 42.1 | 33.2 | 77 | 58.8 | 61.2 | 84.2 | 3.2 | 3.89 | 3 | 5.9 | 0.083 | 5.9 | 3.4 | 0.15041 | 55.8 | 89 | 0.2521 | 0.0492 | 15.35 | 13.24 | 14.21 | 0.97 | 0 | 0 | 0 | 1.8904 | 27.78 | 4.3 | 14.6 | 2020-04-15
2020-04-16 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-04-16
2020-04-17 | Click Here |  | 5.63 | 5.15 | 5.25 | 5.2 | 5.26 | 7.1 | 7.35 | 1.57 | 1.76 | 1.9 | 1.9 | 53 | 46 | 16 | 6 | 0 | 0 | 0.368 | 0.247 | 1.33 | 0.131 | 0.553 | 0.449 | 15.9 | 35.5 | 29.8 | 30.2 | 41.9 | 31.8 | 71 | 59.6 | 60.4 | 83.8 | 3.16 | 3.8 | 3.1 | 6 | 0.015 | 5.9 | 3.5 | 0.43941 | 51.2 | 91.7 | 0.2901 | 0.0373 | 14.76 | 13.71 | 14.68 | 0.97 | 0 | 0 | 0 | 2.4094 | 34.27 | 4.3 | 15.2 | 2020-04-17
2020-04-18 | Click Here |  | 5.73 | 5.22 | 5.1 | 5.3 | 5.33 | 7.12 | 7.09 | 1.66 | 1.92 | 2.01 | 1.98 | 50 | 43 | 14 | 2 | 0 | 0 | 0.324 | 0.243 | 1.17 | 0.109 | 0.511 | 0.473 | 16.1 | 35.3 | 30.1 | 30 | 42.1 | 32.2 | 70.6 | 60.2 | 60 | 84.2 | 3.04 | 3.66 | 3.1 | 5.9 | 0.018 | 6 | 3.6 |  | 51.3 | 91.4 | 0.29 | 0.0381 | 14.82 | 13.8 | 14.77 | 0.97 | 0 | 0 | 0 |  | 31.92 | 4.3 | 15.2 | 2020-04-18
2020-04-19 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-04-19
2020-04-20 | Click Here |  | 6 | 5.06 | 5.21 | 5.19 | 5.22 | 6.21 | 6.83 | 1.61 | 1.89 | 1.99 | 1.96 | 50 | 44 | 15 | 1 | 0 | 0 | 0.311 | 0.216 | 1.06 | 0.113 | 0.471 | 0.354 | 13.4 | 34.2 | 28.6 | 28.7 | 30.3 | 26.8 | 68.4 | 57.2 | 57.4 | 60.6 | 3.07 | 3.7 | 3.1 | 5.8 | 0.036 | 5.9 | 3.6 | 0.63669 | 51.5 | 91.6 | 0.2909 | 0.0379 | 14.261 | 13.187 | 14.155 | 0.968 | 0 | 0 | 0 | 2.7267 | 25.14 | 4.3 | 15.2 | 2020-04-20
2020-04-21 | Click Here |  | 6.04 | 5.3 | 5.01 | 5.15 | 5.17 | 5.53 | 5.65 | 1.86 | 1.99 | 2.11 | 2.22 | 50 | 42 | 20 | 3 | 1 | 0 | 0.396 | 0.22 | 1.89 | 0.121 | 0.271 | 0.123 | 14.2 | 35.7 | 28.7 | 27.8 | 30.3 | 28.4 | 71.4 | 57.4 | 55.6 | 60.6 | 3.06 | 4.43 | 2.9 | 5.5 | 0.089 | 6.3 | 3.5 | 0.50485 | 51.5 | 87.8 | 0.2899 | 0.0565 | 14.96 | 13.97 | 14.94 | 0.97 | 1.575 | 2.504 | 9.891 | 2.7948 | 28.62 | 4.3 | 15.2 | 2020-04-21
2020-04-22 | Click Here |  | 5.51 | 5.25 | 5.29 | 5.05 | 5.09 | 0 | 5.62 | 1.98 | 2.03 | 2.13 | 2.33 | 49 | 42 | 16 | 2 | 0 | 0 | 0.321 | 0.228 | 1.29 | 0.136 | 0.135 | 0.069 | 14.1 | 34.5 | 29.5 | 30 | 32.6 | 28.2 | 69 | 59 | 60 | 65.2 | 2.95 | 4.05 | 3 | 5.6 | 0.178 | 6.2 | 3.5 | 0.42511 | 47.1 | 90 | 0.3268 | 0.0454 | 14.91 | 13.82 | 14.79 | 0.97 | 0 | 0 | 0 | 2.5351 | 31.92 | 4.3 | 15.2 | 2020-04-22
2020-04-23 | Click Here |  | 5.68 | 5.16 | 5.23 | 5.23 | 5.25 | 7.04 | 6.95 | 1.6 | 1.8 | 2.04 | 1.83 | 48 | 41 | 14 | 1 | 0 | 0 | 0.314 | 0.222 | 1.59 | 0.107 | 0.624 | 0.533 | 14.2 | 32.9 | 28.2 | 28.5 | 38.1 | 28.4 | 65.8 | 56.4 | 57 | 76.2 | 2.92 | 4 | 3.1 | 6 | 0.025 | 6.4 | 3.7 | 0.92895 | 47.3 | 88.3 | 0.325 | 0.054 | 14.97 | 13.8 | 14.76 | 0.96 | 0 | 0 | 0 | 2.8289 | 30.04 | 4.3 | 15.2 | 2020-04-23
2020-04-24 | Click Here |  | 5.86 | 5.09 | 5.13 | 5.32 | 5.36 | 7.14 | 7.1 | 1.67 | 1.93 | 1.88 | 1.97 | 53 | 44 | 14 | 0 | 0 | 0 | 0.311 | 0.218 | 0.692 | 0.106 | 0.51 | 0.58 | 14.2 | 34 | 28.4 | 28.2 | 36.2 | 28.4 | 68 | 56.8 | 56.4 | 72.4 | 3.09 | 3.91 | 2.9 | 6 | 0.076 | 6.1 | 3.9 | 0.73791 | 47.7 | 90.7 | 0.3229 | 0.0423 | 14.716 | 13.441 | 14.4 | 0.959 | 0 | 0 | 0 | 2.7579 | 29.39 | 4.3 | 15.2 | 2020-04-24
2020-04-25 | Click Here |  | 5.89 | 5.09 | 5.03 | 6.36 | 5.39 | 7.27 | 7.3 | 1.74 | 2.01 | 2 | 1.91 | 51 | 43 | 14 | 0 | 0 | 0 | 0.324 | 0.217 | 0.609 | 0.112 | 0.369 | 0.458 | 14 | 35.4 | 28.1 | 28.2 | 40.2 | 28 | 70.8 | 56.2 | 56.4 | 80.4 | 3.13 | 3.77 | 2.9 | 5.9 | 0.094 | 6.3 | 3.8 | 0.76784 | 48 | 91.2 | 0.3201 | 0.0399 | 14.41 | 13.26 | 14.23 | 0.97 | 1.575 | 2.504 | 9.181 | 2.7178 | 30.06 | 4.3 | 15.2 | 2020-04-25
2020-04-26 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-04-26
2020-04-27 | Click Here |  | 5.54 | 5.05 | 5.03 | 5.18 | 5.22 | 6.94 | 7.26 | 1.68 | 1.8 | 1.91 | 1.8 | 59 | 52 | 34 | 2 | 0 | 0 | 0.314 | 0.225 | 1.61 | 0.203 | 0.686 | 0.543 | 14 | 34.6 | 28.1 | 28.2 | 39.7 | 28 | 69.2 | 56.2 | 56.4 | 79.4 | 2.88 | 3.67 | 3 | 5.8 | 0.013 | 6.7 | 3.8 | 0.56422 | 48.8 | 86.5 | 0.311 | 0.0628 | 14.74 | 13.61 | 14.55 | 0.94 | 0 | 0 | 0 | 2.5742 | 30.04 | 4.3 | 15.2 | 2020-04-27
2020-04-28 | Click Here |  | 5.78 | 5.09 | 4.97 | 5.18 | 5.24 | 7.09 | 7.24 | 1.69 | 1.81 | 1.95 | 1.96 | 56 | 49 | 21 | 1 | 0 | 0 | 0.294 | 0.216 | 1.73 | 0.194 | 0.677 | 0.597 | 14.1 | 36.3 | 28.3 | 28.2 | 37 | 28.2 | 72.6 | 56.6 | 56.4 | 74 | 2.87 | 3.73 | 3.1 | 5.9 | 0.016 | 8.4 | 4 | 0.82077 | 49.1 | 88.6 | 0.3089 | 0.0561 | 14.95 | 13.84 | 14.8 | 0.96 | 0 | 0 | 0 | 2.8208 | 30.04 | 4.3 | 15.2 | 2020-04-28
2020-04-29 | Click Here |  | 5.84 | 5 | 5.09 | 5.29 | 5.32 | 7.12 | 7.18 | 1.74 | 1.96 | 1.99 | 1.98 | 54 | 48 | 14 | 1 | 0 | 0 | 0.296 | 0.233 | 0.895 | 0.112 | 0.479 | 0.524 | 14.2 | 36.5 | 28.4 | 28.3 | 39.1 | 28.4 | 73 | 56.8 | 56.6 | 78.2 | 3.03 | 3.76 | 3.1 | 5.7 | 0.029 | 8.7 | 4 | 0.57916 | 49 | 89.6 | 0.3101 | 0.047 | 13.32 | 12.96 | 12.96 | 0 | 0 | 0 | 0 | 2.5692 | 29.91 | 4.3 | 15.2 | 2020-04-29
2020-04-30 | Click Here |  | 5.9 | 5.05 | 5.07 | 5.22 | 5.27 | 7.19 | 7.55 | 1.69 | 1.88 | 1.97 | 2.05 | 56 | 49 | 17 | 0 | 0 | 0 | 0.324 | 0.238 | 1.57 | 0.139 | 0.512 | 0.49 | 14.2 | 36.5 | 28.4 | 28.5 | 40.9 | 28.4 | 73 | 56.8 | 57 | 81.8 | 3.03 | 3.77 | 2.9 | 5.8 | 0.097 | 8.6 | 4.1 | 0.68377 | 49.6 | 88.1 | 0.3051 | .0549i | 15.86 | 14.81 | 15.75 | 0.94 | 0 | 0 | 0 | 2.7038 | 30.32 | 4.3 | 15.2 | 2020-04-30
2020-05-01 | Click Here |  | 5.7 | 4.62 | 5.04 | 4.84 | 4.81 | 7.01 | 6.53 | 1.61 | 1.87 | 1.95 | 2 | 55 | 49 | 18 | 1 | 0 | 0 | 0.316 | 0.228 | 1.49 | 0.113 | 0.361 | 0.186 | 14.1 | 36.5 | 28.8 | 28.9 | 38.7 | 28.2 | 73 | 57.6 | 57.8 | 77.4 | 3.01 | 3.87 | 3 | 5.9 | 0.081 | 8.4 | 4.1 | 0.81728 | 49.8 | 88.4 | 0.3052 | 0.0546 | 14.14 | 13.1 | 14.04 | 0.94 | 0 | 0 | 0 | 2.8273 | 26.46 | 4.3 | 15.2 | 2020-05-01
2020-05-02 | Click Here |  | 5.79 | 4.75 | 5.04 | 4.88 | 4.83 | 6.56 | 6.84 | 1.69 | 1.98 | 2.07 | 2.12 | 56 | 48 | 16 | 0 | 0 | 0 | 0.324 | 0.02 | 1.36 | 0.104 | 0.563 | 0.527 | 13.6 | 35.2 | 29.2 | 29.3 | 39.5 | 27.2 | 70.4 | 58.4 | 58.6 | 79 | 2.99 | 3.97 | 3.1 | 5.6 | 0.069 | 7.6 | 4 | 0.57676 | 49.7 | 86.9 | 0.3052 | 0.0607 | 14.67 | 13.5 | 14.46 | 0.96 | 0 | 0 | 0 | 2.6968 | 30.46 | 4.3 | 15.2 | 2020-05-02
2020-05-03 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.57852 | 0 | 0 | 0 | 0 | 16.41 | 15.32 | 16.32 | 1 | 0 | 0 | 0 | 2.7385 | 0 | 4.3 | 15.2 | 2020-05-03
2020-05-04 | Click Here |  | 6.2 | 5.07 | 4.99 | 5.09 | 5.15 | 6.69 | 6.68 | 1.66 | 1.9 | 1.94 | 2.06 | 57 | 50 | 16 | 2 | 0 | 0 | 0.298 | 0.016 | 1.19 | 0.109 | 0.507 | 0.624 | 11.6 | 33.5 | 28.1 | 28 | 35.1 | 23.2 | 67 | 56.2 | 56 | 70.2 | 3.05 | 3.97 | 3 | 5.7 | 0.064 | 6.8 | 4 | 0.70447 | 49 | 89.6 | 0.3092 | 0.0491 | 15.54 | 14.31 | 15.29 | 0.98 | 0 | 0 | 0 | 2.7345 | 29.66 | 4.3 | 15.2 | 2020-05-04
2020-05-05 | Click Here |  | 6.09 | 5 | 5.03 | 5.17 | 5.19 | 6.91 | 6.57 | 1.7 | 1.99 | 1.93 | 1.98 | 59 | 51 | 10 | 0 | 0 | 0 | 0.304 | 0.017 | 1.39 | 0.107 | 0.542 | 0.647 | 11.6 | 34 | 28.6 | 28.2 | 36.3 | 23.2 | 68 | 57.2 | 56.4 | 72.6 | 2.91 | 4.03 | 3.1 | 6.2 | 0.074 | 7.3 | 4.1 | 0.54029 | 47.3 | 88 | 0.325 | 0.055 | 14.37 | 13.14 | 14.11 | 0.97 | 0 | 0 | 0 | 2.5903 | 30.6 | 4.6 | 15.4 | 2020-05-05
2020-05-06 | Click Here |  | 5.91 | 4.96 | 5.02 | 5.04 | 5.09 | 6.21 | 7.02 | 1.55 | 1.75 | 1.86 | 2.13 | 58 | 50 | 15 | 0 | 0 | 0 | 0.301 | 0.017 | 1.41 | 0.102 | 0.538 | 0.624 | 11.7 | 34.4 | 28.2 | 28.3 | 35.6 | 23.4 | 68.8 | 56.4 | 56.6 | 71.2 | 2.88 | 4.03 | 3 | 6 | 0.083 | 7.8 | 4.4 | 0.66418 | 47.5 | 84.4 | 0.3249 | 0.0736 | 14.57 | 13.41 | 14.37 | 0.96 | 0 | 0 | 0 | 2.7142 | 27.59 | 4.8 | 15.4 | 2020-05-06
2020-05-07 | Click Here |  | 5.93 | 5.04 | 5.11 | 5.1 | 5.13 | 6.71 | 6.8 | 1.64 | 1.8 | 2 | 2.19 | 57 | 50 | 16 | 0 | 0 | 0 | 0.286 | 0.001 | 1.37 | 0.098 | 0.53 | 0.631 | 11.5 | 34.6 | 27.9 | 28.1 | 35.4 | 23 | 69.2 | 55.8 | 56.2 | 70.8 | 2.96 | 4.01 | 2.9 | 6.1 | 0.091 | 7.8 | 4.5 | 0.52752 | 47.7 | 86.2 | 0.3231 | 0.0619 | 14.44 | 14.05 | 14.05 | 0 | 1.575 | 2.504 | 9.971 | 2.7075 | 29.64 | 4.8 | 15.6 | 2020-05-07
2020-05-08 | Click Here |  | 5.46 | 4.89 | 5.05 | 5.05 | 5.1 | 6.98 | 7.11 | 1.63 | 1.75 | 1.97 | 1.95 | 58 | 51 | 15 | 1 | 0 | 0 | 0.342 | 0.008 | 1.99 | 0.28 | 0.822 | 0.592 | 10.4 | 32.8 | 27.1 | 27.3 | 35.2 | 20.8 | 65.6 | 54.2 | 54.6 | 70.4 | 2.99 | 3.8 | 3.1 | 5.9 | 0.003 | 6.9 | 4.1 | 0.60141 | 50.3 | 87 | 0.2977 | 0.0601 | 14.04 | 0 | 13.75 | 0.97 | 0 | 0 | 0 | 2.7414 | 31.69 | 4.8 | 15.6 | 2020-05-08
2020-05-09 | Click Here |  | 5.26 | 4.98 | 2.05 | 5.03 | 5.09 | 7.03 | 7.07 | 1.65 | 1.81 | 2.05 | 2.02 | 56 | 49 | 14 | 1 | 0 | 0 | 0.317 | 0.01 | 2.18 | 0.313 | 0.468 | 0.384 | 10.6 | 30.3 | 26.3 | 26.6 | 33.6 | 21.2 | 60.6 | 52.6 | 53.2 | 67.2 | 2.94 | 3.76 | 3 | 5.9 | 0.011 | 7.7 | 4.5 |  | 50.8 | 88.4 | 0.2965 | 0.0589 | 14.23 | 13.84 | 13.84 | 0 | 0 | 0 | 0 |  | 30.75 | 4.8 | 15.6 | 2020-05-09
2020-05-10 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-05-10
2020-05-11 | Click Here |  | 5.96 | 4.92 | 5.02 | 5.04 | 5.05 | 8.91 | 8.86 | 1.44 | 1.6 | 1.76 | 1.91 | 55 | 47 | 16 | 1 | 0 | 0 | 0.312 | 0.274 | 1.71 | 0.161 | 0.473 | 0.427 | 9.8 | 32.4 | 25.5 | 26 | 42.2 | 19.6 | 64.8 | 51 | 52 | 84.4 | 2.96 | 3.79 | 3 | 6.3 | 0.02 | 6.1 | 4.1 | 0.70598 | 50.6 | 85.5 | 0.2967 | 0.0684 | 14.328 | 13.036 | 14.001 | 0.965 | 0 | 0 | 0 | 2.736 | 28.19 | 4.8 | 15 | 2020-05-11
2020-05-12 | Click Here |  | 6.01 | 4.95 | 5.03 | 5.06 | 5.11 | 6.3 | 6.51 | 1.58 | 1.76 | 1.96 | 2.04 | 54 | 48 | 14 | 1 | 0 | 0 | 0.316 | 0.257 | 1.49 | 0.183 | 0.766 | 0.704 | 9.6 | 32.2 | 25.8 | 25.6 | 32.9 | 19.2 | 64.4 | 51.6 | 51.2 | 65.8 | 2.97 | 3.87 | 3 | 5.6 | 0.026 | 5.9 | 4 | 0.48457 | 52.2 | 88.3 | 0.2823 | 0.0538 | 14.53 | 13.3 | 14.25 | 0.95 | 1.575 | 2.504 | 9.221 | 2.6346 | 29.13 | 5 | 14 | 2020-05-12
2020-05-13 | Click Here |  | 5.66 | 4.96 | 5.11 | 4.99 | 5.01 | 6.7 | 6.27 | 1.66 | 1.8 | 1.95 | 2.44 | 52 | 44 | 12 | 0 | 0 | 0 | 0.352 | 0.294 | 1.4 | 0.165 | 0.731 | 0.606 | 9.6 | 30.8 | 26.5 | 26.6 | 32.7 | 19.2 | 61.6 | 53 | 26.6 | 65.4 | 2.94 | 3.73 | 3.1 | 5.8 | 0.022 | 6.6 | 4 | 0.66966 | 53.5 | 89.7 | 0.2714 | 0.0472 | 14.53 | 13.3 | 14.26 | 0.96 | 1.575 | 2.504 | 9.221 | 2.7097 | 30.28 | 5.3 | 15.2 | 2020-05-13
2020-05-14 | Click Here |  | 5.76 | 5.01 | 5.07 | 5.13 | 5.12 | 7 | 6.81 | 1.68 | 1.83 | 2.01 | 1.76 | 52 | 43 | 13 | 1 | 0 | 0 | 0.35 | 0.335 | 1.29 | 0.2 | 0.681 | 0.573 | 9.4 | 32.2 | 25.7 | 26.1 | 33.2 | 18.8 | 64.4 | 51.4 | 52.2 | 66.4 | 2.8 | 3.75 | 3.1 | 5.9 | 0.02 | 7.4 | 4 | 0.98011 | 53.2 | 88.5 | 0.2738 | 0.0528 | 14.34 | 13.1 | 14.06 | 0.96 | 0 | 0 | 0 | 2.9801 | 30.04 | 5.3 | 15.5 | 2020-05-14
2020-05-15 | Click Here |  | 5.9 | 4.96 | 4.98 | 5.24 | 5.19 | 7.43 | 7.53 | 1.71 | 1.95 | 1.97 | 2.13 | 60 | 54 | 17 | 0 | 0 | 0 | 0.284 | 0.328 | 1.39 | 0.087 | 0.524 | 0.568 | 9.7 | 34.3 | 26.7 | 26.8 | 34.2 | 19.4 | 68.6 | 53.4 | 56.6 | 68.4 | 2.97 | 3.8 | 3.1 | 5.8 | 0.091 | 8.7 | 4.4 | 0.59872 | 53.3 | 88 | 0.2726 | 0.0553 | 13.98 | 13.59 | 13.59 | 0 | 0 | 0 | 0 | 2.7487 | 30.59 | 5.5 | 15.3 | 2020-05-15
2020-05-16 | Click Here |  | 5.98 | 5.08 | 5.02 | 5.2 | 5.19 | 7.67 | 7.71 | 1.75 | 1.96 | 2 | 2.05 | 56 | 48 | 14 | 0 | 0 | 0 | 0.31 | 0.324 | 0.928 | 0.087 | 0.368 | 0.429 | 10.2 | 34.7 | 27.1 | 27.4 | 35.2 | 20.4 | 69.4 | 54.2 | 54.8 | 70.4 | 2.89 | 3.8 | 3 | 5.8 | 0.084 | 8.7 | 4.4 | 0.7683 | 51.3 | 89.6 | 0.29 | 0.0491 | 13.24 | 11.94 | 12.93 | 0.99 | 1.575 | 2.504 | 7.861 | 3.0183 | 30.03 | 5.7 | 15.3 | 2020-05-16
2020-05-17 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-05-17
2020-05-18 | Click Here |  | 6.05 | 4.95 | 4.94 | 5 | 5.04 | 7.19 | 7.01 | 1.61 | 1.73 | 1.95 | 2.12 | 54 | 47 | 12 | 0 | 0 | 0 | 0.308 | 0.299 | 0.987 | 0.094 | 0.469 | 0.445 | 10.1 | 33.6 | 28 | 27.2 | 34.2 | 20.2 | 67.2 | 56 | 54.4 | 68.4 | 2.8 | 3.86 | 3.1 | 5.9 | 0.044 | 8.8 | 4.6 | 0.5961 | 53.6 | 90.1 | 0.2719 | 0.0508 | 13.63 | 12.39 | 13.33 | 0.94 | 1.575 | 2.504 | 8.311 | 2.6661 | 30.04 | 5.7 | 15.3 | 2020-05-18
2020-05-19 | Click Here |  | 5.71 | 5.01 | 5.15 | 5.05 | 5.07 | 7.26 | 7.3 | 1.79 | 1.93 | 2.15 | 1.96 | 48 | 41 | 19 | 1 | 0 | 0 | 0.334 | 0.288 | 0.959 | 0.135 | 0.543 | 0.408 | 10.7 | 34.8 | 29.4 | 29.3 | 36.5 | 21.4 | 69.6 | 58.8 | 58.6 | 73 | 2.83 | 3.77 | 3.1 | 6 | 0.023 | 10 | 5.9 | 0.86397 | 54.7 | 89 | 0.2613 | 0.0502 | 13.99 | 12.7 | 13.68 | 0.98 | 0 | 0 | 0 | 3.074 | 29.81 | 5.7 | 15.3 | 2020-05-19
2020-05-20 | Click Here |  | 5.98 | 5.09 | 5.02 | 5.14 | 5.17 | 7.12 | 7.09 | 1.84 | 1.99 | 2.2 | 2.28 | 56 | 47 | 15 | 0 | 0 | 0 | 0.317 | 0.298 | 0.864 | 0.081 | 0.427 | 0.435 | 10.9 | 34.8 | 29.6 | 29.1 | 32.6 | 21.8 | 69.6 | 59.2 | 58.2 | 65.2 | 2.93 | 3.83 | 3 | 5.9 | 0.058 | 9.8 | 6.2 | 0.66594 | 55.6 | 90 | 0.2523 | 0.0455 | 13.887 | 14.483 | 13.448 | 0.965 | 0 | 0 | 0 | 3.0059 | 29.63 | 5.7 | 15.3 | 2020-05-20
2020-05-21 | Click Here |  | 5.92 | 5.01 | 4.98 | 5.07 | 5.1 | 6.39 | 6.45 | 1.81 | 1.94 | 2.09 | 2.19 | 59 | 50 | 14 | 0 | 0 | 0 | 0.327 | 0.284 | 0.741 | 0.089 | 0.594 | 0.671 | 10 | 35 | 30.1 | 29.4 | 31.2 | 20 | 70 | 60.2 | 58.8 | 62.4 | 2.93 | 3.79 | 2.9 | 6.1 | 0.041 | 10.8 | 6.8 | 0.6886 | 53.4 | 88.8 | 0.2732 | 0.0513 | 14.47 | 13.24 | 14.22 | 0.98 | 0 | 0 | 0 | 2.9486 | 30.36 | 5.7 | 15.3 | 2020-05-21
2020-05-22 | Click Here |  | 5.73 | 4.73 | 4.98 | 4.82 | 4.87 | 6.7 | 7.15 | 1.84 | 2.07 | 2.2 | 2.31 | 59 | 51 | 15 | 1 | 0 | 0 | 0.342 | 0.336 | 0.814 | 0.086 | 0.481 | 0.493 | 10.6 | 36.2 | 31.5 | 31.4 | 35.6 | 21.2 | 72.4 | 63 | 62.8 | 71.2 | 2.97 | 3.85 | 3 | 5.9 | 0.036 | 12.7 | 7.4 | 0.55616 | 53.6 | 89 | 0.273 | 0.0511 | 13.722 | 12.397 | 13.36 | 0.963 | 0 | 0 | 0 | 2.8862 | 29.22 | 5.9 | 15.7 | 2020-05-22
2020-05-23 | Click Here |  | 6.23 | 5.01 | 5.06 | 5.06 | 5.07 | 8.04 | 8.35 | 1.57 | 1.78 | 1.94 | 2.16 | 58 | 51 | 16 | 1 | 0 | 0 | 0.361 | 0.332 | 0.801 | 0.096 | 0.397 | 0.38 | 35.4 | 31.5 | 31.8 | 31.6 | 42 | 70.8 | 63 | 63.6 | 63.2 | 84 | 2.92 | 3.82 | 3 | 6.2 | 0.039 | 11.6 | 7.6 | 0.49644 | 53.3 | 89.1 | 0.2733 | 0.0499 | 13.94 | 12.73 | 13.7 | 0.97 | 0 | 0 | 0 | 3.0164 | 30.4 | 6.3 | 16 | 2020-05-23
2020-05-24 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.27765 | 0 | 0 | 0 | 0 | 14.15 | 13.76 | 13.76 | 0 | 0 | 0 | 0 | 2.8877 | 0 | 6.3 | 15.7 | 2020-05-24
2020-05-25 | Click Here |  | 6.19 | 5.01 | 5.04 | 5.1 | 5.12 | 7.84 | 7.97 | 1.8 | 2.04 | 2.2 | 2.51 | 57 | 50 | 15 | 0 | 0 | 0 | 0.309 | 0.346 | 0.784 | 0.089 | 0.201 | 0.117 | 10.2 | 34.8 | 30.9 | 31.3 | 41.4 | 20.4 | 69.6 | 61.8 | 62.6 | 82.8 | 2.99 | 3.85 | 2.9 | 6.2 | 0.047 | 12 | 8.1 | 0.50836 | 54.6 | 89.7 | 0.2622 | 0.0472 | 15.034 | 13.847 | 14.821 | 0.974 | 0 | 0 | 0 | 3.0784 | 30.38 | 6.3 | 15.7 | 2020-05-25
2020-05-26 | Click Here |  | 6.09 | 5.1 | 5.02 | 5.09 | 5.12 | 7.68 | 7.7 | 1.79 | 1.98 | 2.2 | 2.64 | 59 | 52 | 17 | 0 | 0 | 0 | 0.401 | 0.524 | 0.817 | 0.085 | 0.237 | 0.129 | 10.4 | 32.9 | 28.4 | 28.7 | 40.7 | 20.8 | 65.8 | 56.8 | 57.4 | 81.4 | 3.07 | 3.97 | 3.1 | 0 | 0 | 3.1 | 5.9 | 0.3681 | 55.1 | 90.5 | 0.2595 | 0.0437 | 14.85 | 13.6 | 14.55 | 0.95 | 1.575 | 2.504 | 9.521 | 3.0181 | 29.34 | 6.3 | 15.7 | 2020-05-26
2020-05-27 | Click Here |  | 5.97 | 4.98 | 5.02 | 5.01 | 5.02 | 7.69 | 7.8 | 1.89 | 2.06 | 2.2 | 2.54 | 57 | 49 | 10 | 1 | 0 | 0 | 0.37 | 0.424 | 0.817 | 0.098 | 0.281 | 0.156 | 10.1 | 33.2 | 27.9 | 28.4 | 43.1 | 20.4 | 66.4 | 55.8 | 56.8 | 86.2 | 3.03 | 3.66 | 3.1 | 5.9 | 0.081 | 12.3 | 8.2 | 0.58103 | 54.8 | 90.8 | 0.262 | 0.0421 | 16.35 | 15.22 | 16.16 | 0.94 | 0 | 0 | 0 | 3.121 | 29.72 | 6.3 | 15.5 | 2020-05-27
2020-05-28 | Click Here |  | 5.96 | 5.01 | 4.99 | 5.07 | 5.1 | 7.68 | 7.77 | 1.87 | 2 | 2.2 | 2.51 | 54 | 47 | 14 | 0 | 0 | 0 | 0.392 | 0.441 | 0.896 | 0.094 | 0.174 | 0.111 | 11.6 | 39.2 | 34.1 | 33.9 | 44.8 | 23.2 | 78.4 | 68.2 | 67.8 | 89.6 | 2.91 | 3.59 | 2.9 | 5.8 | 0.062 | 15.3 | 9.3 | 0.31403 | 56.4 | 91.3 | 0.2483 | 0.0392 | 14.74 | 13.44 | 14.43 | 0.99 | 1.575 | 2.504 | 9.361 | 3.054 | 30.18 | 6.3 | 15.5 | 2020-05-28
2020-05-29 | Click Here |  | 5.79 | 4.8 | 4.97 | 4.82 | 4.8 | 8.43 | 7.88 | 1.83 | 2 | 2.2 | 2.85 | 49 | 42 | 12 | 0 | 0 | 0 | 0.431 | 0.482 | 0.53 | 0.101 | 0.201 | 0.118 | 12.2 | 40 | 34.7 | 33.6 | 44 | 24.4 | 80 | 69.4 | 67.2 | 88 | 3.01 | 3.71 | 3.1 | 5.9 | 0.25 | 16.1 | 9.7 | -0.070511 | 56.6 | 91.1 | 0.2472 | 0.0408 | 16.49 | 15.26 | 16.24 | 0.98 | 0 | 0 | 0 | 2.6895 | 30.51 | 6.3 | 15.5 | 2020-05-29
2020-05-30 | Click Here |  | 5.96 | 4.9 | 4.94 | 4.93 | 5.03 | 7.77 | 7.56 | 1.64 | 1.76 | 2.07 | 2.65 | 48 | 40 | 11 | 0 | 0 | 0 | 0.389 | 0.391 | 0.451 | 0.09 | 0.272 | 0.169 | 12.4 | 40.5 | 37 | 35.3 | 41.6 | 24.8 | 81 | 74 | 70.6 | 83.2 | 2.8 | 3.7 | 3 | 6 | 0.18 | 18 | 10.6 |  | 56.4 | 91.3 | 0.2478 | 0.0401 | 15.45 | 14.29 | 15.24 | 0.95 | 0 | 0 | 0 |  | 30.04 | 6.3 | 13.5 | 2020-05-30
2020-05-31 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-05-31
2020-06-01 | Click Here |  | 6.18 | 4.82 | 5.01 | 4.83 | 4.85 | 7.41 | 7.48 | 1.6 | 1.91 | 2.11 | 2.16 | 49 | 42 | 13 | 0 | 0 | 0 | 0.416 | 0.427 | 0.613 | 0.084 | 0.236 | 0.217 | 13.5 | 39.7 | 38 | 37.6 | 44.8 | 27 | 79.4 | 76 | 75.2 | 89.6 | 2.83 | 3.99 | 2.9 | 6.1 | 0.083 | 17.5 | 12 | 1.0689 | 56.6 | 91.6 | 0.2476 | 0.0399 | 15.1 | 13 | 14.95 | 1.95 | 0 | 0 | 0 | 3.2789 | 28.47 | 6.6 | 12.7 | 2020-06-01
2020-06-02 | Click Here |  | 6.58 | 4.93 | 5.02 | 4.94 | 4.997 | 7.91 | 7.58 | 1.58 | 1.83 | 2.06 | 2.13 | 52 | 44 | 20 | 3 | 1 | 0 | 0.407 | 0.416 | 1.126 | 0.114 | 0.261 | 0.125 | 13 | 40.5 | 37.7 | 36.9 | 45 | 26 | 81 | 75.4 | 73.8 | 90 | 2.89 | 3.99 | 3 | 6.3 | 0.097 | 17.7 | 12.1 | 0.66835 | 56.4 | 91.4 | 0.2478 | 0.0401 | 15.9 | 14.31 | 14.31 | 0 | 1.575 | 2.504 | 10.231 | 2.8684 | 29.11 | 6.8 | 12.5 | 2020-06-02
2020-06-03 | Click Here |  | 5.94 | 5.08 | 5.04 | 5.13 | 5.14 | 8.06 | 7.52 | 1.48 | 1.75 | 2.1 | 2.17 | 47 | 40 | 41 | 2 | 0 | 0 | 0.485 | 0.413 | 0.432 | 0.125 | 0.203 | 0.171 | 12.7 | 39.3 | 36.6 | 37.3 | 45.7 | 25.4 | 78.6 | 73.2 | 74.6 | 91.4 | 3.85 | 3.61 | 3.1 | 6.4 | 0.228 | 17.6 | 12.1 | 0.71396 | 57.1 | 92.2 | 0.2432 | 0.0353 | 16.61 | 13.49 | 14.42 | 0.93 | 0 | 0 | 0 | 2.894 | 31.69 | 6.8 | 12.3 | 2020-06-03
2020-06-04 | Click Here |  | 5.99 | 5.13 | 5.21 | 5.06 | 5.08 | 7.88 | 7.96 | 1.62 | 1.75 | 2.02 | 2.02 | 57 | 49 | 14 | 0 | 0 | 0 | 0.511 | 0.001 | 0.431 | 0.097 | 0.231 | 0.107 | 12.5 | 34.2 | 34.3 | 34.5 | 42.9 | 25 | 68.4 | 68.6 | 69 | 85.8 | 3.71 | 3.59 | 3.1 | 6.2 | 0.21 | 16.2 | 12 | 0.52167 | 57.3 | 92 | 0.2426 | 0.0362 | 14.97 | 13.26 | 14.74 | 0.98 | 0 | 0 | 0 | 2.6917 | 30.28 | 6.8 | 11 | 2020-06-04
2020-06-05 | Click Here |  | 6.01 | 5.2 | 5.12 | 5.09 | 5.12 | 4.69 | 4.78 | 1.69 | 1.92 | 2.18 | 2.24 | 54 | 47 | 11 | 0 | 0 | 0 | 0.401 | 0 | 0.392 | 0.084 | 0.124 | 0.059 | 12.7 | 34.5 | 33.7 | 34.1 | 43.4 | 25.4 | 69 | 67.4 | 68.2 | 86.8 | 3.55 | 3.6 | 3 | 5.9 | 0.174 | 16.3 | 12.1 | 0.028442 | 57.1 | 92.3 | 0.243 | 0.0341 | 14.631 | 13.311 | 14.276 | 0.965 | 0 | 0 | 0 | 2.4584 | 30.05 | 6.8 | 11 | 2020-06-05
2020-06-06 | Click Here |  | 6.07 | 5.09 | 5.12 | 5.04 | 5.1 | 7.29 | 7.55 | 1.77 | 1.99 | 2.2 | 2.32 | 59 | 51 | 10 | 0 | 0 | 0 | 0.346 | 0 | 0.34 | 0.079 | 0.127 | 0.088 | 13.5 | 33.9 | 31.9 | 32.4 | 44.6 | 27 | 67.8 | 63.8 | 64.8 | 89.2 | 3.75 | 3.94 | 3.1 | 6.2 | 0.098 | 0 | 0 | 0.85321 | 56.9 | 93.1 | 0.2441 | 0.0296 | 13.72 | 12.54 | 13.47 | 0.93 | 0 | 0 | 0 | 3.1932 | 30.18 | 6.8 | 11 | 2020-06-06
2020-06-07 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-06-07
2020-06-08 | Click Here |  | 5.76 | 5.1 | 5.13 | 5.12 | 5.09 | 7.83 | 7.88 | 1.68 | 1.81 | 2.19 | 2.24 | 50 | 42 | 8 | 0 | 0 | 0 | 0.566 | 0.532 | 0.424 | 0.168 | 0.169 | 0.076 | 12.3 | 35.4 | 34.1 | 34.5 | 44 | 24.6 | 70.8 | 68.2 | 69 | 88 | 3.27 | 3.69 | 3.1 | 6 | 0.198 | 16.3 | 12.9 | 0.6253 | 54.3 | 91.5 | 0.2646 | 0.0385 | 14.54 | 13.3 | 14.29 | 0.99 | 0 | 0 | 0 | 2.9353 | 30.04 | 6.8 | 11 | 2020-06-08
2020-06-09 | Click Here |  | 5.84 | 5.17 | 5.15 | 5.17 | 5.19 | 7.62 | 7.35 | 1.71 | 1.89 | 2.2 | 2.22 | 48 | 40 | 8 | 0 | 0 | 0 | 0.584 | 0.471 | 0.484 | 0.094 | 0.225 | 0.112 | 12.4 | 35 | 34.4 | 34.3 | 44.2 | 24.8 | 70 | 68.8 | 68.6 | 88.4 | 3.38 | 3.88 | 3 | 5.8 | 0.164 | 16.1 | 12.8 | 0.83237 | 54.2 | 91.7 | 0.2652 | 0.0378 | 14.65 | 13.49 | 14.46 | 0.97 | 0 | 0 | 0 | 3.0424 | 29.81 | 6.8 | 10 | 2020-06-09
2020-06-10 | Click Here |  | 6.05 | 5.1 | 5.19 | 5.12 | 5.17 | 7.4 | 7.23 | 1.73 | 1.86 | 2.18 | 2.14 | 47 | 40 | 6 | 0 | 0 | 0 | 0.379 | 0.448 | 0.358 | 0.088 | 0.212 | 0.135 | 12.1 | 35 | 32.7 | 32.2 | 40.5 | 24.2 | 70 | 65.4 | 64.4 | 81 | 3.3 | 3.63 | 3.1 | 5.9 | 0.073 | 14.5 | 12.1 | 0.74909 | 54.4 | 91.5 | 0.2647 | 0.0382 | 14.17 | 13.86 | 13.86 | 0 | 0 | 0 | 0 | 2.8891 | 30.04 | 6.8 | 9.7 | 2020-06-10
2020-06-11 | Click Here |  | 5.85 | 5.06 | 5.07 | 5.11 | 5.15 | 7.25 | 7.27 | 1.74 | 1.88 | 2.12 | 2.14 | 51 | 43 | 10 | 0 | 0 | 0 | 0.409 | 0.396 | 0.379 | 0.093 | 0.597 | 0.349 | 12.3 | 35.1 | 33.1 | 33.2 | 40.8 | 24.6 | 70.2 | 66.2 | 66.4 | 81.6 | 3.46 | 3.99 | 3.2 | 6 | 0.03 | 15.2 | 12.2 | 0.721 | 54.6 | 90.7 | 0.2629 | 0.0423 | 14.12 | 13.79 | 13.79 | 0 | 0 | 0 | 0 | 2.831 | 29.57 | 6.8 | 9.7 | 2020-06-11
2020-06-12 | Click Here |  | 6.36 | 5 | 5.07 | 5.04 | 5.06 | 6.83 | 6.95 | 1.69 | 1.87 | 2.03 | 2.06 | 51 | 44 | 11 | 0 | 0 | 0 | 0.499 | 0.496 | 0.397 | 0.084 | 0.306 | 0.158 | 12.6 | 36.2 | 33.4 | 33.2 | 40.7 | 25.2 | 72.4 | 66.8 | 66.4 | 81.4 | 3.43 | 4.05 | 3.1 | 6.1 | 0.037 | 15 | 12.5 | 0.79 | 54.7 | 90.9 | 0.2628 | 0.0421 | 14.77 | 13.62 | 14.55 | 0.93 | 0 | 0 | 0 | 2.94 | 25.87 | 6.8 | 9.7 | 2020-06-12
2020-06-13 | Click Here |  | 6.28 | 5.03 | 5.05 | 5.05 | 5.08 | 7.14 | 7.53 | 1.73 | 1.91 | 2.14 | 2.2 | 50 | 43 | 10 | 0 | 0 | 0 | 0.731 | 0.806 | 0.381 | 0.082 | 0.116 | 0.074 | 12.5 | 36.4 | 34.3 | 34.4 | 41.9 | 25 | 72.8 | 68.6 | 68.8 | 83.8 | 3.37 | 3.93 | 3 | 6.3 | 0.014 | 16.1 | 12.9 | 0.69654 | 59.9 | 91 | 0.2126 | 0.042 | 14.45 | 13.22 | 14.22 | 1 | 0 | 0 | 0 | 2.9465 | 31.27 | 6.8 | 9.7 | 2020-06-13
2020-06-14 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.61924 | 0 | 0 | 0 | 0 | 13.91 | 13.6 | 13.6 | 0 | 0 | 0 | 0 | 2.8892 | 0 | 6.8 | 9.7 | 2020-06-14
2020-06-15 | Click Here |  | 6.07 | 5.14 | 5.08 | 5.17 | 5.2 | 7.09 | 7.17 | 1.74 | 1.9 | 2.16 | 2.22 | 49 | 42 | 10 | 0 | 0 | 0 | 0.468 | 0.593 | 0.371 | 0.079 | 0.301 | 0.454 | 12.6 | 36 | 34.1 | 34.2 | 41.7 | 25.2 | 72 | 68.2 | 68.4 | 83.4 | 3.43 | 4.05 | 3.1 | 5.7 | 0.046 | 16.1 | 13.1 | 0.78856 | 54.9 | 92.1 | 0.2119 | 0.0357 | 15.54 | 14.38 | 15.36 | 0.98 | 0 | 0 | 0 | 3.0486 | 30.38 | 6.8 | 9.7 | 2020-06-15
2020-06-16 | Click Here |  | 6.02 | 5.07 | 5.05 | 5.38 | 5.39 | 7.57 | 7.6 | 1.8 | 2.04 | 2.2 | 2.33 | 57 | 50 | 7 | 0 | 0 | 0 | 0.261 | 0.532 | 0.319 | 0.074 | 0.176 | 0.067 | 12.9 | 36.7 | 34.9 | 35.2 | 44.1 | 25.8 | 73.4 | 69.8 | 70.4 | 88.2 | 3.27 | 3.89 | 3.2 | 6.1 | 0.061 | 16.9 | 13.4 | 0.85489 | 55.1 | 93.7 | 0.2571 | 0.0283 | 15.68 | 14.55 | 15.51 | 0.96 | 0 | 0 | 0 | 3.1649 | 30.48 | 6.8 | 9.5 | 2020-06-16
2020-06-17 | Click Here |  | 6.26 | 5.14 | 5.09 | 5.13 | 5.18 | 7.54 | 7.67 | 1.77 | 2.02 | 2.18 | 2.31 | 56 | 48 | 9 | 0 | 0 | 0 | 0.461 | 0.487 | 0.369 | 0.081 | 0.192 | 0.063 | 12.9 | 38.1 | 35 | 34.9 | 43.9 | 25.8 | 76.2 | 70 | 69.8 | 87.8 | 3.15 | 3.94 | 3.1 | 6.3 | 0.044 | 17.2 | 13.8 | 0.47394 | 55.3 | 93.5 | 0.2569 | 0.0285 | 15.18 | 14.88 | 14.88 | 0 | 0 | 0 | 0 | 2.8039 | 27.13 | 6.8 | 9.5 | 2020-06-17
2020-06-18 | Click Here |  | 6.36 | 5.13 | 5.18 | 5.14 | 5.17 | 7.22 | 7.44 | 1.73 | 1.98 | 2.16 | 2.28 | 57 | 48 | 10 | 1 | 0 | 0 | 0.422 | 0.436 | 0.401 | 0.086 | 0.173 | 0.064 | 12.8 | 36.5 | 33.1 | 34.7 | 43.2 | 25.6 | 36.5 | 66.2 | 69.4 | 86.4 | 3.18 | 4.04 | 3 | 6.4 | 0.029 | 16.9 | 13.8 | 0.62449 | 55.5 | 88.8 | 0.2567 | 0.0512 | 14.38 | 13.26 | 14.24 | 0.98 | 0 | 0 | 0 | 2.9445 | 30.06 | 6.8 | 9.4 | 2020-06-18
2020-06-19 | Click Here |  | 5.72 | 5.13 | 5.13 | 5.17 | 5.2 | 7.6 | 7.24 | 1.73 | 1.81 | 2.12 | 2.31 | 55 | 47 | 10 | 0 | 0 | 0 | 0.436 | 0.441 | 0.41 | 0.09 | 0.15 | 0.071 | 13 | 35.7 | 34.4 | 34.7 | 43.5 | 26 | 71.4 | 68.8 | 69.4 | 87 | 3.27 | 3.93 | 3.1 | 6.2 | 0.031 | 17.1 | 13.8 | 0.34084 | 55.3 | 90.2 | 0.2571 | 0.0442 | 15.06 | 13.91 | 14.86 | 0.95 | 0 | 0 | 0 | 2.5908 | 29.57 | 6.8 | 9.4 | 2020-06-19
2020-06-20 | Click Here |  | 5.68 | 5.09 | 5.14 | 5.14 | 5.18 | 7.6 | 7.52 | 1.77 | 1.81 | 2.2 | 1.68 | 53 | 45 | 9 | 0 | 0 | 0 | 0.398 | 0.4 | 0.405 | 0.088 | 0.148 | 0.107 | 12.9 | 35.1 | 34.2 | 34.5 | 42.8 | 25.8 | 70.2 | 68.4 | 69 | 85.6 | 3.28 | 4.03 | 3.2 | 6.1 | 0.028 | 17 | 13.6 | 0.86998 | 55.4 | 91 | 0.2568 | 0.0429 | 14.09 | 12.97 | 13.92 | 0.95 | 0 | 0 | 0 | 3.01 | 30.04 | 6.8 | 9.1 | 2020-06-20
2020-06-21 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-06-21
2020-06-22 | Click Here |  | 6.38 | 5.26 | 5.14 | 5.17 | 5.16 | 7.28 | 7.44 | 1.69 | 1.8 | 2.09 | 2.06 | 54 | 46 | 11 | 0 | 0 | 0 | 0.373 | 0.384 | 0.417 | 0.081 | 0.117 | 0.073 | 12.6 | 36.2 | 33.4 | 34.2 | 43.4 | 25.2 | 72.4 | 66.8 | 68.4 | 86.8 | 3.24 | 4.07 | 3.1 | 6.3 | 0.033 | 16.3 | 13.9 | 0.91267 | 55.6 | 91.3 | 0.2566 | 0.0427 | 15.64 | 13.68 | 15.63 | 1.95 | 0 | 0 | 0 | 3.1027 | 29.91 | 6.8 | 8.8 | 2020-06-22
2020-06-23 | Click Here |  | 6.25 | 5.17 | 5.12 | 5.19 | 5.18 | 7.49 | 7.63 | 1.74 | 1.88 | 2.1 | 2.22 | 56 | 48 | 10 | 0 | 0 | 0 | 0.344 | 0.386 | 0.407 | 0.089 | 0.128 | 0.078 | 12.9 | 35.7 | 33.1 | 34.4 | 44.2 | 25.8 | 71.4 | 66.2 | 68.8 | 88.4 | 3.37 | 4.08 | 3 | 6.1 | 0.041 | 16.4 | 13.9 | 0.40137 | 55.8 | 91.9 | 0.2554 | 0.0397 | 17.52 | 17.29 | 17.29 | 0 | 0 | 0 | 0 | 2.7214 | 28.93 | 6.8 | 8.8 | 2020-06-23
2020-06-24 | Click Here |  | 5.77 | 5.08 | 5.07 | 5.05 | 5.12 | 7.61 | 7.54 | 1.64 | 1.75 | 2.07 | 2.23 | 44 | 37 | 11 | 0 | 0 | 0 | 0.409 | 0.371 | 0.473 | 0.086 | 0.159 | 0.071 | 14 | 38.2 | 36.3 | 36.2 | 44.6 | 28 | 76.4 | 72.6 | 72.4 | 89.2 | 3.11 | 3.83 | 3.1 | 6 | 0.158 | 19.5 | 14.6 | 0.49593 | 57.9 | 91.3 | 0.2374 | 0.0396 | 17.71 | 17.58 | 16.59 | 0.99 | 0 | 0 | 0 | 2.8359 | 29.81 | 6.8 | 8.8 | 2020-06-24
2020-06-25 | Click Here |  | 5.89 | 5.13 | 5.17 | 5.14 | 5.12 | 7.44 | 7.56 | 1.6 | 1.72 | 2.12 | 2.77 | 42 | 35 | 10 | 0 | 0 | 0 | 0.394 | 0.375 | 0.439 | 0.091 | 0.196 | 0.094 | 14.7 | 39.7 | 38.4 | 38.4 | 46.4 | 29.4 | 79.4 | 76.8 | 76.8 | 92.8 | 3.18 | 4 | 3 | 5.9 | 0.143 | 21.3 | 15.6 | 0.53012 | 57.6 | 91.1 | 0.238 | 0.0402 | 17.84 | 16.74 | 17.72 | 0.98 | 0 | 0 | 0 | 2.9301 | 30.04 | 6.8 | 8.5 | 2020-06-25
2020-06-26 | Click Here |  | 5.91 | 5.15 | 5.19 | 5.14 | 5.11 | 7.48 | 7.58 | 1.63 | 1.79 | 2.11 | 2.6 | 43 | 37 | 11 | 0 | 0 | 0 | 0.39 | 0.369 | 0.411 | 0.083 | 0.181 | 0.076 | 14.5 | 39.3 | 38.5 | 38.2 | 44.3 | 29 | 78.6 | 77 | 76.4 | 88.6 | 3.14 | 3.98 | 3.1 | 6 | 0.083 | 21.4 | 15.6 | 0.17132 | 57.8 | 91.3 | 0.2379 | 0.04 | 17.25 | 16.99 | 16.99 | 0 | 0 | 0 | 0 | 2.6513 | 0 | 6.8 | 8.3 | 2020-06-26
2020-06-27 | Click Here |  | 5.95 | 5.01 | 5.25 | 5 | 4.97 | 6.83 | 7.38 | 1.61 | 1.77 | 2.06 | 2.49 | 41 | 32 | 10 | 0 | 0 | 0 | 0.376 | 0 | 0.403 | 0.096 | 0.191 | 0.147 | 15.7 | 40.2 | 40 | 40.8 | 47.2 | 31.4 | 80.4 | 80 | 81.6 | 94.4 | 3.18 | 3.93 | 3 | 5.9 | 0.091 | 23 | 17.4 | 0.32649 | 57.6 | 91.5 | 0.2381 | 0.0399 | 16.21 | 15.11 | 16.09 | 0.98 | 0 | 0 | 0 | 2.7165 | 28.46 | 6.8 | 8.3 | 2020-06-27
2020-06-28 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-06-28
2020-06-29 | Click Here |  | 5.61 | 5.09 | 5.06 | 5.12 | 5.15 | 7.54 | 6.98 | 1.48 | 1.67 | 2.14 | 2.43 | 41 | 33 | 16 | 0 | 0 | 0 | 0.406 | 0 | 0.804 | 0.087 | 0.162 | 0.069 | 15.3 | 40.6 | 39.2 | 39.1 | 48.8 | 30.6 | 81.2 | 78.4 | 78.2 | 97.6 | 3.19 | 3.86 | 3.1 | 6 | 0.129 | 21.7 | 17.6 | 0.58134 | 58.8 | 91.7 | 0.23 | 0.0375 | 17.09 | 16.05 | 17.02 | 0.97 | 0 | 0 | 0 | 2.9313 | 29.81 | 7 | 8.2 | 2020-06-29
2020-06-30 | Click Here |  | 6.05 | 5.16 | 5.08 | 5.35 | 5.39 | 7.44 | 7.5 | 1.54 | 1.7 | 2.2 | 2.26 | 40 | 32 | 12 | 0 | 0 | 0 | 0.387 | 0.374 | 0.452 | 0.086 | 0.143 | 0.09 | 15.4 | 40.5 | 38.9 | 39.2 | 49.3 | 30.8 | 81 | 77.8 | 78.4 | 98.6 | 2.98 | 3.7 | 3.3 | 5.8 | 0.099 | 22 | 17.5 | 0.50674 | 59.1 | 92.1 | 0.2278 | 0.0345 | 16.09 | 14.98 | 15.96 | 0.98 | 0 | 0 | 0 | 2.8067 | 29.57 | 7 | 7.5 | 2020-06-30
2020-07-01 | Click Here |  | 6.01 | 5.1 | 5.13 | 5.3 | 5.41 | 7.16 | 7.1 | 1.58 | 1.27 | 2.2 | 2.39 | 48 | 39 | 17 | 0 | 0 | 0 | 0.359 | 0.391 | 0.399 | 0.091 | 0.17 | 0.049 | 15.6 | 40.4 | 38.2 | 37.3 | 47 | 31.2 | 80.8 | 76.4 | 74.6 | 94 | 3.29 | 3.93 | 3 | 6.1 | 0.107 | 22.6 | 18.1 | 0.43601 | 57.6 | 92.2 | 0.2381 | 0.0358 | 15.53 | 15.32 | 15.32 | 0 | 0 | 0 | 0 | 2.796 | 29.72 | 7 | 7.5 | 2020-07-01
2020-07-02 | Click Here |  | 6.03 | 5.15 | 5.11 | 5.31 | 5.37 | 7.29 | 7.38 | 1.61 | 1.84 | 2.2 | 2.43 | 42 | 33 | 14 | 0 | 0 | 0 | 0.298 | 0.397 | 0.399 | 0.094 | 0.137 | 0.05 | 15.9 | 39.8 | 39.1 | 40.3 | 49 | 31.8 | 79.6 | 79.2 | 80.6 | 98 | 3.12 | 4.05 | 3 | 6 | 0.086 | 23.3 | 18.5 |  | 61 | 92.4 | 0.2144 | 0.0339 | 14.97 | 13.9 | 14.84 | 0.94 | 0 | 0 | 0 |  | 30.54 | 7 | 7.5 | 2020-07-02
2020-07-03 | Click Here |  | 6.31 | 5.33 | 5.18 | 5.39 | 5.42 | 7.06 | 7.23 | 1.59 | 1.8 | 1.99 | 2.27 | 44 | 36 | 12 | 0 | 0 | 0 | 0.381 | 0.426 | 0.421 | 0.096 | 0.163 | 0.074 | 14.9 | 38.1 | 36.4 | 37 | 47 | 29.8 | 76.2 | 72.8 | 74 | 94 | 3.16 | 4.01 | 3.1 | 5.8 | 0.094 | 20.4 | 17.9 | 0.90262 | 59.9 | 92.6 | 0.2146 | 0.0337 | 14.138 | 12.993 | 13.965 | 0.972 | 0 | 0 | 0 | 3.1126 | 28.09 | 7 | 7.5 | 2020-07-03
2020-07-04 | Click Here |  | 6.3 | 5.18 | 5.14 | 5.21 | 5.32 | 6.96 | 6.96 | 1.76 | 1.95 | 2.01 | 2.14 | 43 | 36 | 14 | 1 | 0 | 0 | 0.421 | 0.436 | 0.506 | 0.098 | 0.189 | 0.074 | 14.2 | 38.5 | 36.6 | 36.2 | 46.4 | 28.4 | 77 | 73.2 | 72.4 | 92.8 | 3.12 | 3.89 | 3 | 6 | 0.071 | 18.8 | 17.3 | 1.5477 | 59.7 | 92.4 | 0.2148 | 0.0339 | 14.2 | 13.03 | 14.02 | 0.99 | 0 | 0 | 0 | 3.6877 | 29.06 | 7 | 7.5 | 2020-07-04
2020-07-05 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-07-05
2020-07-06 | Click Here |  | 5.61 | 5.06 | 5.08 | 5.04 | 5.18 | 7.43 | 6.87 | 1.79 | 1.92 | 2.2 | 2.04 | 39 | 32 | 18 | 0 | 0 | 0 | 0.415 | 0.406 | 0.669 | 0.094 | 0.144 | 0.075 | 14.4 | 38.8 | 37.4 | 36.6 | 46.7 | 28.8 | 77.6 | 74.8 | 73.2 | 93.4 | 3.07 | 3.8 | 3.1 | 5.9 | 0.088 | 19.2 | 17.1 | 0.83546 | 59.8 | 91.9 | 0.223 | 0.0363 | 16.8 | 15.83 | 16.67 | 0.84 | 0 | 0 | 0 | 3.0355 | 28.64 | 7 | 7.5 | 2020-07-06
2020-07-07 | Click Here |  | 5.62 | 4.85 | 4.87 | 4.53 | 4.79 | 7 | 6.91 | 1.62 | 1.74 | 2.05 | 2.14 | 40 | 33 | 25 | 1 | 0 | 0 | 0.405 | 0.405 | 1.08 | 0.117 | 0.415 | 0.319 | 15 | 41.9 | 39.2 | 30.8 | 36.5 | 30 | 83.8 | 78.4 | 61.6 | 73 | 2.78 | 3.73 | 3 | 6 | 0.017 | 20 | 17.3 | 0.74053 | 72.4 | 89.7 | 0.1398 | 0.0471 | 18.11 | 17.08 | 18.04 | 0.96 | 0 | 0 | 0 | 2.9305 | 29.81 | 7 | 7.5 | 2020-07-07
2020-07-08 | Click Here |  | 6.11 | 5.28 | 4.93 | 5.27 | 5.07 | 6.83 | 7.55 | 1.6 | 1.8 | 2.1 | 2.45 | 40 | 34 | 21 | 3 | 1 | 0 | 0.391 | 0.386 | 1.03 | 0.121 | 0.217 | 0.064 | 15.4 | 41.4 | 39.7 | 39.6 | 50.7 | 30.8 | 82.8 | 79.4 | 79.2 | 101.4 | 2.82 | 3.83 | 3.1 | 6.2 | 0.029 | 20.8 | 17.8 | 0.5376 | 72.1 | 89.9 | 0.1401 | 0.0469 | 17.86 | 16.81 | 17.8 | 0.99 | 0 | 0 | 0 | 2.9776 | 29.95 | 7 | 7.5 | 2020-07-08
2020-07-09 | Click Here |  | 6.13 | 5.34 | 5.31 | 5.06 | 5.04 | 6.96 | 7.08 | 1.72 | 1.87 | 2.04 | 2.55 | 39 | 33 | 23 | 2 | 1 | 0 | 0.399 | 0.396 | 1.14 | 0.13 | 0.178 | 0.16 | 15.5 | 38.4 | 39.7 | 40.1 | 49.6 | 31 | 76.8 | 79.4 | 80.2 | 99.2 | 2.85 | 3.88 | 3 | 6.1 | 0.047 | 22.1 | 18.3 | 0.54353 | 59.9 | 86.2 | 0.2219 | 0.0643 | 16.3 | 15.21 | 16.19 | 0.98 | 0 | 0 | 0 | 3.0935 | 29.28 | 7 | 7.5 | 2020-07-09
2020-07-10 | Click Here |  | 6.05 | 5.33 | 5.18 | 5.26 | 5.32 | 7.81 | 7.07 | 1.63 | 1.9 | 2.22 | 2.41 | 38 | 31 | 18 | 1 | 0 | 0 | 0.405 | 0.414 | 0.892 | 0.111 | 0.143 | 0.06 | 15.2 | 39 | 38.3 | 38.2 | 48.7 | 30.4 | 78 | 76.6 | 76.4 | 97.4 | 2.85 | 3.73 | 3.1 | 5.9 | 0.106 | 19.9 | 18 | 0.69215 | 61 | 92.2 | 0.2145 | 0.0352 | 16.47 | 15.39 | 16.37 | 0.98 | 0 | 0 | 0 | 2.9922 | 29.57 | 6.8 | 7.9 | 2020-07-10
2020-07-11 | Click Here |  | 5.9 | 5.43 | 5.3 | 5.26 | 5.27 | 7.21 | 7.27 | 1.77 | 1.9 | 2.2 | 2.31 | 37 | 30 | 16 | 1 | 0 | 0 | 0.421 | 0.418 | 1 | 0.104 | 0.191 | 0.062 | 15.8 | 38.6 | 37.7 | 38.2 | 48.6 | 31.6 | 77.2 | 75.4 | 76.4 | 97.2 | 2.85 | 3.69 | 3 | 6 | 0.069 | 20.4 | 19 |  | 59.8 | 92.3 | 0.2162 | 0.0348 | 16.17 | 15.09 | 16.08 | 0.99 | 0 | 0 | 0 |  | 29.81 | 6.8 | 7.2 | 2020-07-11
2020-07-12 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-07-12
2020-07-13 | Click Here |  | 6.18 | 5.11 | 5.23 | 5 | 5.12 | 6.96 | 6.61 | 1.78 | 1.94 | 2.2 | 2.33 | 39 | 32 | 19 | 2 | 1 | 0 | 0.499 | 0.496 | 1.26 | 0.113 | 0.194 | 0.097 | 15.3 | 39.5 | 38.3 | 37.9 | 45.7 | 30.6 | 79 | 76.6 | 75.8 | 91.4 | 2.89 | 3.77 | 3 | 6.1 | 0.058 | 20.3 | 18 | 0.66234 | 59.9 | 92.1 | 0.2161 | 0.035 | 16.34 | 15.34 | 16.27 | 0.93 | 0 | 0 | 0 | 2.8823 | 29.34 | 6.8 | 7.2 | 2020-07-13
2020-07-14 | Click Here |  | 6.14 | 5.29 | 5.11 | 5.09 | 4.99 | 6.76 | 7.15 | 1.8 | 1.97 | 2.2 | 2.44 | 40 | 33 | 26 | 3 | 1 | 0 | 0.491 | 0.486 | 1.67 | 0.163 | 0.216 | 0.084 | 15.5 | 36.9 | 35.4 | 36.8 | 47.4 | 31 | 73.8 | 70.8 | 73.6 | 94.8 | 2.85 | 3.8 | 3.1 | 6 | 0.083 | 21.3 | 18.4 | 1.0983 | 59.7 | 89.8 | 0.216 | 0.047 | 18.21 | 13.45 | 15.37 | 1.92 | 0 | 0 | 0 | 3.4983 | 29.7 | 6.8 | 7.5 | 2020-07-14
2020-07-15 | Click Here |  | 5.84 | 5.18 | 5.13 | 4.56 | 4.9 | 7.04 | 7.02 | 1.8 | 2.04 | 2.2 | 2.14 | 42 | 35 | 7 | 0 | 0 | 0 | 0.49 | 0.492 | 0.313 | 0.085 | 0.218 | 0.081 | 14.9 | 38.1 | 36.8 | 36.6 | 46.7 | 29.8 | 76.2 | 73.6 | 73.2 | 93.4 | 2.78 | 3.53 | 3 | 5.8 | 0.032 | 18.8 | 17.7 | 1.1201 | 60.7 | 92 | 0.2168 | 0.036 | 14.71 | 13.87 | 13.87 | 0 | 0 | 0 | 0 | 3.3201 | 30.04 | 6.8 | 7.5 | 2020-07-15
2020-07-16 | Click Here |  | 6.06 | 5.05 | 5.19 | 5.09 | 5.1 | 7 | 6.96 | 1.9 | 2.08 | 2.2 | 2.07 | 37 | 30 | 8 | 0 | 0 | 0 | 0.425 | 0.481 | 0.318 | 0.083 | 0.239 | 0.139 | 14.2 | 38.7 | 35.4 | 36 | 46 | 28.4 | 77.4 | 70.8 | 72 | 92 | 2.67 | 3.55 | 3.1 | 6 | 0.026 | 17.3 | 17.1 | 1.3815 | 61.9 | 91.7 | 0.2079 | 0.0375 | 14.91 | 13.85 | 14.82 | 0.97 | 0 | 0 | 0 | 3.5415 | 29.57 | 6.8 | 7.5 | 2020-07-16
2020-07-17 | Click Here |  | 5.91 | 5.12 | 5.15 | 5.01 | 5.13 | 7.11 | 7.19 | 1.84 | 2.01 | 2.16 | 2.18 | 54 | 47 | 13 | 0 | 0 | 0 | 0.326 | 0.445 | 0.478 | 0.114 | 0.124 | 0.085 | 14.3 | 38.1 | 35.9 | 36.3 | 47.3 | 28.6 | 76.2 | 71.8 | 72.6 | 94.6 | 2.87 | 3.55 | 3.1 | 5.8 | 0.044 | 17.6 | 16.9 | 1.0406 | 59.9 | 90.9 | 0.2219 | 0.0412 | 16.82 | 15.81 | 16.78 | 0.97 | 0 | 0 | 0 | 3.2906 | 29.82 | 6.8 | 7.5 | 2020-07-17
2020-07-18 | Click Here |  | 5.89 | 5.07 | 5.15 | 4.94 | 4.99 | 7.01 | 6.79 | 1.87 | 2.09 | 2.14 | 2.2 | 43 | 36 | 9 | 0 | 0 | 0 | 0.317 | 0.421 | 0.337 | 0.094 | 0.196 | 0.172 | 14.4 | 37.8 | 36.1 | 36.5 | 47.7 | 28.8 | 75.6 | 72.2 | 73 | 95.4 | 2.82 | 3.56 | 3 | 5.9 | 0.041 | 17.5 | 17 | 0.819 | 60.1 | 91.4 | 0.2194 | 0.0389 | 15.68 | 15.52 | 15.52 | 0 | 0 | 0 | 0 | 3.049 | 30.23 | 6.8 | 7.5 | 2020-07-18
2020-07-19 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-07-19
2020-07-20 | Click Here |  | 6.06 | 5 | 4.98 | 4.99 | 5.02 | 6.34 | 7.03 | 1.87 | 1.94 | 2.2 | 2.45 | 37 | 29 | 7 | 0 | 0 | 0 | 0.37 | 0.361 | 0.361 | 0.087 | 0.315 | 0.179 | 15.6 | 38.5 | 39.5 | 39.7 | 44.2 | 31.2 | 77 | 79 | 79.4 | 88.4 | 2.76 | 3.75 | 3.1 | 6 | 0.012 | 21 | 18.2 | 0.60897 | 62.1 | 88.4 | 0.2064 | 0.0532 | 17.73 | 16.69 | 17.69 | 1 | 0 | 0 | 0 | 3.119 | 29.57 | 6.8 | 8 | 2020-07-20
2020-07-21 | Click Here |  | 6.05 | 4.78 | 4.95 | 4.82 | 4.88 | 6.38 | 7 | 1.78 | 1.86 | 2.2 | 2.45 | 35 | 28 | 5 | 0 | 0 | 0 | 0.39 | 0.37 | 0.4 | 0.088 | 0.336 | 0.158 | 16.1 | 41.3 | 40 | 39.9 | 43.9 | 32.2 | 82.6 | 80 | 79.8 | 87.8 | 2.6 | 3.77 | 3 | 5.8 | 0.013 | 21.9 | 18.4 | 0.46458 | 62.5 | 90.6 | 0.2041 | 0.0428 | 18.32 | 18.2 | 18.2 | 0 | 0 | 0 | 0 | 2.9146 | 29.34 | 6.8 | 9 | 2020-07-21
2020-07-22 | Click Here |  | 5.94 | 4.97 | 4.86 | 4.87 | 4.91 | 6.54 | 6.51 | 1.87 | 2 | 2.2 | 2.44 | 40 | 31 | 9 | 0 | 0 | 0 | 0.368 | 0.47 | 0.41 | 0.091 | 0.296 | 0.175 | 16.2 | 42 | 40.9 | 39.2 | 43.6 | 32.4 | 84 | 81.8 | 78.4 | 87.2 | 2.8 | 4 | 2.9 | 5.8 | 0.037 | 22.5 | 18.8 | 0.68835 | 64.6 | 90.9 | 0.1893 | 0.0411 | 21.13 | 19.74 | 21.25 | 1.51 | 0 | 0 | 0 | 3.1883 | 29.6 | 6.8 | 9.6 | 2020-07-22
2020-07-23 | Click Here |  | 5.93 | 5.02 | 4.96 | 5.03 | 5.08 | 6.99 | 6.83 | 1.9 | 2.06 | 2.2 | 2.52 | 39 | 31 | 14 | 0 | 0 | 0 | 0.306 | 0.431 | 0.417 | 0.103 | 0.211 | 0.154 | 16.3 | 42.3 | 40.4 | 40.3 | 46.2 | 32.6 | 84.6 | 80.8 | 80.6 | 92.4 | 2.88 | 3.86 | 3 | 5.8 | 0.064 | 22.3 | 18.9 | 0.21681 | 63.9 | 91.4 | 0.191 | 0.0392 | 20.32 | 19.82 | 20.3 | 0.48 | 0 | 0 | 0 | 2.6768 | 29.09 | 7 | 9.6 | 2020-07-23
2020-07-24 | Click Here |  | 6.41 | 4.99 | 4.9 | 4.97 | 4.99 | 6.63 | 6.92 | 1.87 | 2.03 | 2.2 | 2.41 | 40 | 34 | 16 | 1 | 0 | 0 | 0.316 | 0.307 | 0.528 | 0.096 | 0.194 | 0.146 | 16.4 | 41.7 | 36.4 | 40.8 | 48.7 | 32.8 | 83.4 | 72.8 | 81.6 | 97.4 | 2.94 | 3.9 | 3.1 | 5.9 | 0.073 | 22.4 | 19.3 | 0.80197 | 63.7 | 91.1 | 0.1912 | 0.039 | 17.64 | 15.82 | 17.76 | 1.94 | 0 | 0 | 0 | 3.302 | 29.28 | 7 | 9.6 | 2020-07-24
2020-07-25 | Click Here |  | 6.28 | 4.96 | 5.03 | 4.92 | 5.04 | 6.83 | 7.02 | 1.75 | 1.98 | 2.19 | 2.36 | 39 | 32 | 12 | 0 | 0 | 0 | 0.352 | 0.336 | 0.395 | 0.081 | 0.396 | 0.388 | 16.3 | 41.3 | 40.1 | 39.5 | 47.4 | 32.6 | 82.6 | 80.2 | 79 | 94.8 | 2.91 | 3.89 | 3 | 5.7 | 0.059 | 21.6 | 19.1 | 0.59468 | 62.1 | 90.1 | 0.2067 | 0.0449 | 16.42 | 15.42 | 16.38 | 0.96 | 0 | 0 | 0 | 3.0947 | 29.85 | 7 | 9.1 | 2020-07-25
2020-07-26 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.45241 | 0 | 0 | 0 | 0 | 13.57 | 13.4 | 13.4 | 0 | 0 | 0 | 0 | 2.8524 | 0 | 7 | 10.2 | 2020-07-26
2020-07-27 | Click Here |  | 5.97 | 5.14 | 5.12 | 5.24 | 5.21 | 7.56 | 7.72 | 1.79 | 1.94 | 2.2 | 2.41 | 51 | 45 | 10 | 0 | 0 | 0 | 0.391 | 0.419 | 0.412 | 0.094 | 0.104 | 0.099 | 16.1 | 40.6 | 39 | 40.2 | 52.5 | 32.2 | 81.2 | 78 | 80.4 | 105 | 3 | 3.71 | 3 | 5.9 | 0.061 | 20.9 | 18.9 | 0.69366 | 62.1 | 90.6 | 0.2067 | 0.0416 | 14.94 | 13.87 | 14.84 | 0.97 | 0 | 0 | 0 | 3.1237 | 29.69 | 7 | 10.2 | 2020-07-27
2020-07-28 | Click Here |  | 6.01 | 5.1 | 5.14 | 5.34 | 5.37 | 7.6 | 7.69 | 1.84 | 1.98 | 2.17 | 2.39 | 42 | 34 | 15 | 0 | 0 | 0 | 0.368 | 0.399 | 0.391 | 0.074 | 0.113 | 0.099 | 16.1 | 40.4 | 39.4 | 39.6 | 51.1 | 32.2 | 80.8 | 78.8 | 79.2 | 102.2 | 3.11 | 3.9 | 3.1 | 6.2 | 0.057 | 20.8 | 18.8 | 0.70819 | 65.1 | 92 | 0.186 | 0.0359 | 15.48 | 14.4 | 15.38 | 0.98 | 0 | 0 | 0 | 3.1282 | 29.52 | 7 | 10.2 | 2020-07-28
2020-07-29 | Click Here |  | 6.34 | 5.05 | 5.1 | 5.01 | 5.05 | 6.81 | 7.13 | 1.79 | 1.93 | 2.14 | 2.31 | 41 | 32 | 13 | 0 | 0 | 0 | 0.863 | 0.871 | 0.387 | 0.081 | 0.344 | 0.336 | 16.3 | 41 | 39.1 | 39.7 | 49.3 | 32.6 | 82 | 78.2 | 79.4 | 98.6 | 3.04 | 3.83 | 3 | 6 | 0.077 | 20.8 | 18.9 | 0.76223 | 64.9 | 92.2 | 0.1862 | 0.0357 | 15.99 | 14.98 | 15.95 | 0.97 | 0 | 0 | 0 | 3.1222 | 29.85 | 7 | 10.2 | 2020-07-29
2020-07-30 | Click Here |  | 6.28 | 5.07 | 5.11 | 5.03 | 5.09 | 6.92 | 7.43 | 1.82 | 1.95 | 2.16 | 2.37 | 43 | 34 | 15 | 1 | 0 | 0 | 0.491 | 0.436 | 0.487 | 0.101 | 0.213 | 0.204 | 16.1 | 40.3 | 39.2 | 39.5 | 48.4 | 32.2 | 80.6 | 78.4 | 79 | 96.8 | 2.97 | 3.99 | 3.1 | 6.2 | 0.069 | 20.7 | 18.8 | 0.75664 | 64.7 | 92 | 0.1864 | 0.0359 | 14.29 | 13.17 | 14.14 | 0.97 | 0 | 0 | 0 | 3.1166 | 29.85 | 7 | 10.2 | 2020-07-30
2020-07-31 | Click Here |  | 6.38 | 5 | 5.1 | 5.05 | 5.08 | 6.83 | 7.25 | 1.63 | 1.73 | 1.97 | 1.98 | 40 | 33 | 12 | 1 | 0 | 0 | 0.403 | 0.678 | 0.322 | 0.089 | 0.313 | 0.278 | 16.3 | 40 | 38.8 | 39.8 | 48.7 | 32.6 | 80 | 77.6 | 79.6 | 97.4 | 2.84 | 3.77 | 3 | 6 | 0.041 | 20.5 | 18.7 | 1.2473 | 64.7 | 92.4 | 0.1866 | 0.0351 | 13.84 | 12.79 | 13.73 | 0.94 | 0 | 0 | 0 | 3.2873 | 30.04 | 7 | 10.2 | 2020-07-31
2020-08-01 | Click Here |  | 5.67 | 5.02 | 5.11 | 5.01 | 5.1 | 7.06 | 7.42 | 1.57 | 1.75 | 2.12 | 2.22 | 39 | 32 | 11 | 0 | 0 | 0 | 0.389 | 0.552 | 0.312 | 0.086 | 0.209 | 0.153 | 16.4 | 39.8 | 38.9 | 39.5 | 47.6 | 32.8 | 79.6 | 77.8 | 79 | 95.2 | 2.95 | 3.84 | 3.1 | 6.2 | 0.045 | 20.4 | 18.5 | 0.91337 | 64.4 | 92.1 | 0.1874 | 0.0362 | 13.24 | 12.13 | 13.11 | 0.98 | 0 | 0 | 0 | 3.0534 | 29.57 | 7 | 10.2 | 2020-08-01
2020-08-02 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-08-02
2020-08-03 | Click Here |  | 6.41 | 5.03 | 5.09 | 5.02 | 5.08 | 6.83 | 7.27 | 1.59 | 1.79 | 2.09 | 2.13 | 40 | 33 | 12 | 1 | 0 | 0 | 0.361 | 0.437 | 0.407 | 0.093 | 0.261 | 0.224 | 16 | 39.6 | 38.6 | 38.5 | 48 | 32 | 79.2 | 77.2 | 76 | 96 | 2.99 | 3.95 | 3 | 6 | 0.049 | 20.5 | 18.7 | 0.63925 | 64.6 | 91.9 | 0.1872 | 0.0364 | 14.93 | 14.81 | 14.81 | 0 | 0 | 0 | 0 | 2.7593 | 28.85 | 7 | 10.2 | 2020-08-03
2020-08-04 | Click Here |  | 6.22 | 4.83 | 5.58 | 4.87 | 4.96 | 6.84 | 7.38 | 1.68 | 1.92 | 2.16 | 2.27 | 39 | 32 | 10 | 0 | 0 | 0 | 0.373 | 0.456 | 0.396 | 0.091 | 0.226 | 0.173 | 16.9 | 41.3 | 40.4 | 39.6 | 46.6 | 33.8 | 82.6 | 80.8 | 79.2 | 93.2 | 2.93 | 4.03 | 3.1 | 5.9 | 0.026 | 21.8 | 19.2 | 0.83388 | 64.4 | 92.1 | 0.1874 | 0.0362 | 14.82 | 13.71 | 14.71 | 1 | 0 | 0 | 0 | 2.9939 | 29.66 | 7 | 10.2 | 2020-08-04
2020-08-05 | Click Here |  | 6.19 | 5.1 | 5.13 | 5.17 | 5.14 | 7.14 | 7.06 | 1.7 | 1.8 | 2.15 | 2.11 | 38 | 31 | 11 | 0 | 0 | 0 | 0.439 | 0.512 | 0.298 | 0.086 | 0.212 | 0.2 | 15.9 | 40 | 38.9 | 39.9 | 51.2 | 31.8 | 80 | 77.8 | 79.8 | 102.4 | 2.93 | 3.75 | 3 | 6.2 | 0.031 | 19.9 | 18.8 | 0.78285 | 66.2 | 92.8 | 0.179 | 0.0325 | 14.98 | 13.89 | 14.87 | 0.98 | 0 | 0 | 0 | 2.8829 | 30.04 | 7.2 | 10.4 | 2020-08-05
2020-08-06 | Click Here |  | 6.28 | 5.08 | 5.13 | 5.15 | 5.13 | 7.22 | 7.48 | 1.73 | 1.89 | 2.17 | 2.14 | 38 | 33 | 12 | 0 | 0 | 0 | 0.613 | 0.658 | 0.347 | 0.091 | 0.116 | 0.084 | 16.1 | 41.3 | 38.7 | 39.6 | 48.3 | 32.2 | 82.6 | 77.4 | 79.2 | 96.6 | 2.95 | 3.79 | 3 | 6.3 | 0.034 | 19.9 | 18.9 | 0.78371 | 65.8 | 92.4 | 0.1794 | 0.0321 | 16.48 | 15.46 | 16.4 | 0.94 | 0 | 0 | 0 | 2.9137 | 0 | 7.2 | 10.4 | 2020-08-06
2020-08-07 | Click Here |  | 5.89 | 5.09 | 5.13 | 5.19 | 5.2 | 6.74 | 6.7 | 1.65 | 1.84 | 2.04 | 2.11 | 59 | 51 | 17 | 1 | 0 | 0 | 0.507 | 0.594 | 0.695 | 0.113 | 0.139 | 0.152 | 16.1 | 40.8 | 36.6 | 37.4 | 49.2 | 32.2 | 81.6 | 73.2 | 74.8 | 98.4 | 3.01 | 3.79 | 2.9 | 6.2 | 0.047 | 20.1 | 19 | 0.82166 | 63.7 | 92.6 | 0.1912 | 0.0317 | 16.99 | 15.96 | 16.94 | 0.98 | 0 | 0 | 0 | 2.9317 | 29.5 | 7.2 | 10.4 | 2020-08-07
2020-08-08 | Click Here |  | 5.94 | 5.06 | 5.13 | 5.19 | 5.24 | 6.79 | 6.62 | 1.7 | 1.96 | 2.12 | 2.17 | 60 | 52 | 16 | 1 | 0 | 0 | 0.417 | 0.654 | 0.591 | 0.094 | 0.192 | 0.504 | 16.3 | 39.9 | 36 | 36.8 | 47.4 | 32.6 | 79.8 | 72 | 73.6 | 94.8 | 2.93 | 3.91 | 3.1 | 5.1 | 0.071 | 20.1 | 19 | 0.87947 | 63.4 | 93 | 0.1929 | 0.0297 | 15.94 | 14.92 | 15.88 | 0.96 | 0 | 0 | 0 | 3.0195 | 29.62 | 7.2 | 10.4 | 2020-08-08
2020-08-09 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-08-09
2020-08-10 | Click Here |  | 5.73 | 4.93 | 4.98 | 4.84 | 4.89 | 6.29 | 6.3 | 1.75 | 1.89 | 2.2 | 2.22 | 33 | 26 | 14 | 3 | 0 | 0 | 0.423 | 0.51 | 0.688 | 0.098 | 0.332 | 0.234 | 17.3 | 42.6 | 41.9 | 40.8 | 45.5 | 34.6 | 85.2 | 83.8 | 81.6 | 91 | 2.74 | 3.82 | 3.1 | 5.6 | 0.019 | 22.6 | 19.9 | 0.72222 | 67 | 89.2 | 0.1739 | 0.0493 | 16.01 | 14.92 | 15.93 | 1.01 | 0 | 0 | 0 | 2.9522 | 30.04 | 7.2 | 10.4 | 2020-08-10
2020-08-11 | Click Here |  | 5.75 | 4.86 | 4.95 | 4.93 | 4.98 | 6.51 | 6.66 | 1.7 | 1.89 | 2.16 | 2.21 | 36 | 28 | 11 | 0 | 0 | 0 | 0.466 | 0.592 | 0.667 | 0.094 | 0.242 | 0.178 | 17.6 | 43 | 42.3 | 41.5 | 46.3 | 35.2 | 86 | 84.6 | 83 | 92.6 | 2.79 | 3.73 | 3 | 5.8 | 0 | 22.9 | 20.1 | 0.87444 | 66.9 | 90.1 | 0.1743 | 0.0481 | 16.82 | 15.8 | 16.75 | 0.95 | 0 | 0 | 0 | 3.1044 | 29.57 | 7.2 | 11 | 2020-08-11
2020-08-12 | Click Here |  | 5.86 | 5.01 | 4.98 | 5.04 | 5.09 | 6.79 | 6.88 | 1.72 | 1.9 | 2.2 | 2.26 | 37 | 30 | 12 | 1 | 0 | 0 | 0.423 | 0.586 | 0.681 | 0.104 | 0.149 | 0.175 | 17.8 | 44 | 42.7 | 44.2 | 50.7 | 35.6 | 88 | 85.4 | 88.4 | 101.4 | 2.8 | 3.85 | 3.2 | 6 | 0.029 | 23.5 | 20.5 | 0.81547 | 64.9 | 90.8 | 0.1852 | 0.0447 | 16.51 | 15.45 | 16.4 | 0.95 | 0 | 0 | 0 | 3.0455 | 30.36 | 7.2 | 11 | 2020-08-12
2020-08-13 | Click Here |  | 5.89 | 5.04 | 5 | 5 | 4.99 | 6.79 | 6.82 | 1.67 | 1.88 | 2.15 | 2.27 | 37 | 30 | 14 | 1 | 0 | 0 | 0.541 | 0.665 | 0.526 | 0.101 | 0.186 | 0.173 | 17.6 | 43.8 | 42.5 | 41.9 | 47.4 | 35.2 | 87.6 | 85 | 41.9 | 47.4 | 2.94 | 3.66 | 2.9 | 6.1 | 0.074 | 23.1 | 20.3 | 0.76365 | 66.5 | 91.2 | 0.1766 | 0.0396 | 16.63 | 15.56 | 16.54 | 0.98 | 0 | 0 | 0 | 3.0237 | 29.56 | 7.2 | 11 | 2020-08-13
2020-08-14 | Click Here |  | 6.23 | 4.86 | 5.01 | 4.89 | 4.91 | 6.53 | 6.91 | 1.7 | 1.91 | 2.17 | 2.29 | 39 | 32 | 16 | 1 | 0 | 0 | 0.614 | 0.683 | 0.611 | 0.113 | 0.344 | 0.321 | 17.4 | 42.8 | 42.2 | 42.3 | 49 | 34.8 | 85.6 | 84.4 | 84.6 | 98 | 2.97 | 3.78 | 3 | 6 | 0.052 | 22.8 | 20.5 | 0.76699 | 66.7 | 91.4 | 0.1764 | 0.0394 | 15.36 | 14.22 | 15.22 | 1 | 0 | 0 | 0 | 3.027 | 29.56 | 7.2 | 11 | 2020-08-14
2020-08-15 | Click Here |  | 6.33 | 4.83 | 5.08 | 4.86 | 4.85 | 6.58 | 6.75 | 1.63 | 1.9 | 2.14 | 2.27 | 38 | 32 | 14 | 0 | 0 | 0 | 0.611 | 0.624 | 0.593 | 0.109 | 0.173 | 0.158 | 16.5 | 40.1 | 39.8 | 40 | 48 | 33 | 80.2 | 79.6 | 80 | 96 |  |  | 3.1 | 5.9 | 0.067 | 20.2 | 19.8 | 0.96444 | 66.9 | 91.2 | 0.1762 | 0.0396 | 14.9 | 13.08 | 14.05 | 0.97 | 0 | 0 | 0 | 3.2144 | 29.13 | 7.4 | 11.3 | 2020-08-15
2020-08-16 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-08-16
2020-08-17 | Click Here |  | 5.9 | 4.9 | 5.06 | 4.96 | 4.96 | 6.4 | 7.49 | 1.74 | 1.92 | 2.2 | 2.17 | 28 | 21 | 13 | 0 | 0 | 0 | 0.471 | 0.53 | 0.534 | 0.094 | 0.309 | 0.14 | 16.8 | 40.6 | 40.2 | 41.6 | 49 | 33.6 | 81.2 | 80.4 | 83.2 | 98 |  |  | 3 | 6 | 0.014 | 20.8 | 20 | 0.94679 | 67.2 | 92.2 | 0.1725 | 0.0351 | 15.93 | 14.87 | 15.82 | 0.95 | 0 | 0 | 0 | 3.0968 | 29.57 | 7.6 | 11.5 | 2020-08-17
2020-08-18 | Click Here |  | 5.72 | 4.88 | 5.06 | 4.92 | 4.74 | 6.68 | 6.53 | 1.69 | 1.78 | 2.12 | 2.06 | 32 | 25 | 18 | 2 | 0 | 0 | 0.447 | 0.599 | 0.686 | 0.097 | 0.286 | 0.437 | 17.2 | 41.4 | 40.9 | 41.9 | 49.6 | 34.4 | 82.8 | 81.8 | 83.8 | 99.2 |  |  | 3.1 | 5.8 | 0.027 | 21.3 | 19.9 | 0.85615 | 66.9 | 91.9 | 0.1743 | 0.0364 | 15.18 | 14.08 | 15.04 | 0.96 | 0 | 0 | 0 | 2.9861 | 29.57 | 7.6 | 11.5 | 2020-08-18
2020-08-19 | Click Here |  | 6.42 | 4.97 | 4.92 | 5 | 4.99 | 6.7 | 6.56 | 1.7 | 1.84 | 2.13 | 2.18 | 35 | 27 | 20 | 3 | 1 | 0 | 0.766 | 0.814 | 0.833 | 0.116 | 0.193 | 0.224 | 18 | 40.5 | 39.9 | 40.3 | 48 | 36 | 81 | 79.8 | 80.6 | 96 |  |  | 3 | 5.7 | 0.037 | 20.5 | 19.7 | 0.73213 | 66.5 | 91.6 | 0.1747 | 0.0367 | 14.72 | 13.64 | 14.6 | 0.96 | 0 | 0 | 0 | 2.8621 | 29.48 | 7.6 | 11.5 | 2020-08-19
2020-08-20 | Click Here |  | 6.27 | 4.86 | 4.99 | 4.91 | 4.92 | 6.36 | 7.03 | 1.67 | 1.81 | 2.1 | 2.14 | 43 | 36 | 22 | 2 | 0 | 0 | 1.973 | 2.156 | 0.851 | 0.114 | 0.206 | 0.234 | 16.7 | 41.3 | 40.3 | 40.1 | 46.4 | 33.4 | 82.6 | 80.6 | 80.2 | 92.8 |  |  | 3.1 | 5.4 | 0.081 | 21.3 | 19.7 | 0.98169 | 59.7 | 90.1 | 0.2148 | 0.0481 | 14.1 | 12.91 | 13.91 | 1 | 0 | 0 | 0 | 3.1017 | 29.16 | 7.8 | 11.8 | 2020-08-20
2020-08-21 | Click Here |  | 5.69 | 4.84 | 5.05 | 4.88 | 4.97 | 6.52 | 7.16 | 1.74 | 1.91 | 2.2 | 2.16 | 37 | 30 | 11 | 0 | 0 | 0 | 1.26 | 1.47 | 0.462 | 0.091 | 0.411 | 0.53 | 19.3 | 39.6 | 38.7 | 39.2 | 46.8 | 38.6 | 79.2 | 77.4 | 78.4 | 93.6 |  |  | 3 | 5.9 | 0.003 | 19.8 | 19.9 | 0.21653 | 66.9 | 91.6 | 0.1744 | 0.0377 | 15 | 14.01 | 14.96 | 0.95 | 0 | 0 | 0 | 2.2865 | 30.04 | 7.8 | 12.2 | 2020-08-21
2020-08-22 | Click Here |  | 5.82 | 4.96 | 4.84 | 4.97 | 5.01 | 6.38 | 6.4 | 1.75 | 1.91 | 2.18 | 2.11 | 36 | 29 | 10 | 0 | 0 | 0 | 0.851 | 1.057 | 0.454 | 0.111 | 0.353 | 0.247 | 16.5 | 40.3 | 38.6 | 39.1 | 45.9 | 33 | 80.6 | 77.2 | 78.2 | 91.8 |  |  | 3 | 6 | 0.021 | 19.9 | 19.3 |  | 70.9 | 91.2 | 0.1488 | 0.0398 | 13.23 | 11.94 | 12.89 | 0.97 | 0 | 0 | 0 |  | 29.57 | 7.8 | 12.2 | 2020-08-22
2020-08-23 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-08-23
2020-08-24 | Click Here |  | 6.36 | 4.9 | 4.82 | 4.86 | 4.91 | 6.38 | 6.4 | 1.73 | 1.9 | 2.16 | 2.14 | 40 | 32 | 14 | 1 | 0 | 0 | 0.841 | 0.927 | 0.632 | 0.11 | 0.313 | 0.296 | 16.6 | 40.1 | 38.8 | 38.9 | 44.8 | 33.2 | 80.2 | 77.6 | 77.8 | 89.6 |  |  | 3.1 | 5.8 | 0.023 | 19.4 | 19.2 | 1.1372 | 70.6 | 91 | 0.1491 | 0.04 | 15.49 | 14.49 | 15.42 | 0.89 | 0 | 0 | 0 | 3.2472 | 29.17 | 7.8 | 12.2 | 2020-08-24
2020-08-25 | Click Here |  | 6.27 | 4.96 | 4.94 | 4.9 | 4.89 | 6.59 | 6.79 | 1.74 | 1.93 | 2.14 | 2.12 | 43 | 35 | 19 | 3 | 1 | 0 | 0.993 | 1.05 | 0.814 | 0.126 | 0.336 | 0.293 | 16.6 | 39 | 36.8 | 38.7 | 47.6 | 33.2 | 78 | 73.6 | 77.4 | 95.2 |  |  | 3 | 5.9 | 0.058 | 19.6 | 19.1 | 0.99295 | 70.8 | 90.9 | 0.1693 | 0.0402 | 16.28 | 13.55 | 14.49 | 0.94 | 0 | 0 | 0 | 3.1029 | 27.86 | 7.8 | 12.6 | 2020-08-25
2020-08-26 | Click Here |  | 6 | 5 | 4.95 | 4.96 | 4.86 | 6.68 | 6.91 | 1.68 | 1.87 | 2.2 | 2.1 | 33 | 26 | 14 | 1 | 0 | 0 | 0.953 | 1.16 | 0.754 | 0.099 | 0.237 | 0.213 | 16.7 | 39.9 | 38.6 | 39.8 | 49.9 | 33.4 | 79.8 | 0 | 79.6 | 99.8 |  |  | 3.1 | 5.9 | 0.032 | 19.5 | 19.1 | 0.66817 | 68.2 | 92.2 | 0.1665 | 0.035 | 16.8 | 14.88 | 15.85 | 0.97 | 0 | 0 | 0 | 2.7582 | 29.57 | 7.8 | 12.8 | 2020-08-26
2020-08-27 | Click Here |  | 5.88 | 5.04 | 4.84 | 5.08 | 5.11 | 6.74 | 6.63 | 1.8 | 1.94 | 2.2 | 1.93 | 32 | 26 | 10 | 0 | 0 | 0 | 0.785 | 0.944 | 0.216 | 0.087 | 0.091 | 0.158 | 15.9 | 38.6 | 37.2 | 38 | 46.8 | 31.8 | 77.2 | 74.4 | 76 | 93.6 |  |  | 3 | 6 | 0.011 | 18.7 | 18.4 | 1.0417 | 69 | 92.5 | 0.161 | 0.0388 | 14.56 | 13.52 | 14.5 | 0.98 | 0 | 0 | 0 | 2.9617 | 29.34 | 7.8 | 12.8 | 2020-08-27
2020-08-28 | Click Here |  | 5.94 | 5.07 | 5.02 | 5.01 | 4.94 | 6.89 | 7.05 | 1.77 | 1.99 | 1.94 | 1.6 | 41 | 36 | 13 | 1 | 0 | 0 | 1.12 | 1.204 | 0.682 | 0.102 | 0.22 | 0.286 | 16.1 | 38.5 | 36.8 | 38.1 | 44.6 | 32.2 | 77 | 73.6 | 76.2 | 89.2 |  |  | 3.2 | 6 | 0.028 | 17.7 | 18.1 | 1.0304 | 60.1 | 89.3 | 0.2211 | 0.0488 | 13.85 | 13.37 | 13.37 | 0 | 0 | 0 | 0 | 2.9104 | 29.23 | 7.8 | 12.8 | 2020-08-28
2020-08-29 | Click Here |  | 6.04 | 5.1 | 5.03 | 5.06 | 4.98 | 7.59 | 7.63 | 1.86 | 2.01 | 2.04 | 2.08 | 40 | 32 | 14 | 1 | 0 | 0 | 0.946 | 1.02 | 0.719 | 0.113 | 0.209 | 0.276 | 15.9 | 39.1 | 36.4 | 37.6 | 44.4 | 31.8 | 78.2 | 72.8 | 75.2 | 88.8 |  |  | 3 | 5.9 | 0.07 | 17.6 | 18 | 1.0806 | 59.9 | 90.9 | 0.224 | 0.0428 | 12.96 | 11.87 | 12.83 | 0.96 | 0 | 0 | 0 | 3.1206 | 30.04 | 7.8 | 12.8 | 2020-08-29
2020-08-30 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-08-30
2020-08-31 | Click Here |  | 5.85 | 4.85 | 5.02 | 5.02 | 5.04 | 6.7 | 7.47 | 1.77 | 1.93 | 2.2 | 1.61 | 38 | 31 | 5 | 0 | 0 | 0 | 0.583 | 0.814 | 0.282 | 0.091 | 0.353 | 0.175 | 15.5 | 38.5 | 35.7 | 36.7 | 46.8 | 31 | 77 | 71.4 | 73.4 | 93.6 |  |  | 3 | 5.8 | 0.017 | 16.8 | 17 | 1.0419 | 62.7 | 90.1 | 0.2022 | 0.0451 | 13.88 | 12.75 | 13.74 | 0.99 | 0 | 0 | 0 | 3.0619 | 29.11 | 7.8 | 12.8 | 2020-08-31
2020-09-01 | Click Here |  | 6.09 | 4.95 | 4.81 | 4.96 | 5.02 | 6.42 | 6.5 | 1.75 | 1.89 | 2.2 | 1.98 | 36 | 29 | 7 | 0 | 0 | 0 | 0.651 | 0.853 | 0.396 | 0.093 | 0.365 | 0.203 | 15.6 | 39.4 | 36.6 | 35.5 | 42.7 | 31.2 | 78.8 | 73.2 | 71 | 85.4 |  |  | 3.1 | 5.9 | 0.019 | 16.6 | 17.5 | 0.91397 | 62.5 | 90.3 | 0.2034 | 0.0438 | 14.77 | 13.78 | 14.75 | 0.97 | 0 | 0 | 0 | 3.124 | 29.11 | 7.8 | 12.8 | 2020-09-01
2020-09-02 | Click Here |  | 6.14 | 4.94 | 4.89 | 4.96 | 5.04 | 6.76 | 6.81 | 1.77 | 1.91 | 2.15 | 2.22 | 40 | 32 | 10 | 0 | 0 | 0 | 0.916 | 1.031 | 0.426 | 0.101 | 0.359 | 0.207 | 15.8 | 39.6 | 36.7 | 35.3 | 41.9 | 31.6 | 79.2 | 73.4 | 70.6 | 83.8 |  |  | 3 | 5.7 | 0.022 | 16.6 | 17.4 | 0.8372 | 62.3 | 90.2 | 0.2036 | 0.0439 | 14.83 | 13.82 | 14.77 | 0.95 | 0 | 0 | 0 | 3.1872 | 0 | 8 | 13.2 | 2020-09-02
2020-09-03 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-09-03
2020-09-04 | Click Here |  | 6.41 | 4.87 | 4.81 | 4.94 | 5.01 | 6.75 | 6.41 | 1.75 | 1.9 | 2.13 | 2.22 | 44 | 36 | 12 | 0 | 0 | 0 | 1.316 | 1.482 | 0.514 | 0.106 | 0.318 | 0.418 | 16.6 | 41.2 | 39.4 | 36.9 | 41.9 | 33.2 | 82.4 | 78.8 | 73.8 | 83.8 |  |  | 3.1 | 5.8 | 0.038 | 18.5 | 17.2 | 0.95427 | 62.1 | 90.3 | 0.2039 | 0.0437 | 14.651 | 13.588 | 14.56 | 0.97 | 0 | 0 | 0 | 3.0943 | 30.13 | 8 | 13.2 | 2020-09-04
2020-09-05 | Click Here |  | 6.43 | 5.08 | 4.93 | 5.07 | 5.02 | 6.89 | 7.41 | 1.78 | 1.94 | 2.16 | 2.29 | 48 | 39 | 14 | 1 | 0 | 0 | 1.214 | 1.396 | 0.553 | 0.116 | 0.311 | 0.304 | 16.8 | 40 | 38.1 | 39.2 | 48.5 | 33.6 | 80 | 76.2 | 78.4 | 97 |  |  | 3 | 5.9 | 0.043 | 19.2 | 17.5 |  | 61.9 | 90.6 | 0.2041 | 0.0434 | 13.3 | 12.25 | 13.18 | 0.93 | 0 | 0 | 0 |  | 29.52 | 8.4 | 13.2 | 2020-09-05
2020-09-06 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.51489 | 0 | 0 | 0 | 0 | 12.92 | 12.76 | 12.76 | 0 | 0 | 0 | 0 | 3.0549 | 0 | 8.4 | 13 | 2020-09-06
2020-09-07 | Click Here |  | 6.27 | 5.1 | 5.08 | 5.12 | 5.07 | 7 | 7.13 | 1.77 | 2.01 | 2.19 | 2.63 | 44 | 36 | 15 | 0 | 0 | 0 | 1.3 | 1.012 | 0.498 | 0.098 | 0.326 | 0.436 | 16.6 | 39.7 | 38.3 | 39.1 | 48.7 | 33.2 | 79.4 | 76.6 | 78.2 | 97.4 |  |  | 3.1 | 6.1 | 0.061 | 19 | 17.3 | 0.83177 | 62.2 | 91.2 | 0.2017 | 0.0398 | 14.63 | 12.74 | 14.64 | 1.9 | 0 | 0 | 0 | 3.4118 | 29.32 | 8.4 | 13 | 2020-09-07
2020-09-08 | Click Here |  | 6.26 | 4.99 | 5.03 | 5.06 | 5.1 | 7.04 | 7.11 | 1.91 | 2.09 | 2.2 | 2.64 | 40 | 33 | 14 | 0 | 0 | 0 | 0.746 | 0.914 | 0.492 | 0.106 | 0.374 | 0.448 | 16.8 | 41 | 38.5 | 37.9 | 45 | 33.6 | 82 | 77 | 75.8 | 90 |  |  | 3.1 | 5.9 | 0.054 | 19.2 | 17.9 | 0.11159 | 60.1 | 90.6 | 0.2194 | 0.0428 | 15.21 | 15.08 | 15.08 | 0 | 0 | 0 | 0 | 2.7216 | 30.2 | 8.4 | 13 | 2020-09-08
2020-09-09 | Click Here |  | 6.39 | 4.88 | 4.99 | 4.9 | 4.95 | 6.68 | 6.79 | 1.87 | 2.04 | 2.2 | 2.51 | 40 | 34 | 13 | 0 | 0 | 0 | 0.912 | 0.963 | 0.471 | 0.111 | 0.363 | 0.436 | 17 | 41.6 | 38.7 | 38.6 | 43.6 | 34 | 83.2 | 77.4 | 77.2 | 87.2 | 2.86 | 3.81 | 3 | 6 | 0.044 | 19.4 | 17.7 | 0.87649 | 60.3 | 90.8 | 0.2116 | 0.0426 | 15.63 | 13.75 | 15.65 | 1.9 | 0 | 0 | 0 | 3.4065 | 29.41 | 8.4 | 13 | 2020-09-09
2020-09-10 | Click Here |  | 6.3 | 4.99 | 5.07 | 5.05 | 5.07 | 6.89 | 7.39 | 1.97 | 2.18 | 2.2 | 2.73 | 43 | 37 | 12 | 1 | 0 | 0 | 0.974 | 0.883 | 0.428 | 0.103 | 0.271 | 0.216 | 17 | 40.6 | 38.5 | 39.7 | 48.1 | 34 | 81.2 | 77 | 79.4 | 96.2 | 2.91 | 3.97 | 3 | 6.1 | 0.038 | 19.4 | 17.7 | 0.69023 | 60 | 91 | 0.2119 | 0.0423 | 15.37 | 14.3 | 15.28 | 0.98 | 0 | 0 | 0 | 3.2202 | 30.06 | 8.7 | 13.2 | 2020-09-10
2020-09-11 | Click Here |  | 5.75 | 4.92 | 5.07 | 4.9 | 4.95 | 6.33 | 7.07 | 1.65 | 1.87 | 2.2 | 2.27 | 40 | 33 | 11 | 0 | 0 | 0 | 0.745 | 0.905 | 0.881 | 0.102 | 0.366 | 0.23 | 16.9 | 40.6 | 37.9 | 37.6 | 45.1 | 33.8 | 81.2 | 75.8 | 75.2 | 90.2 | 2.86 | 3.74 | 3.1 | 5.8 | 0.031 | 18.9 | 17.5 | 0.54591 | 60.9 | 89.6 | 0.2148 | 0.0474 | 14.38 | 13.32 | 14.28 | 0.96 | 0 | 0 | 0 | 2.8559 | 30.04 | 8.7 | 13.2 | 2020-09-11
2020-09-12 | Click Here |  | 5.68 | 4.99 | 5.1 | 4.96 | 5.05 | 6.74 | 6.88 | 1.71 | 1.92 | 2.18 | 2.24 | 39 | 32 | 10 | 0 | 0 | 0 | 0.732 | 0.84 | 0.746 | 0.096 | 0.456 | 0.414 | 16.8 | 40.7 | 37.7 | 36.9 | 44.8 | 33.6 | 81.4 | 75.4 | 73.8 | 89.6 | 2.89 | 3.72 | 3 | 6 | 0.028 | 18.7 | 17.4 |  | 61.2 | 90.2 | 0.2124 | 0.0456 | 13.53 | 12.5 | 13.45 | 0.95 | 0 | 0 | 0 |  | 29.57 | 8.7 | 13.2 | 2020-09-12
2020-09-13 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-09-13
2020-09-14 | Click Here |  | 6.47 | 5.01 | 5.08 | 5.04 | 5.02 | 7.12 | 7.3 | 1.64 | 1.86 | 1.97 | 1.95 | 42 | 33 | 11 | 0 | 0 | 0 | 0.714 | 0.746 | 0.783 | 0.116 | 0.361 | 0.342 | 16.3 | 39.1 | 36.1 | 36.8 | 44.1 | 32.6 | 78.2 | 72.2 | 73.6 | 88.2 | 2.91 | 3.83 | 3.1 | 6 | 0.033 | 17.8 | 16.5 | -0.15922 | 61 | 90.5 | 0.2126 | 0.0459 | 15.14 | 13.26 | 15.18 | 1.92 | 0 | 0 | 0 | 1.8708 | 29.52 | 8.7 | 12.8 | 2020-09-14
2020-09-15 | Click Here |  | 6.87 | 5.08 | 5.08 | 5.11 | 5.2 | 7.06 | 6.83 | 1.73 | 1.96 | 2.18 | 2.27 | 41 | 34 | 13 | 1 | 0 | 0 | 0.736 | 0.784 | 0.799 | 0.113 | 0.248 | 0.226 | 15.6 | 38.4 | 35.4 | 34.3 | 41.3 | 31.2 | 76.8 | 70.8 | 68.6 | 82.6 | 2.87 | 3.91 | 3.1 | 6.1 | 0.027 | 16.1 | 16.3 | 0.96404 | 61.2 | 87 | 0.2124 | 0.0601 | 14.62 | 13.52 | 14.48 | 0.96 | 0 | 0 | 0 | 3.184 | 30.59 | 8.7 | 12.8 | 2020-09-15
2020-09-16 | Click Here |  | 6.23 | 5.1 | 5.09 | 5.17 | 5.31 | 6.35 | 6.64 | 1.86 | 2.02 | 2.2 | 2 | 39 | 32 | 10 | 0 | 0 | 0 | 0.597 | 0.803 | 1.17 | 0.105 | 1.15 | 0.793 | 15.4 | 38.8 | 34.8 | 34.5 | 40 | 30.8 | 77.6 | 69.6 | 69 | 80 | 2.78 | 3.8 | 3 | 5.9 | 0.033 | 15.5 | 15.9 | 0.70462 | 61 | 88.2 | 0.2128 | 0.0575 | 14.47 | 13.42 | 14.38 | 0.96 | 0 | 0 | 0 | 2.8346 | 30.04 | 8.7 | 12.8 | 2020-09-16
2020-09-17 | Click Here |  | 6.23 | 5.12 | 5.23 | 5.18 | 5.16 | 6.57 | 7.03 | 1.84 | 1.97 | 2.2 | 2.26 | 41 | 34 | 12 | 0 | 0 | 0 | 0.625 | 0.797 | 0.635 | 0.121 | 0.306 | 0.156 | 15.8 | 38 | 35.5 | 35.9 | 45.8 | 31.6 | 76 | 71 | 71.8 | 91.6 | 2.73 | 3.83 | 3.1 | 5.8 | 0.028 | 16.1 | 16.1 | 0.78712 | 61.3 | 90.1 | 0.2122 | 0.0457 | 13.86 | 12.77 | 13.72 | 0.95 | 0 | 0 | 0 | 3.0571 | 30.28 | 8.7 | 12.8 | 2020-09-17
2020-09-18 | Click Here |  | 6.17 | 5.19 | 5.07 | 5.2 | 5.14 | 6.74 | 6.6 | 1.84 | 2 | 2.19 | 2.25 | 44 | 36 | 14 | 0 | 0 | 0 | 1.09 | 1.316 | 0.607 | 0.129 | 0.297 | 0.311 | 16.2 | 37.6 | 35.4 | 35.7 | 46.1 | 32.4 | 0 | 70.8 | 71.4 | 92.2 | 2.91 | 3.84 | 3 | 5.9 | 0.034 | 16.2 | 16 | 0.82609 | 61 | 90.6 | 0.2139 | 0.0421 | 14.42 | 13.38 | 14.35 | 0.97 | 0 | 0 | 0 | 3.1261 | 30.36 | 8.7 | 12.8 | 2020-09-18
2020-09-19 | Click Here |  | 6.24 | 5.11 | 5.08 | 5.14 | 5.2 | 6.93 | 6.88 | 1.79 | 1.96 | 2.14 | 2.27 | 47 | 40 | 16 | 1 | 0 | 0 | 0.926 | 1.214 | 0.737 | 0.124 | 0.284 | 0.321 | 16.2 | 40.9 | 34.9 | 35.2 | 46 | 32.4 | 81.8 | 69.8 | 70.4 | 92 | 3.63 | 3.69 | 3.1 | 6 | 0.041 | 16 | 16.2 | 0.92938 | 61.1 | 90.9 | 0.213 | 0.0411 | 13.01 | 11.89 | 12.87 | 0.98 | 0 | 0 | 0 | 3.1994 | 29.76 | 8.7 | 12.8 | 2020-09-19
2020-09-20 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-09-20
2020-09-21 | Click Here |  | 6.2 | 5.06 | 5.04 | 5.16 | 5.25 | 6.34 | 6.22 | 1.9 | 2.05 | 2.2 | 2.2 | 42 | 35 | 11 | 0 | 0 | 0 | 0.844 | 0.835 | 0.641 | 0.139 | 0.381 | 0.427 | 14.9 | 37.1 | 35.6 | 33.7 | 40.6 | 29.8 | 74.2 | 71.2 | 67.4 | 81.2 | 2.8 | 3.65 | 3.1 | 5.9 | 0.038 | 14.3 | 15.2 |  | 64.5 | 89.3 | 0.1901 | 0.0489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30.04 | 8.7 | 12.8 | 2020-09-21
2020-09-22 | Click Here |  | 6.32 | 5.18 | 5.07 | 5.16 | 5.22 | 5.98 | 6.03 | 1.83 | 1.99 | 2.2 | 1.98 | 40 | 32 | 16 | 1 | 0 | 0 | 0.622 | 0.819 | 1.09 | 0.189 | 0.498 | 0.378 | 15.2 | 38.1 | 35.2 | 32.8 | 39.7 | 30.4 | 76.2 | 70.4 | 65.6 | 79.4 | 2.88 | 3.79 | 3 | 5.8 | 0.033 | 15.4 | 15.4 |  | 64.1 | 89.7 | 0.1917 | 0.0475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29.81 | 8.7 | 12.8 | 2020-09-22
2020-09-23 | Click Here |  | 6.24 | 5.12 | 5.18 | 5.29 | 5.34 | 6.47 | 6.05 | 1.86 | 2.04 | 2 | 2.06 | 46 | 40 | 19 | 2 | 0 | 0 | 0.594 | 0.723 | 1.26 | 0.107 | 0.361 | 0.388 | 15.2 | 37.8 | 37.4 | 34.3 | 40 | 30.4 | 75.6 | 74.8 | 68.6 | 80 | 3 | 3.89 | 2.9 | 5.8 | 0.047 | 14.8 | 15.2 | 0.69928 | 66.3 | 89.7 | 0.1781 | 0.0472 | 15.51 | 13.01 | 14.01 | 1 | 0 | 0 | 0 | 2.8493 | 30.08 | 8.7 | 12.8 | 2020-09-23
2020-09-24 | Click Here |  | 6.24 | 5.18 | 5.2 | 5.27 | 5.3 | 7.14 | 7.25 | 1.94 | 2.1 | 2.2 | 2.29 | 41 | 35 | 7 | 0 | 0 | 0 | 0.741 | 1.095 | 0.398 | 0.104 | 0.216 | 0.264 | 15.6 | 39.6 | 39 | 35 | 43.4 | 31.2 | 79.2 | 78 | 70 | 86.8 | 2.92 | 3.97 | 3 | 6.1 | 0.034 | 16.1 | 15.8 | 0.50805 | 65.9 | 91.9 | 0.1799 | 0.0364 | 15.39 | 14.36 | 15.36 | 1 | 0 | 0 | 0 | 2.8581 | 29.06 | 8.7 | 12.8 | 2020-09-24
2020-09-25 | Click Here |  | 6.67 | 5.22 | 5.66 | 5.12 | 5.21 | 6.82 | 7.2 | 1.86 | 2.03 | 2.18 | 2.22 | 42 | 34 | 9 | 0 | 0 | 0 | 0.314 | 0.963 | 0.401 | 0.131 | 0.161 | 0.176 | 15.4 | 39.9 | 38.9 | 35 | 46.1 | 30.8 | 79.8 | 77.8 | 70 | 92.2 | 2.97 | 4.11 | 3 | 6 | 0.048 | 16.1 | 15.3 |  | 65.7 | 91.6 | 0.18 | 0.0367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 8.7 | 12.8 | 2020-09-25
2020-09-26 | Click Here |  | 6.63 | 5.22 | 5.15 | 5.14 | 5.2 | 6.82 | 7.52 | 1.93 | 2.09 | 2.2 | 2.45 | 41 | 34 | 7 | 0 | 0 | 0 | 0.902 | 0.913 | 0.396 | 0.118 | 0.263 | 0.274 | 15 | 38.6 | 38.5 | 34.6 | 44.7 | 30 | 77.2 | 77 | 69.2 | 89.4 | 2.92 | 4.05 | 3 | 6.1 | 0.033 | 14.9 | 15.1 |  | 65.8 | 91.4 | 0.1799 | 0.0369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28.36 | 8.5 | 12.8 | 2020-09-26
2020-09-27 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.33297 | 0 | 0 | 0 | 0 | 13.65 | 13.46 | 13.46 | 0 | 0 | 0 | 0 | 2.693 | 0 | 8.5 | 12.8 | 2020-09-27
2020-09-28 | Click Here |  | 6.34 | 5.17 | 5.14 | 5.16 | 5.21 | 6.89 | 7.32 | 1.88 | 2.06 | 2.04 | 2.1 | 44 | 37 | 7 | 1 | 0 | 0 | 0.724 | 0.816 | 0.421 | 0.127 | 0.286 | 0.347 | 15.2 | 39.2 | 36.1 | 34.7 | 45.4 | 30.4 | 78.4 | 72.2 | 69.4 | 90.8 | 2.93 | 4.02 | 3.1 | 6 | 0.043 | 14.8 | 15.2 | 0.71782 | 66 | 91.7 | 0.169 | 0.0352 | 15.25 | 14.22 | 15.21 | 0.99 | 0 | 0 | 0 | 2.9778 | 29.54 | 8.5 | 12.8 | 2020-09-28
2020-09-29 | Click Here |  | 6.37 | 5.1 | 5.19 | 5.15 | 5.24 | 7.89 | 8.88 | 1.9 | 2.1 | 2.2 | 2.9 | 44 | 36 | 7 | 0 | 0 | 0 | 0.592 | 0.77 | 0.314 | 0.099 | 0.127 | 0.151 | 16.1 | 41.7 | 42.8 | 41 | 59.3 | 32.2 | 83.4 | 85.6 | 82 | 118.6 | 3.06 | 4.1 | 3.2 | 6.4 | 0.031 | 17.3 | 15.4 | 0.10818 | 64.6 | 92.2 | 0.1897 | 0.0349 | 14.89 | 13.85 | 14.78 | 0.93 | 0 | 0 | 0 | 3.1082 | 29.04 | 8.5 | 12.8 | 2020-09-29
2020-09-30 | Click Here |  | 6.2 | 5.13 | 5.19 | 5.2 | 5.14 | 5.94 | 5.16 | 1.98 | 2.1 | 2.2 | 3.02 | 42 | 34 | 7 | 0 | 0 | 0 | 0.671 | 0.849 | 0.424 | 0.123 | 0.137 | 0.069 | 15.8 | 41.3 | 42.6 | 41.8 | 55.4 | 31.6 | 82.6 | 85.2 | 83.6 | 110.8 | 3.13 | 3.99 | 3 | 5.8 | 0.046 | 17.4 | 15.4 | -0.093158 | 64.2 | 92.9 | 0.1918 | 0.0314 | 15.17 | 14.06 | 15.03 | 0.97 | 0 | 0 | 0 | 2.9868 | 29.74 | 8.5 | 12.8 | 2020-09-30
2020-10-01 | Click Here |  | 6.25 | 5.1 | 5.22 | 5.13 | 5.17 | 7.69 | 8.21 | 1.86 | 2.09 | 2.2 | 0 | 51 | 43 | 9 | 0 | 0 | 0 | 0.812 | 0.957 | 0.491 | 0.139 | 0.141 | 0.126 | 17.1 | 45.3 | 44.4 | 42.2 | 55 | 34.2 | 90.6 | 88.8 | 84.4 | 110 | 2.97 | 3.87 | 3 | 6.1 | 0.029 | 20.1 | 16.8 | 0.17727 | 65.9 | 91.1 | 0.1809 | 0.0404 | 15.13 | 14.13 | 15.1 | 0.97 | 0 | 0 | 0 | 3.1173 | 29.92 | 8.5 | 12.2 | 2020-10-01
2020-10-02 | Click Here |  | 6.3 | 5.29 | 5.28 | 5.51 | 5.55 | 8.88 | 8.19 | 1.68 | 1.83 | 2.2 | 2.83 | 35 | 27 | 20 | 0 | 0 | 0 | 0.786 | 0.921 | 0.333 | 0.098 | 0.173 | 0.163 | 16.9 | 44.9 | 45.2 | 42.3 | 61.4 | 33.8 | 89.8 | 90.4 | 84.6 | 122.8 | 2.85 | 3.68 | 3.1 | 5.9 | 0.214 | 19.3 | 16.7 | -0.1515 | 67.2 | 91.5 | 0.1721 | 0.0382 | 14.49 | 14.36 | 14.36 | 0 | 0 | 0 | 0 | 2.7885 | 29.57 | 8.5 | 11 | 2020-10-02
2020-10-03 | Click Here |  | 6.37 | 5.35 | 5.32 | 5.7 | 5.58 | 7.89 | 8.4 | 1.68 | 1.85 | 2.2 | 2.83 | 34 | 26 | 14 | 0 | 0 | 0 | 0.972 | 0.884 | 0.829 | 0.096 | 0.131 | 0.101 | 15.2 | 43.1 | 39.2 | 40.2 | 54 | 30.4 | 86.2 | 78.4 | 80.4 | 108 | 2.81 | 3.75 | 3 | 6 | 0.095 | 19.3 | 17.1 | 0.30213 | 67.4 | 91.3 | 0.1718 | 0.0388 | 13.32 | 12.17 | 13.17 | 1 | 0 | 0 | 0 | 3.0821 | 30.04 | 8 | 9 | 2020-10-03
2020-10-04 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.49759 | 0 | 0 | 0 | 0 | 14.17 | 13.07 | 14.04 | 0.97 | 0 | 0 | 0 | 3.0276 | 0 | 7.8 | 8 | 2020-10-04
2020-10-05 | Click Here |  | 6.27 | 5.21 | 5.28 | 5.24 | 5.29 | 7.47 | 7.53 | 1.82 | 2 | 2.2 | 2.55 | 37 | 29 | 16 | 0 | 0 | 0 | 0.674 | 0.788 | 0.341 | 0.09 | 0.101 | 0.04 | 16.5 | 43 | 37.8 | 38.8 | 52.6 | 33 | 86 | 75.6 | 77.6 | 105.2 | 2.92 | 3.81 | 3 | 6.1 | 0.141 | 17.5 | 16.5 | 0.65818 | 67 | 91 | 0.1752 | 0.0398 | 14.36 | 13.3 | 14.27 | 0.97 | 0 | 0 | 0 | 3.0582 | 29.38 | 7.8 | 8 | 2020-10-05
2020-10-06 | Click Here |  | 6.32 | 5.24 | 5.3 | 5.31 | 5.34 | 7.84 | 7.9 | 1.77 | 1.94 | 2.19 | 2.33 | 39 | 33 | 7 | 0 | 0 | 0 | 0.591 | 0.76 | 0.326 | 0.124 | 0.109 | 0.092 | 16.1 | 42.8 | 37.9 | 39.1 | 54.1 | 32.2 | 85.6 | 75.8 | 78.2 | 108.2 | 2.87 | 3.93 | 3 | 6.1 | 0.13 | 17.2 | 16.1 | 0.7422 | 66.7 | 91.1 | 0.1764 | 0.0404 | 14.91 | 13.81 | 14.79 | 0.98 | 0 | 0 | 0 | 2.9722 | 29.73 | 7.8 | 8 | 2020-10-06
2020-10-07 | Click Here |  | 6.64 | 5.81 | 5.31 | 5.82 | 5.86 | 6.92 | 7.68 | 1.67 | 1.88 | 2.2 | 2.05 | 33 | 27 | 15 | 0 | 0 | 0 | 0 | 0.696 | 0 | 0 | 0 | 0.088 | 15.6 | 37.9 | 35.6 | 37.5 | 50.7 | 31.2 | 75.8 | 71.2 | 75 | 101.4 | 2.81 | 3.73 | 3.1 | 5.9 | 0.011 | 15 | 15.5 | 0.54207 | 67 | 93.1 | 0.1737 | 0.0307 | 14.22 | 14.02 | 14.02 | 0 | 0 | 0 | 0 | 2.6421 | 29.81 | 7.8 | 8 | 2020-10-07
2020-10-08 | Click Here |  | 6.32 | 5.31 | 5.63 | 5.33 | 5.75 | 7.24 | 8.16 | 1.69 | 1.86 | 2.2 | 2.23 | 33 | 26 | 11 | 0 | 0 | 0 | 0 | 0.709 | 0 | 0 | 0 | 0.083 | 15.6 | 37.6 | 34.3 | 33.1 | 44.8 | 31.2 | 75.2 | 68.6 | 66.2 | 89.6 | 2.84 | 3.76 | 3 | 5.9 | 0.032 | 15.1 | 14.9 | 0.67353 | 66.4 | 92.5 | 0.1774 | 0.0339 | 13.77 | 12.59 | 13.58 | 0.99 | 0 | 0 | 0 | 2.8235 | 30.28 | 6.7 | 8.5 | 2020-10-08
2020-10-09 | Click Here |  | 6.25 | 5.11 | 5.09 | 5.27 | 5.39 | 7.31 | 7.76 | 1.72 | 1.91 | 2.07 | 2.12 | 35 | 27 | 9 | 0 | 0 | 0 | 0 | 0.812 | 0 | 0 | 0 | 0.084 | 15.2 | 37.5 | 34.3 | 34.8 | 46.9 | 30.4 | 75 | 68.6 | 69.6 | 93.8 | 2.93 | 3.83 | 3.1 | 5.9 | 0.047 | 14.8 | 14.7 | 0.75592 | 66.9 | 92.9 | 0.1757 | 0.0313 | 14.27 | 13.15 | 14.13 | 0.98 | 0 | 0 | 0 | 2.8859 | 29.82 | 6.7 | 8.7 | 2020-10-09
2020-10-10 | Click Here |  | 6.32 | 5.14 | 5.08 | 5.3 | 5.36 | 7.42 | 7.39 | 1.76 | 2.07 | 2.12 | 2.04 | 39 | 32 | 9 | 0 | 0 | 0 | 0 | 0.835 | 0 | 0 | 0 | 0.15 | 14.3 | 36.1 | 32.3 | 33 | 44.9 | 28.6 | 72.2 | 64.6 | 66 | 89.8 | 2.86 | 3.81 | 2.9 | 5.8 | 0.026 | 13.1 | 14 | 0.86633 | 68.2 | 92 | 0.1658 | 0.0361 | 13.57 | 12.4 | 13.39 | 0.99 | 0 | 0 | 0 | 2.9063 | 30.08 | 6.7 | 8.7 | 2020-10-10
2020-10-11 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-10-11
2020-10-12 | Click Here |  | 6.32 | 5.39 | 5.06 | 5.37 | 5.43 | 7.17 | 7.35 | 1.77 | 1.96 | 2.19 | 1.95 | 39 | 32 | 15 | 0 | 0 | 0 | 0 | 1.153 | 0 | 0 | 0 | 0.128 | 13.9 | 36.7 | 31.9 | 33 | 44.3 | 27.8 | 73.4 | 63.8 | 66 | 88.6 | 2.78 | 3.69 | 3 | 5.9 | 0.031 | 11.8 | 13.1 | 0.42243 | 67.9 | 92.7 | 0.1677 | 0.0325 | 14.32 | 13.18 | 14.17 | 0.99 | 0 | 0 | 0 | 2.5824 | 29.81 | 6.7 | 8.7 | 2020-10-12
2020-10-13 | Click Here |  | 6.34 | 5.4 | 5.53 | 5.45 | 5.5 | 7.22 | 7.27 | 1.81 | 1.95 | 2.2 | 2.27 | 37 | 30 | 10 | 0 | 0 | 0 | 0 | 0.985 | 0 | 0 | 0 | 0.16 | 14.4 | 38.3 | 31.6 | 32.7 | 42.6 | 28.8 | 76.6 | 63.2 | 65.4 | 83.2 | 2.69 | 3.58 | 3.1 | 5.9 | 0.034 | 12.9 | 13 | 0.80695 | 68.2 | 93.1 | 0.166 | 0.031 | 14.33 | 13.07 | 14.05 | 0.98 | 0 | 0 | 0 | 2.987 | 29.57 | 6.7 | 7.8 | 2020-10-13
2020-10-14 | Click Here |  | 6.52 | 5.44 | 5.38 | 5.54 | 5.66 | 7.54 | 7.7 | 1.79 | 1.97 | 2.17 | 2.22 | 42 | 36 | 14 | 0 | 0 | 0 | 0 | 0.922 | 0 | 0 | 0 | 0.063 | 14.2 | 37.5 | 32 | 33.8 | 45.4 | 28.4 | 75 | 64 | 67.6 | 90.8 | 2.78 | 3.86 | 3.1 | 6 | 0.07 | 12.5 | 12.8 | 0.66977 | 68 | 92.6 | 0.1662 | 0.033 | 14.7 | 13.56 | 14.53 | 0.97 | 0 | 0 | 0 | 2.8998 | 30.08 | 6.7 | 8 | 2020-10-14
2020-10-15 | Click Here |  | 6.24 | 5.3 | 5.4 | 5.34 | 5.48 | 7.01 | 7.13 | 1.77 | 2.01 | 2.16 | 2.27 | 39 | 33 | 17 | 1 | 0 | 0 | 0 | 0.951 | 0 | 0 | 0 | 0.093 | 14.9 | 38.3 | 32.5 | 33.1 | 42.6 | 29.8 | 76.6 | 65 | 66.2 | 85.2 | 2.79 | 3.73 | 3.1 | 5.9 | 0.062 | 12.9 | 12.5 | 0.72624 | 65.9 | 91.2 | 0.1809 | 0.0397 | 14.34 | 13.18 | 14.15 | 0.96 | 0 | 0 | 0 | 2.8862 | 29.99 | 6.5 | 8 | 2020-10-15
2020-10-16 | Click Here |  | 6.59 | 5.3 | 5.41 | 5.33 | 5.48 | 6.94 | 7.11 | 1.73 | 1.96 | 2.11 | 2.14 | 41 | 34 | 15 | 1 | 0 | 0 | 0.963 | 0.773 | 0.841 | 0.106 | 0.163 | 0.116 | 14.8 | 36.3 | 32.6 | 33 | 44.4 | 29.6 | 72.6 | 65.2 | 66 | 88.8 | 2.81 | 3.84 | 3 | 5.8 | 0.058 | 13 | 12.6 | 0.84493 | 67.8 | 91.4 | 0.1664 | 0.0395 | 14.25 | 13.06 | 14.04 | 0.98 | 0 | 0 | 0 | 2.9249 | 28.93 | 6.5 | 8.6 | 2020-10-16
2020-10-17 | Click Here |  | 6.9 | 5.38 | 5.35 | 5.37 | 5.5 | 6.73 | 6.45 | 1.7 | 1.91 | 2.04 | 2.08 | 42 | 35 | 14 | 0 | 0 | 0 | 0 | 0.773 | 0 | 0 | 0 | 0.106 | 15.1 | 35.9 | 31.7 | 31.8 | 41.9 | 30.2 | 71.8 | 63.4 | 63.6 | 83.8 | 2.87 | 3.88 | 3.1 | 5.9 | 0.074 | 13.6 | 12.7 | 0.81116 | 67.9 | 91 | 0.1662 | 0.0399 | 13.64 | 12.48 | 13.45 | 0.97 | 0 | 0 | 0 | 2.9012 | 29.14 | 6.2 | 8.6 | 2020-10-17
2020-10-18 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.8878 | 0 | 0 | 0 | 0 | 14.46 | 13.24 | 14.25 | 0.99 | 0 | 0 | 0 | 2.9678 | 0 | 5.6 | 9 | 2020-10-18
2020-10-19 | Click Here |  | 6.84 | 5.3 | 5.29 | 5.3 | 5.49 | 6.95 | 7.02 | 1.73 | 2 | 2.07 | 2.1 | 41 | 33 | 13 | 0 | 0 | 0 | 0 | 0.76 | 0 | 0 | 0 | 0.076 | 15.8 | 37.6 | 33.3 | 32.1 | 41.2 | 31.6 | 75.2 | 66.6 | 64.2 | 82.4 | 2.88 | 3.86 | 2.9 | 5.8 | 0.062 | 14.5 | 13.2 | 0.89939 | 65.2 | 91.2 | 0.1857 | 0.0398 | 15.17 | 14 | 14.98 | 0.98 | 0 | 0 | 0 | 2.8894 | 29.43 | 5.6 | 9 | 2020-10-19
2020-10-20 | Click Here |  | 6.74 | 5.19 | 5.25 | 5.26 | 5.32 | 7.01 | 7.12 | 1.77 | 2.04 | 2.09 | 2.16 | 40 | 32 | 19 | 0 | 0 | 0 | 0 | 0.72 | 0 | 0 | 0 | 0.059 | 16.1 | 38.1 | 33.4 | 33.7 | 43 | 32.2 | 76.2 | 66.8 | 67.4 | 86 | 2.87 | 3.81 | 2.9 | 5.8 | 0.072 | 14.6 | 13.5 | 1.145 | 66 | 91.6 | 0.1802 | 0.0381 | 14.68 | 13.48 | 14.46 | 0.97 | 0 | 0 | 0 | 3.045 | 29.97 | 5.3 | 9 | 2020-10-20
2020-10-21 | Click Here |  | 6.67 | 5.31 | 5.28 | 5.38 | 5.41 | 6.74 | 8.07 | 1.71 | 1.84 | 1.93 | 1.89 | 41 | 34 | 18 | 2 | 1 | 0 | 0 | 0.734 | 0 | 0 | 0 | 0.056 | 16.1 | 38.6 | 34.2 | 34.7 | 44.4 | 32.2 | 77.2 | 68.4 | 69.4 | 88.8 | 2.92 | 3.8 | 3 | 5.9 | 0.063 | 15.5 | 13.5 | 1.031 | 66.4 | 91.2 | 0.18 | 0.0385 | 15.07 | 13.92 | 14.9 | 0.98 | 0 | 0 | 0 | 2.921 | 28.38 | 5.6 | 9 | 2020-10-21
2020-10-22 | Click Here |  | 6.51 | 5.16 | 5.13 | 5.2 | 5.28 | 6.86 | 7.34 | 1.67 | 1.82 | 1.97 | 2.02 | 42 | 34 | 19 | 1 | 0 | 0 | 1.01 | 0.741 | 1.18 | 0.165 | 0.556 | 0.406 | 16.1 | 36.1 | 33.2 | 32.6 | 40.7 | 32.2 | 72.2 | 66.4 | 65.2 | 81.4 | 2.88 | 3.93 | 3 | 5.7 | 0.081 | 14.7 | 13 | 1.2444 | 66 | 88.2 | 0.1803 | 0.0544 | 15.52 | 13.5 | 15.42 | 1.92 | 0 | 0 | 0 | 3.1144 | 29.04 | 4.8 | 9.3 | 2020-10-22
2020-10-23 | Click Here |  | 6.07 | 5.18 | 5.15 | 5.18 | 5.25 | 6.79 | 6.56 | 1.72 | 1.81 | 2.05 | 1.95 | 39 | 32 | 15 | 0 | 0 | 0 | 0.834 | 0.86 | 1.58 | 0.134 | 0.585 | 0.475 | 15.3 | 37.1 | 32.5 | 32.4 | 41 | 30.6 | 74.2 | 65 | 64.8 | 82 | 2.8 | 3.79 | 3.1 | 5.9 | 0.066 | 13.4 | 12.9 | 0.75338 | 64.8 | 90.2 | 0.1879 | 0.0448 | 15.01 | 13.79 | 14.78 | 0.99 | 0 | 0 | 0 | 2.6134 | 29.11 | 5.5 | 10.3 | 2020-10-23
2020-10-24 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-10-24
2020-10-25 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-10-25
2020-10-26 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-10-26
2020-10-27 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-10-27
2020-10-28 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-10-28
2020-10-29 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-10-29
2020-10-30 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-10-30
2020-10-31 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-10-31
2020-11-01 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-01
2020-11-02 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-02
2020-11-03 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-03
2020-11-04 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-04
2020-11-05 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-05
2020-11-06 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-06
2020-11-07 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-07
2020-11-08 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-08
2020-11-09 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-09 |  | 0.28109 | 55.7 | 89.8 | 0.2547 | 0.0476 | 14.38 | 14.16 | 14.16 | 0 | 1.507 | 2.847 | 9.807 | 2.4611 | 30.39 | 5
2020-11-10 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-10 |  | 0.87916 | 62 | 91.3 | 0.2077 | 0.0394 | 13.46 | 12.43 | 13.42 | 0.99 | 1.444 | 2.68 | 8.444 | 3.0692 | 29.58 | 5
2020-11-11 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-11 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
2020-11-12 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-12 |  | 0.67099 | 61.5 | 89.1 | 0.2131 | 0.0497 | 14.38 | 13.25 | 14.25 | 1 | 1.537 | 3.076 | 7.41 | 2.871 | 31.45 | 5
2020-11-13 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-13 |  | 0.65843 | 61.8 | 89.4 | 0.2086 | 0.0483 | 14.24 | 13.17 | 14.12 | 0.95 | 1.541 | 2.88 | 7.003 | 2.8884 | 31.22 | 5
2020-11-14 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-14 |  |  | 62.1 | 90.6 | 0.2058 | 0.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30.1 | 5
2020-11-15 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-15 |  | 1.0158 | 60.4 | 89 | 0.2187 | 0.0502 | 14.81 | 13.3 | 14.77 | 1.47 | 1.467 | 2.791 | 7.216 | 3.0858 | 30.48 | 5
2020-11-16 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-16 |  | 0.34981 | 60.6 | 90.8 | 0.2185 | 0.0418 | 15.47 | 14.13 | 15.59 | 1.46 | 1.489 | 2.815 | 9.385 | 2.4798 | 32.41 | 5
2020-11-17 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-17 |  | 0.73536 | 60.2 | 90.4 | 0.2188 | 0.042 | 14.68 | 13.7 | 14.67 | 0.97 | 0 | 0 | 0 | 2.7754 | 31.43 | 5
2020-11-18 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-18 |  | 0.76841 | 0 | 0 | 0 | 0 | 14.95 | 13.93 | 14.87 | 0.94 | 1.436 | 2.805 | 9.777 | 2.8084 | 0 | 5
2020-11-19 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-19 |  | 0.7073 | 60.6 | 90.6 | 0.2139 | 0.0409 | 15.42 | 14.47 | 15.41 | 0.94 | 1.498 | 2.798 | 10 | 2.7673 | 30.69 | 5
2020-11-20 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-20 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
2020-11-21 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-21 |  | 0.76216 | 60.2 | 90.8 | 0.2141 | 0.0407 | 15.29 | 14.29 | 15.28 | 0.99 | 1.514 | 2.791 | 10 | 2.8022 | 31.9 | 5
2020-11-22 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-22 |  | 0.92429 | 60.6 | 89 | 0.2139 | 0.0504 | 14.93 | 13.98 | 14.91 | 0.93 | 1.473 | 2.792 | 9.821 | 2.8643 | 30.38 | 5
2020-11-23 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-23 |  | 0.85772 | 60 | 90.6 | 0.2144 | 0.0413 | 14.21 | 13.24 | 14.17 | 0.93 | 1.412 | 2.785 | 8.823 | 2.7977 | 30.04 | 4.8
2020-11-24 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-24 |  | 0.7895 | 56.6 | 90.4 | 0.2472 | 0.0437 | 14.5 | 13.54 | 14.48 | 0.94 | 1.47 | 2.673 | 9.673 | 2.8095 | 30.28 | 4.8
2020-11-25 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-25 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
2020-11-26 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-26 |  | 0.73861 | 56.9 | 90.1 | 0.2469 | 0.044 | 14.69 | 13.74 | 14.68 | 0.94 | 1.504 | 2.711 | 9.307 | 2.7686 | 30.19 | 4.8
2020-11-27 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-27 |  | 0.78455 | 56.7 | 90.4 | 0.247 | 0.0439 | 13.87 | 12.85 | 13.8 | 0.95 | 1.455 | 2.719 | 8.417 | 2.8046 | 30.31 | 4.8
2020-11-28 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-28 |  | 0.78473 | 54.7 | 89.6 | 0.2618 | 0.0473 | 14.16 | 13.16 | 14.11 | 0.95 | 1.417 | 2.715 | 8.464 | 2.8147 | 30.04 | 4.8
2020-11-29 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-29 |  | 0.72533 | 58.8 | 90.1 | 0.2326 | 0.0447 | 13.555 | 12.488 | 13.45 | 0.962 | 1.37 | 2.713 | 8.221 | 2.7953 | 30.51 | 4.8
2020-11-30 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-11-30
2020-12-01 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-12-01
2020-12-02 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-12-02
2020-12-03 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-12-03
2020-12-04 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-12-04
2020-12-05 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-12-05
2020-12-06 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-12-06
2020-12-07 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-12-07
2020-12-08 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-12-08
2020-12-09 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-12-09
2020-12-10 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2020-12-10 |  |  | 76.76
2020-12-11 | Click Here |  | 5.93 | 5.12 | 5.06 | 5.29 | 5.53 | 7.1 | 7 | 1.89 | 2.06 | 2.09 | 2.12 | 38 | 30 | 10 | 0 | 0 | 0 | 0.596 | 0.617 | 0.682 | 0.081 | 0.467 | 0.524 | 14 | 34.7 | 28.8 | 29.2 | 38 | 28 | 69.4 | 57.6 | 58.4 | 76 | 3.25 | 4.02 | 3 | 5.9 | 0.034 | 8.3 | 6.6 | 0.28109 | 55.7 | 89.8 | 0.2547 | 0.0476 | 14.38 | 14.16 | 14.16 | 0 | 1.507 | 2.847 | 9.807 | 2.4611 | 30.39 | 5 |  | 1900-01-09 19:12 |  |  | 84.03
2020-12-12 | Click Here |  | 6 | 5.1 | 5.02 | 5.24 | 5.29 | 6.84 | 6.62 | 1.94 | 2.07 | 2.15 | 2.28 | 37 | 30 | 13 | 0 | 0 | 0 | 0.587 | 0.607 | 0.714 | 0.102 | 0.391 | 0.486 | 13.4 | 35.8 | 28.7 | 29.1 | 33.8 | 26.8 | 71.6 | 57.4 | 58.2 | 67.6 | 3.14 | 3.92 | 3.2 | 6.1 | 0.049 | 8 | 6.3 | 0.87916 | 62 | 91.3 | 0.2077 | 0.0394 | 13.46 | 12.43 | 13.42 | 0.99 | 1.444 | 2.68 | 8.444 | 3.0692 | 29.58 | 5 |  | 1900-01-09 19:12 |  |  | 0
2020-12-13 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 83.79
2020-12-14 | Click Here |  | 5.99 | 5.21 | 5.1 | 5.32 | 5.36 | 8.05 | 8.38 | 1.89 | 2.03 | 2.2 | 2.14 | 37 | 30 | 15 | 2 | 0 | 0 | 0.593 | 0.604 | 0.891 | 0.079 | 0.086 | 0.179 | 12.6 | 36 | 27.4 | 28.2 | 43.4 | 25.2 | 72 | 54.8 | 56.4 | 86.8 | 2.64 | 3.88 | 3.1 | 5.9 | 0.207 | 6 | 5.9 | 0.67099 | 61.5 | 89.1 | 0.2131 | 0.0497 | 14.38 | 13.25 | 14.25 | 1 | 1.537 | 3.076 | 7.41 | 2.871 | 31.45 | 5 |  | 1900-01-09 19:12 |  |  | 83.79
2020-12-15 | Click Here |  | 6.02 | 5.24 | 5.23 | 5.34 | 5.41 | 7.96 | 8.09 | 1.96 | 2.1 | 2.2 | 2.21 | 37 | 30 | 12 | 0 | 0 | 0 | 0.591 | O.603 | 0.887 | 0.082 | O.144 | 0.186 | 12.8 | 35.6 | 27.3 | 28 | 42.1 | 25.6 | 71.2 | 54.6 | 56 | 84.2 | 2.57 | 3.7 | 3 | 6 | 0.161 | 6.1 | 6 | 0.65843 | 61.8 | 89.4 | 0.2086 | 0.0483 | 14.24 | 13.17 | 14.12 | 0.95 | 1.541 | 2.88 | 7.003 | 2.8884 | 31.22 | 5 |  | 1900-01-09 |  |  | 0
2020-12-16 | Click Here |  | 5.96 | 5.17 | 5.25 | 5.3 | 5.42 | 7.42 | 7.35 | 1.82 | 1.97 | 2.09 | 2.06 | 40 | 34 | 11 | 0 | 0 | 0 | 0.563 | 0.594 | 0.765 | 0.089 | 0.391 | 0.526 | 13.1 | 35.4 | 27.7 | 28.5 | 41.7 | 26.2 | 70.8 | 55.4 | 57 | 83.4 | 2.73 | 3.84 | 3.1 | 5.9 | 0.156 | 5.9 | 6 |  | 62.1 | 90.6 | 0.2058 | 0.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30.1 | 5 |  | 1900-01-08 12:00 |  |  | 90.4
2020-12-17 | Click Here |  | 6.01 | 5.19 | 5.24 | 5.51 | 5.38 | 7.59 | 7.67 | 1.84 | 2.06 | 2.09 | 1.95 | 37 | 30 | 13 | 0 | 0 | 0 | 0.574 | 0.607 | 0.819 | 0.099 | 0.241 | 0.286 | 13.6 | 34.8 | 27.7 | 28.1 | 39.9 | 27.2 | 69.6 | 55.4 | 56.2 | 79.9 | 2.86 | 3.84 | 3 | 6.1 | 0.094 | 6.4 | 6.1 | 1.0158 | 60.4 | 89 | 0.2187 | 0.0502 | 14.81 | 13.3 | 14.77 | 1.47 | 1.467 | 2.791 | 7.216 | 3.0858 | 30.48 | 5 |  | 1900-01-08 12:00 |  |  | 77.18
2020-12-18 | Click Here |  | 6.29 | 5.2 | 5.27 | 5.36 | 5.42 | 7.71 | 7.56 | 1.87 | 2.08 | 2.16 | 2.12 | 38 | 32 | 14 | 1 | 0 | 0 | 0.614 | 0.563 | 1.1 | 0.07 | 0.196 | 0.174 | 12.8 | 37 | 27.3 | 26.2 | 40.1 | 25.6 | 74 | 54.6 | 54.4 | 80.2 | 2.89 | 3.88 | 3.1 | 6.3 | 0.072 | 6.3 | 5.2 | 0.34981 | 60.6 | 90.8 | 0.2185 | 0.0418 | 15.47 | 14.13 | 15.59 | 1.46 | 1.489 | 2.815 | 9.385 | 2.4798 | 32.41 | 5 |  | 1900-01-08 12:00 |  |  | 83.75
2020-12-19 | Click Here |  | 6.36 | 5.18 | 5.25 | 5.3 | 5.39 | 7.14 | 7.39 | 1.72 | 1.89 | 1.93 | 1.86 | 37 | 32 | 16 | 0 | O | 0 | 0.604 | O.581 | 1.09 | 0.104 | 0.288 | 0.276 | 12.7 | 36.5 | 27.1 | 27 | 38.3 | 25.4 | 72 | 54.2 | 54 | 76.6 | 2.99 | 4.1 | 3 | 6.1 | 0.061 | 6.3 | 5.1 | 0.73536 | 60.2 | 90.4 | 0.2188 | 0.042 | 14.68 | 13.7 | 14.67 | 0.97 | 0 | 0 | 0 | 2.7754 | 31.43 | 5 |  | 1900-01-08 12:00 |  |  | 86.17
2020-12-20 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.76841 | 0 | 0 | 0 | 0 | 14.95 | 13.93 | 14.87 | 0.94 | 1.436 | 2.805 | 9.777 | 2.8084 | 0 | 5 |  | 1900-01-08 12:00 |  |  | 88.2
2020-12-21 | Click Here |  | 6.24 | 5.14 | 5.25 | 5.26 | 5.33 | 7.24 | 7.39 | 1.78 | 1.96 | 1.99 | 1.93 | 39 | 33 | 19 | 0 | 0 | 0 | 0.541 | 0.536 | 0.989 | 0.113 | 0.291 | 0.336 | 13 | 35.9 | 27.4 | 26.8 | 39.1 | 26 | 71.8 | 54.8 | 53.6 | 78.2 | 3.06 | 4.11 | 3.1 | 6 | 0.074 | 6.2 | 5 | 0.7073 | 60.6 | 90.6 | 0.2139 | 0.0409 | 15.42 | 14.47 | 15.41 | 0.94 | 1.498 | 2.798 | 10 | 2.7673 | 30.69 | 5 |  | 1900-01-08 12:00 |  |  | 0
2020-12-22 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 88.2
2020-12-23 | Click Here |  | 6.28 | 5.25 | 5.45 | 5.44 | 5.49 | 7.27 | 6.92 | 1.8 | 1.98 | 2.01 | 1.96 | 39 | 32 | 18 | 1 | 0 | 0 | 0.563 | 0.546 | 1.104 | 0.116 | 0.207 | 0.155 | 13.8 | 37 | 28 | 28.4 | 40.1 | 27.6 | 74 | 56 | 56.8 | 80.2 | 3.01 | 4.11 | 3 | 5.8 | 0.066 | 7 | 5.3 | 0.76216 | 60.2 | 90.8 | 0.2141 | 0.0407 | 15.29 | 14.29 | 15.28 | 0.99 | 1.514 | 2.791 | 10 | 2.8022 | 31.9 | 5 |  | 1900-01-08 12:00 |  |  | 88.2
2020-12-24 | Click Here |  | 6.33 | 5.21 | 5.11 | 5.35 | 5.39 | 7.1 | 7.5 | 1.79 | 2 | 2.04 | 1.98 | 38 | 32 | 19 | 1 | 0 | 0 | 0.59 | 0.563 | 1.41 | 0.263 | 0.66 | 0.448 | 13.6 | 37.5 | 28.3 | 28.7 | 39.8 | 27.2 | 75 | 56.6 | 57.4 | 79.6 | 3.05 | 4.22 | 3.1 | 6.1 | 0.083 | 6.6 | 5.2 | 0.92429 | 60.6 | 89 | 0.2139 | 0.0504 | 14.93 | 13.98 | 14.91 | 0.93 | 1.473 | 2.792 | 9.821 | 2.8643 | 30.38 | 5 |  | 1900-01-08 12:00 |  |  | 81.59
2020-12-25 | Click Here |  | 6.02 | 5.28 | 5.25 | 5.31 | 5.42 | 7.09 | 6.94 | 1.79 | 2.01 | 2.06 | 2.02 | 37 | 30 | 16 | 0 | 0 | 0 | 0.56 | 0.554 | 1.091 | 0.104 | 0.453 | 0.687 | 13.6 | 36.5 | 27.2 | 28.6 | 39.9 | 27.2 | 73 | 54.4 | 57.2 | 79.8 | 3.2 | 4.1 | 3 | 5.9 | 0.056 | 6.9 | 5.3 | 0.85772 | 60 | 90.6 | 0.2144 | 0.0413 | 14.21 | 13.24 | 14.17 | 0.93 | 1.412 | 2.785 | 8.823 | 2.7977 | 30.04 | 4.8 |  | 1900-01-08 12:00 |  |  | 83.79
2020-12-26 | Click Here |  | 5.95 | 5.14 | 5.25 | 5.34 | 5.39 | 7.3 | 6.87 | 1.75 | 1.98 | 1.81 | 1.79 | 36 | 29 | 12 | 0 | 0 | 0 | 0.828 | 0.539 | 1.25 | 0.296 | 0.491 | 0.444 | 13.8 | 34.5 | 27.7 | 28.1 | 39.2 | 27.6 | 69 | 55.4 | 56.2 | 78.4 | 3.1 | 4.18 | 3.1 | 5.9 | 0.024 | 7.1 | 5.4 | 0.7895 | 56.6 | 90.4 | 0.2472 | 0.0437 | 14.5 | 13.54 | 14.48 | 0.94 | 1.47 | 2.673 | 9.673 | 2.8095 | 30.28 | 4.8 |  | 1900-01-08 12:00 |  |  | 0
2020-12-27 | Click Here |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 83.79
2020-12-28 | Click Here |  | 6.39 | 5.27 | 5.09 | 5.39 | 5.41 | 6.94 | 7.55 | 1.8 | 2 | 2.07 | 2.16 | 37 | 30 | 15 | 0 | 0 | 0 | 0.733 | 0.614 | 1.29 | 0.214 | 0.477 | 0.418 | 12.5 | 34.6 | 27.1 | 27.6 | 38.1 | 25 | 69.2 | 54.2 | 55.2 | 76.2 | 3.14 | 4.25 | 3 | 6 | 0.034 | 6.5 | 5.2 | 0.73861 | 56.9 | 90.1 | 0.2469 | 0.044 | 14.69 | 13.74 | 14.68 | 0.94 | 1.504 | 2.711 | 9.307 | 2.7686 | 30.19 | 4.8 |  | 1900-01-08 07:12 |  |  | 79.38
2020-12-29 | Click Here |  | 6.45 | 5.27 | 5.31 | 5.38 | 5.39 | 6.84 | 7.08 | 1.83 | 2.02 | 2.09 | 2.15 | 38 | 30 | 17 | 1 | 0 | 0 | 0.721 | 0.603 | 1.31 | 0.219 | 0.531 | 0.447 | 12.6 | 34.2 | 27.4 | 27.7 | 36.6 | 25.2 | 68.4 | 54.8 | 55.4 | 71.2 | 3.11 | 4.2 | 3.1 | 5.9 | 0.028` | 5.6 | 5.1 | 0.78455 | 56.7 | 90.4 | 0.247 | 0.0439 | 13.87 | 12.85 | 13.8 | 0.95 | 1.455 | 2.719 | 8.417 | 2.8046 | 30.31 | 4.8 |  | 1900-01-08 07:12 |  |  | 81.59
2020-12-30 | Click Here |  | 6.06 | 5.24 | 5.25 | 5.36 | 5.39 | 7.2 | 6.6 | 1.5 | 1.73 | 1.9 | 1.85 | 36 | 29 | 14 | 1 | 0 | 0 | 0.691 | 0.582 | 1.81 | 0.313 | 0.577 | 0.533 | 13.2 | 35.9 | 27.4 | 27.9 | 37.7 | 26.4 | 71.8 | 54.8 | 55.8 | 75.4 | 3.07 | 3.99 | 3.1 | 6 | 0.018 | 6.9 | 5.5 | 0.78473 | 54.7 | 89.6 | 0.2618 | 0.0473 | 14.16 | 13.16 | 14.11 | 0.95 | 1.417 | 2.715 | 8.464 | 2.8147 | 30.04 | 4.8 |  | 1900-01-08 07:12 |  |  | 76.89
2020-12-31 | Click Here |  | 6.12 | 5.26 | 5.23 | 5.33 | 5.39 | 7.31 | 7.4 | 1.78 | 1.94 | 2.06 | 2.1 | 36 | 28 | 15 | 1 | 0 | 0 | 0.569 | 0.544 | 1.27 | 0.199 | 0.501 | 0.482 | 13.1 | 33.6 | 28.2 | 30.1 | 36.7 | 26.2 | 67.2 | 56.4 | 60.2 | 73.4 | 3.01 | 3.96 | 3 | 5.8 | 0.022 | 6.6 | 5.7 | 0.72533 | 58.8 | 90.1 | 0.2326 | 0.0447 | 13.555 | 12.488 | 13.45 | 0.962 | 1.37 | 2.713 | 8.221 | 2.7953 | 30.51 | 4.8 |  | 1900-01-08 07:12
|  |  | pH | [6 empty] | Chlorine |  |  |  | Colour | [5 empty] | Turbidity | [5 empty] | Total Dissolved Solids |  |  |  |  | Conductivity |  |  |  |  | Hardness |  | Alkalinity |  | Aluminum | Temperature |  | Cl Demand | UVT |  | UVA |  | Flows withinin plant |  |  |  | Flows from plant |  |  | Chemical Dosages
|  |  | Raw | PTC | PTC (OL) | SWC | Filter | Finish (OL) | Finish | Free | Total | Sample | Analyzer | Raw A | Raw T | SWC A | Filter A | Finish A | Finish T | Raw | Raw (OL) | SWC | Filter | Finish | Finish (OL) | Raw | PTC | SWC | Filter | Finish | Raw | PTC | SWC | Filter | Finish | Raw | Finish | Raw | Finish | Finish (Free) | Raw | Finish |  | Raw | Filter | Raw | Filter | Raw | Finish | Filter | Backwash | Bishop's | Botwood | GFW | Chlorine | Alum | Lime (Pre) | Lime (Post)
January 2020 Average |  |  | 6.06 | 5.24 | 5.25 | 5.33 | 5.36 | 6.78 | 6.89 | 1.88 | 2.05 | 2.09 | 2.08 | 40.44 | 32.81 | 16.41 | 1.3 | 1 | #DIV/0! | 0.37 | 0.17 | 1.07 | 0.15 | 0.54 | 0.56 | 13.55 | 33.16 | 27.25 | 28.46 | 36.28 | 27.1 | 66.32 | 54.5 | 54.69 | 72.56 | 3.18 | 3.64 | 2.96 | 5.8 | 0.04 | 6.79 | 4.23 | 0.69 | 56.49 | 91.08 | 0.25 | 0.06 | 14.62 | 13.58 | 14.48 | 0.96 | 1.58 | 2.5 | 9.17 | 2.73 | 30.27 | 5.54 | 11.14
February 2020 Average |  |  | 5.98 | 5.28 | 5.3 | 5.38 | 5.42 | 6.85 | 6.95 | 1.66 | 1.87 | 1.91 | 1.89 | 39.21 | 32.38 | 15 | 1.22 | #DIV/0! | #DIV/0! | 0.34 | 0.26 | 1.07 | 0.17 | 0.43 | 0.48 | 15.73 | 34.13 | 27.63 | 28.1 | 38.93 | 30.99 | 68.25 | 55.27 | 56.19 | 77.85 | 3.18 | 3.83 | 3.14 | 5.93 | 0.04 | 7.1 | 4.07 | 0.62 | 57.5 | 91.1 | 0.24 | 0.04 | 14.83 | 13.86 | 14.76 | 1.02 | 1.58 | 2.5 | 8.71 | 2.54 | 30.12 | 5.42 | 12.58
March 2020 Average |  |  | 5.95 | 5.24 | 5.22 | 5.34 | 5.38 | 6.82 | 6.96 | 1.68 | 1.92 | 1.92 | 1.9 | 41 | 34.35 | 14.69 | 1.58 | 1 | #DIV/0! | 0.35 | 0.26 | 1.04 | 0.13 | 0.41 | 0.44 | 16.65 | 35.07 | 28.14 | 28.49 | 39.25 | 33.3 | 70.13 | 56.28 | 56.98 | 78.51 | 3.12 | 3.92 | 3.06 | 5.94 | 0.04 | 6.83 | 3.82 | 0.75 | 57.38 | 91.45 | 0.24 | 0.04 | 14.93 | 13.82 | 14.68 | 0.94 | 1.58 | 2.5 | 9.29 | 2.66 | 29.73 | 4.6 | 13.06
April 2020 Average |  |  | 5.83 | 5.15 | 4.88 | 5.29 | 5.3 | 6.96 | 6.99 | 1.73 | 1.93 | 1.96 | 1.94 | 45.68 | 38.96 | 15.92 | 1.92 | 1 | #DIV/0! | 0.31 | 0.23 | 1.05 | 0.14 | 0.47 | 0.46 | 15.64 | 36.1 | 29.13 | 29.37 | 39.97 | 30.91 | 72.21 | 58.26 | 58.74 | 79.94 | 3.07 | 3.78 | 3.13 | 5.74 | 0.04 | 6.21 | 3.54 | 0.68 | 53.45 | 90.9 | 0.27 | 0.05 | 14.58 | 13.56 | 14.49 | 0.96 | 1.58 | 2.5 | 9.55 | 2.64 | 29.98 | 4.3 | 14.58
May 2020 Average |  |  | 5.89 | 4.96 | 4.92 | 5.05 | 5.07 | 7.23 | 7.26 | 1.7 | 1.89 | 2.04 | 2.21 | 55.52 | 48.07 | 14.56 | 1.09 | #DIV/0! | #DIV/0! | 0.33 | 0.25 | 1.17 | 0.13 | 0.47 | 0.43 | 11.93 | 34.48 | 29.01 | 28.92 | 37.35 | 23.87 | 68.96 | 58.02 | 56.97 | 74.7 | 2.94 | 3.83 | 3.02 | 5.93 | 0.07 | 9.36 | 5.67 | 0.58 | 52.37 | 88.79 | 0.28 | 0.05 | 14.62 | 13.61 | 14.35 | 0.97 | 1.58 | 2.5 | 9.07 | 2.84 | 29.82 | 5.38 | 15.31
June 2022 Average |  |  | 6.03 | 5.09 | 5.11 | 5.11 | 5.13 | 7.34 | 7.35 | 1.68 | 1.85 | 2.13 | 2.24 | 50.52 | 42.92 | 11.84 | 2 | 1 | #DIV/0! | 0.43 | 0.44 | 0.46 | 0.09 | 0.2 | 0.12 | 13.16 | 36.93 | 35.15 | 35.36 | 43.86 | 26.31 | 72.4 | 70.3 | 70.73 | 87.73 | 3.31 | 3.9 | 3.07 | 6.09 | 0.09 | 17.47 | 13.58 | 0.63 | 56.24 | 91.57 | 0.25 | 0.04 | 15.41 | 14.31 | 15.04 | 1.07 | 1.58 | 2.5 | 10.23 | 2.9 | 29.63 | 6.8 | 9.86
July 2020 Average |  |  | 6.05 | 5.12 | 5.09 | 5.07 | 5.13 | 7.02 | 7.11 | 1.76 | 1.91 | 2.16 | 2.33 | 41.19 | 33.78 | 14.37 | 1.6 | 1 | #DIV/0! | 0.41 | 0.43 | 0.61 | 0.1 | 0.21 | 0.14 | 15.46 | 39.77 | 38.26 | 38.22 | 47.24 | 30.92 | 79.55 | 76.56 | 76.44 | 94.49 | 2.92 | 3.8 | 3.05 | 5.95 | 0.06 | 20.64 | 18.15 | 0.75 | 62.23 | 91.15 | 0.2 | 0.04 | 16.4 | 15.32 | 16.18 | 1.05 | #DIV/0! | #DIV/0! | #DIV/0! | 3.1 | 29.57 | 6.92 | 8.33
August 2020 Average |  |  | 6.04 | 4.97 | 5.04 | 4.99 | 5 | 6.73 | 6.93 | 1.7 | 1.88 | 2.13 | 2.13 | 38.96 | 31.92 | 13.85 | 1.5 | 1 | #DIV/0! | 0.69 | 0.81 | 0.57 | 0.1 | 0.24 | 0.24 | 16.79 | 40.69 | 39.29 | 39.81 | 47.6 | 33.58 | 81.38 | 78.63 | 77.97 | 93.38 | 2.91 | 3.82 | 3.04 | 5.91 | 0.04 | 20.55 | 19.32 | 0.86 | 65.88 | 91.48 | 0.18 | 0.04 | 15.21 | 14.07 | 14.96 | 0.97 | #DIV/0! | #DIV/0! | #DIV/0! | 2.99 | 29.52 | 7.43 | 11.34
September 2020 Average |  |  | 6.27 | 5.06 | 5.08 | 5.09 | 5.13 | 6.77 | 6.99 | 1.82 | 2 | 2.16 | 2.26 | 41.84 | 34.56 | 11.28 | 1.14 | #DIV/0! | #DIV/0! | 0.8 | 0.95 | 0.61 | 0.11 | 0.35 | 0.32 | 15.98 | 39.51 | 37.27 | 36.28 | 44.78 | 31.96 | 79.18 | 74.54 | 72.55 | 89.57 | 2.94 | 3.87 | 3.05 | 5.95 | 0.04 | 16.95 | 16.47 | 0.65 | 62.63 | 90.39 | 0.2 | 0.04 | 14.49 | 13.38 | 14.35 | 1.11 | #DIV/0! | #DIV/0! | #DIV/0! | 3 | 29.69 | 8.5 | 12.92
October 2020 Average |  |  | 6.43 | 5.29 | 5.28 | 5.36 | 5.44 | 7.22 | 7.4 | 1.75 | 1.94 | 2.13 | 2.25 | 39.1 | 31.86 | 13.62 | 1.25 | 1 | #DIV/0! | 0.81 | 0.84 | 0.71 | 0.12 | 0.23 | 0.13 | 15.48 | 39.05 | 35.36 | 35.51 | 47.2 | 30.95 | 78.1 | 70.71 | 71.02 | 94.31 | 2.86 | 3.81 | 3.02 | 5.9 | 0.07 | 15.15 | 14.31 | 0.66 | 66.71 | 91.61 | 0.18 | 0.04 | 14.47 | 13.37 | 14.31 | 1.02 | #DIV/0! | #DIV/0! | #DIV/0! | 2.91 | 29.61 | 6.8 | 9.05
November 2020 Average |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
December 2020 Average |  |  | 6.14 | 5.2 | 5.21 | 5.34 | 5.4 | 7.3 | 7.31 | 1.81 | 2 | 2.06 | 2.04 | 37.56 | 30.81 | 14.63 | 1.17 | #DIV/0! | #DIV/0! | 0.62 | 0.58 | 1.08 | 0.15 | 0.38 | 0.38 | 13.19 | 35.74 | 27.66 | 28.01 | 39.24 | 26.39 | 71.43 | 55.31 | 56.14 | 78.36 | 2.99 | 4.02 | 3.06 | 5.99 | 0.08 | 6.63 | 5.58 | 0.73 | 59.41 | 90.12 | 0.23 | 0.04 | 14.59 | 13.58 | 14.54 | 1.02 | 1.48 | 2.79 | 8.9 | 2.8 | 30.68 | 4.94 | #DIV/0!
2020 Average |  |  | 6.05 | 5.14 | 5.12 | 5.2 | 5.24 | 6.99 | 7.09 | 1.74 | 1.93 | 2.06 | 2.12 | 43.11 | 35.94 | 14.21 | 1.45 | 1 | #DIV/0! | 0.47 | 0.46 | 0.86 | 0.13 | 0.37 | 0.34 | 14.9 | 36.78 | 32.31 | 32.53 | 41.97 | 29.72 | 73.42 | 64.58 | 64.6 | 83.75 | 3.05 | 3.83 | 3.06 | 5.93 | 0.05 | 12.31 | 9.99 | 0.69 | 58.97 | 90.88 | 0.23 | 0.04 | 14.95 | 13.89 | 14.76 | 1 | 1.55 | 2.59 | 9.04 | 2.83 | 29.85 | 6.08 | 11.87
*Community flow meters were not working well in 2020 and not at all after July.
Started working again in December.
2020 WTP Flow Assessment
| Month | Finish | BF | Botwood | GFW | Communuity Flow | Percent Diff (%) |  |  | Max Value | Min Value
| January | 14.48 | 2.5 | 9.17 | 2.73 | 14.4 | 0.5525% |  | Finish | 19.82 | 11.87
| February | 14.76 | 2.5 | 8.71 | 2.54 | 13.75 | 6.843% |  | GFW | 10.541 | 7.003
| March | 14.68 | 2.5 | 9.29 | 2.66 | 14.45 | 1.567% |  | Botwood | 3.076 | 2.504
| April | 14.49 | 2.5 | 9.55 | 2.64 | 14.69 | 1.38% |  | Bishops | 1.575 | 1.37
| May | 14.35 | 2.5 | 9.07 | 2.84 | 14.41 | 0.4181%
| June | 15.04 | 2.5 | 10.23 | 2.9 | 15.63 | 3.923%
| July | 16.18
| August | 14.96
| September | 14.35
| October | 14.31
| November | #DIV/0!
| December | 14.54 | 2.79 | 8.9 | 2.8 | 14.49 | 0.3439%
| Yr Average | #DIV/0! | 2.5414 | 9.2743 | 2.73 | 14.5457 | 2.147%
| MONTHLY AVERAGES | UVT RAW | UVT Filter | UVA RAW | UVA Filter |  |  | Max Value | Min Value
| January | 56.49 | 91.08 | 0.248 | 0.0556 |  | UVT Raw | 72.4 | 47.1
| February | 57.43 | 91.04 | 0.24 | 0.0407 |  | UVT Filter | 95.3 | 84.4
| March | 57.45 | 91.52 | 0.242 | 0.0377 |  | UVA Raw | 0.3268 | 0.2319
| April | 53.13 | 90.76 | 0.276 | 0.0543 |  | UVA Filter | 0.448 | 0.0211
| May | 52.47 | 88.82 | 0.052 | 0.052
| June | 56.35 | 91.59 | 0.039 | 0.0385
| July | 62.44 | 91.16 | 0.203 | 0.0401
| August | 65.8 | 91.4 | 0.182 | 0.0392
| September | 62.69 | 90.5 | 0.201 | 0.0433
| October | 66.84 | 91.55 | 0.175 | 0.038
November
December
2020 WTP Averages
| MONTHLY AVERAGES | Temp. (RAW) | Temp. (Finish) | Alkalinity (RAW) | Alkalinity (Finish) | Aluminum (Finish) | Hardness (RAW) | Hardness (Finish) |  |  | Max Value | Min Value
| January | 6.79 | 4.23 | 2.96 | 5.8 | 0.041 | 3.18 | 3.64 |  | Temp. Raw | 23.5 | 3.1
| February | 7.08 | 4.06 | 3.14 | 5.91 | 0.039 | 3.18 | 3.84 |  | Temp. Finish | 20.5 | 3.2
| March | 6.78 | 3.8 | 3.05 | 5.96 | 0.034 | 3.11 | 3.91 |  | Alkalinity Raw | 5.7 | 2.6
| April | 6.34 | 3.57 | 3.13 | 5.73 | 0.045 | 3.07 | 3.78 |  | Alkalinity Finish | 6.8 | 3.3
| May | 9.39 | 5.73 | 3.03 | 5.93 | 0.064 | 2.94 | 3.83 |  | Hardness Raw | 3.95 | 2.57
| June | 17.65 | 13.73 | 3.08 | 6.08 | 0.093 | 3.3 | 3.89 |  | Hardness Finish | 4.52 | 2.24
| July | 20.58 | 18.19 | 3.04 | 5.96 | 0.058 | 2.91 | 3.8
| August | 20.41 | 19.25 | 3.04 | 5.9 | 0.039 | 2.91 | 3.83
| September | 16.97 | 16.4 | 3.05 | 5.95 | 0.037 | 2.95 | 3.88
| October | 15.04 | 14.26 | 3.03 | 5.91 | 0.07 | 2.85 | 3.8
November
December
| Average | 12.703 | 10.322 | 3.055 | 5.913 | 0.052 | 3.04 | 3.82
| MONTHLY AVERAGES | TDS (RAW) | TDS (Finish) | Conduct. (RAW) | Conduct. (Finish) |  |  | Max Value | Min Value
| January | 13.55 | 36.28 | 27.1 | 72.56 |  | TDS (RAW) | 35.4 | 9.4
| February | 15.72 | 38.68 | 31.01 | 77.36 |  | TDS (Finish) | 61.4 | 29.9
| March | 16.67 | 39.62 | 33 | 79.25 |  | Conduct. (RAW) | 70.8 | 18.8
| April | 15.55 | 39.91 | 31.1 | 79.82 |  | Conduct. (Finish) | 122.8 | 47.4
| May | 11.85 | 37.21 | 23.7 | 74.42
| June | 13.24 | 44.07 | 26.48 | 88.15
| July | 15.49 | 47.22 | 30.99 | 94.44
| August | 16.76 | 47.53 | 33.52 | 93.24
| September | 15.99 | 45.13 | 31.98 | 90.26
| October | 15.46 | 46.8 | 30.92 | 93.49
November
December
| MONTHLY AVERAGES | Color (Raw/Actual) | Color (Raw/True) |  |  | Max Value | Min Value
| January | 40.44 | 32.81 |  | Color (Raw/Actual) | 60 | 28 |  |  | 2020 WTP Averages
| February | 39.36 | 32.56 |  | Color (Raw/True) | 54 | 21 |  |  | MONTHLY AVERAGES | Filter Turbidity | Finish Turbidity | Raw Turbidity
| March | 40.96 | 34.27 | [6 empty] | January | 0.149 | 0.545 | 0.374
| April | 46.24 | 39.52 | [6 empty] | February | 0.169 | 0.435 | 0.342 |  |  | >= 1 NTU Finish | 2
| May | 55.5 | 48.04 | [6 empty] | March | 0.134 | 0.411 | 0.353
| June | 50.12 | 42.5 | [6 empty] | April | 0.138 | 0.469 | 0.315
| July | 41.19 | 33.81 | [6 empty] | May | 0.125 | 0.469 | 0.334
| August | 38.88 | 31.85 | [6 empty] | June | 0.092 | 0.203 | 0.435
| September | 42 | 34.68 | [6 empty] | July | 0.1 | 0.21 | 0.41
| October | 38.95 | 31.75 | [6 empty] | August | 0.101 | 0.241 | 0.692
| November | [8 empty] | September | 0.114 | 0.352 | 0.804
| December | 37.69 | 31.08 | [6 empty] | October | 0.119 | 0.233 | 0.813
November
[10 empty] | December | 0.15 | 0.391 | 0.619
|  | 2020 Free Chlorine Assessment | [7 empty] | Average | 0.12645 | 0.35991 | 0.49918
| MONTHLY AVERAGES | Free | Analyzer (Sample) | % Diff. | Residual Loss |  |  | Max Value | Min Value
| January | 1.88 | 2.08 | 9.615% | 0.2 |  | Free Chlorine | 2.07 | 1.44
| February | 1.66 | 1.89 | 12.17% | 0.23 |  | Analyzer Chlorine | 3.02 | 1.44
| March | 1.69 | 1.9 | 11.05% | 0.21
| April | 1.72 | 1.94 | 11.34% | 0.22
| May | 1.7 | 2.21 | 23.08% | 0.51
| June | 1.67 | 2.24 | 25.45% | 0.57
| July | 1.76 | 2.32 | 24.14% | 0.56
| August | 1.71 | 2.12 | 19.34% | 0.41
| September | 1.83 | 2.32 | 21.12% | 0.49
| October | 1.74 | 2.21 | 21.27% | 0.47
| November |  |  |  | 0
| December |  |  |  | 0
| Average | 1.736 | 2.123 | 18.23% | 0.3225

## 2019
Note: The password to unlock the sheets is "WTPLAB". Don't unlock any of them unless you plan on making permanent changes.
|  |  | pH | [6 empty] | Chlorine |  |  |  | Colour | [5 empty] | Turbidity | [5 empty] | Total Dissolved Solids |  |  |  |  | Conductivity |  |  |  |  | Hardness |  | Alkalinity |  | Aluminum | Temperature |  | Cl Demand | UVT |  | UVA |  | Flows withinin plant |  |  |  | Flows from plant |  |  | Chemical Dosages |  |  |  |  | Dennis Penney
Date | Shortcut | Start Time | Raw | PTC | PTC (OL) | SWC | Filter | Finish (OL) | Finish | Free | Total | Sample | Analyzer | Raw A | Raw T | SWC A | Filter A | Finish A | Finish T | Raw | Raw (OL) | SWC | Filter | Finish | Finish (OL) | Raw | PTC | SWC | Filter | Finish | Raw | PTC | SWC | Filter | Finish | Raw | Finish | Raw | Finish | Finish (Free) | Raw | Finish |  | Raw | Filter | Raw | Filter | Raw | Finish | Filter | Backwash | Bishop's | Botwood | GFW | Chlorine | Alum | Lime (Pre) | Lime (Post) | Date | Jerry Loveless
2019-01-01 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.96178 | 0 | 0 | 0 | 0 | 13.978 | 12.885 | 13.866 | 0.981 | 1.655 | 2.36 | 8.87 | 2.9918 | 0 | 5 | 9 | 2019-01-01 | Nolan Simms
2019-01-02 | Click Here | 0:00 | 6.14 | 5.29 | 5.23 | 5.36 | 5.39 | 7.16 | 7.11 | 1.59 | 1.94 | 2.04 | 2.09 | 59 | 51 | 14 | 1 | 0 | 0 | 0.401 | 0.617 | 0.476 | 0.109 | 0.2 | 0.437 | 13.4 | 33.7 | 24.5 | 24.7 | 34.2 | 26.8 | 67.4 | 49 | 49.4 | 68.4 | 3.29 | 18.59 | 3 | 5.9 | 0.062 | 6.5 | 3.4 | 0.88646 | 50.4 | 90 | 0.2974 | 0.0457 | 14.57 | 13.49 | 14.47 | 0.98 | 1.568 | 2.399 | 9.523 | 2.8765 | 28.49 | 5 | 9 | 2019-01-02
2019-01-03 | Click Here | 0:00 | 6.04 | 5.29 | 5.24 | 5.37 | 5.41 | 7.19 | 7.25 | 1.79 | 2.1 | 2.04 | 2 | 59 | 52 | 15 | 0 | 0 | 0 | 0.374 | 0.556 | 0.428 | 0.074 | 0.204 | 0.412 | 12.9 | 32.8 | 24.7 | 25.2 | 34.4 | 25.8 | 65.6 | 49.4 | 50.4 | 68.8 | 3.16 | 18.91 | 3.4 | 6 | 0.067 | 6.5 | 3.5 | 2.2403 | 50.6 | 89.9 | 0.2953 | 0.046 | 13.704 | 9.1 | 10.08 | 0.98 | 1.542 | 2.427 | 5.131 | 4.1803 | 30.32 | 5 | 9 | 2019-01-03
2019-01-04 | Click Here | 0:00 | 6.44 | 5.49 | 5.19 | 5.51 | 5.48 | 6.71 | 7.02 | 1.83 | 2.14 | 2.02 | 2 | 59 | 54 | 13 | 0 | 0 | 0 | 0.361 | 0.546 | 0.643 | 0.088 | 0.216 | 0.457 | 13.5 | 34.7 | 25.2 | 25.9 | 34.8 | 27 | 69.4 | 50.4 | 51.8 | 69.6 | 3.07 | 18.33 | 3.6 | 6.4 | 0.042 | 6.8 | 3.4 | 1.134 | 50.2 | 85.5 | 0.299 | 0.0676 | 15.003 | 12.882 | 14.838 | 1.956 | 1.542 | 2.441 | 8.899 | 3.144 | 27.95 | 5 | 9 | 2019-01-04 | Continuous
2019-01-05 | Click Here | 0:00 | 6.76 | 5.49 | 5.35 | 5.5 | 5.49 | 6.45 | 7.23 | 1.91 | 2.2 | 2.15 | 2.16 | 58 | 52 | 14 | 0 | 0 | 0 | 0.351 | 0.543 | 0.727 | 0.096 | 0.213 | 0.461 | 13.5 | 32.9 | 25.7 | 26.2 | 35.3 | 27 | 65.8 | 51.4 | 52.4 | 70.6 | 2.93 | 17.77 | 3.5 | 6.2 | 0.053 | 7 | 3.4 | 0.75064 | 51.4 | 87.5 | 0.289 | 0.0546 | 14.65 | 13.49 | 14.49 | 1 | 0 | 0 | 0 | 2.9306 | 32.14 | 5.2 | 9.4 | 2019-01-05 | Grab
2019-01-06 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 14.976 | 10.299 | 11.168 | 0.869 | 1.579 | 2.402 | 6.318 |  | 0 | 5.2 | 9.8 | 2019-01-06 | ^ Stuff for form dropdown menus
2019-01-07 | Click Here | 0:00 | 6.19 | 5.3 | 5.23 | 5.46 | 5.4 | 7.2 | 7.18 | 1.88 | 2.17 | 2.04 | 2.08 | 61 | 55 | 15 | 0 | 0 | 0 | 0.339 | 0.517 | 0.688 | 0.084 | 0.191 | 0.472 | 13.2 | 33.1 | 25.4 | 26 | 35.6 | 26.4 | 66.2 | 50.8 | 52 | 71.2 | 2.95 | 18.21 | 3.7 | 6 | 0.064 | 7 | 3.3 | 0.78899 | 52 | 88.8 | 0.2824 | 0.0494 | 15.746 | 14.14 | 15.119 | 0.979 | 1.579 | 2.444 | 10.117 | 2.829 | 31.1 | 5.2 | 9.8 | 2019-01-07
2019-01-08 | Click Here | 0:00 | 6.2 | 5.24 | 5.19 | 5.31 | 5.36 | 7.17 | 7.21 | 1.94 | 2.2 | 2.11 | 2.14 | 64 | 58 | 17 | 0 | 0 | 0 | 0.374 | 0.486 | 0.694 | 0.059 | 0.274 | 0.476 | 12.9 | 33.6 | 25.6 | 26.2 | 34.8 | 25.8 | 67.2 | 51.2 | 52.4 | 69.6 | 3.11 | 19.32 | 4 | 6.7 | 0.094 | 6.9 | 3.2 | 1.5929 | 51.8 | 89.1 | 0.2851 | 0.0468 | 14.62 | 9.92 | 10.89 | 0.97 | 1.645 | 2.441 | 5.837 | 3.6329 | 29.72 | 5.2 | 9.8 | 2019-01-08
2019-01-09 | Click Here | 0:00 | 6.5 | 5.63 | 5.17 | 5.65 | 5.49 | 6.76 | 7.09 | 1.9 | 2.16 | 2.02 | 2.04 | 62 | 56 | 15 | 1 | 0 | 0 | 0.373 | 0.486 | 0.506 | 0.063 | 0.241 | 0.437 | 14.4 | 35.5 | 27.4 | 28.1 | 37.1 | 28.8 | 71 | 54.8 | 56.2 | 74.2 | 2.89 | 17.76 | 4.2 | 6.6 | 0.071 | 7.8 | 3.3 | 0.83697 | 13.7 | 88 | 0.8621 | 0.0554 | 15.705 | 12.944 | 13.92 | 0.976 | 1.607 | 2.454 | 8.883 | 2.847 | 28.55 | 5.2 | 9.8 | 2019-01-09
2019-01-10 | Click Here | 0:00 | 6.3 | 5.56 | 5.61 | 5.55 | 5.57 | 6.78 | 7.28 | 1.61 | 1.98 | 1.94 | 1.97 | 63 | 57 | 18 | 1 | 0 | 0 | 0.369 | 0.472 | 0.856 | 0.104 | 0.316 | 0.524 | 13.8 | 33.1 | 26.8 | 27.2 | 37.4 | 27.6 | 66.2 | 53.6 | 54.4 | 74.8 | 2.97 | 18.21 | 4.1 | 6.8 | 0.063 | 6.2 | 3.4 | 1.7799 | 48.8 | 90 | 0.3108 | 0.0456 | 14.398 | 9.697 | 10.672 | 0.975 | 1.607 | 2.496 | 5.594 | 3.8199 | 29.27 | 5.2 | 10.2 | 2019-01-10
2019-01-11 | Click Here | 0:00 | 5.36 | 5.33 | 5.42 | 5.34 | 5.35 | 7.56 | 7.3 | 1.68 | 1.94 | 1.86 | 2.03 | 55 | 49 | 22 | 3 | 0 | 0 | 0.334 | 0.48 | 0.842 | 0.092 | 0.262 | 0.421 | 13.6 | 29.9 | 25.9 | 27.1 | 37.3 | 27.2 | 59.8 | 51.8 | 54.2 | 74.6 | 3.38 | 18.71 | 3.7 | 6.3 | 0.065 | 5.9 | 3.3 | 0.71018 | 50.5 | 88.6 | 0.2994 | 0.0525 | 14.48 | 13.27 | 14.28 | 0.97 | 1.666 | 2.488 | 9.13 | 2.6402 | 29.57 | 5.1 | 10.4 | 2019-01-11
2019-01-12 | Click Here | 0:00 | 5.24 | 5.15 | 5.27 | 5.27 | 5.3 | 7.01 | 7.59 | 1.52 | 1.91 | 1.95 | 1.89 | 54 | 47 | 16 | 1 | 0 | 0 | 0.341 | 0.487 | 0.833 | 0.087 | 0.256 | 0.416 | 13.5 | 30 | 26.1 | 26.9 | 37.6 | 27 | 60 | 52.2 | 53.8 | 75.2 | 3.39 | 19.21 | 3.6 | 6.1 | 0.061 | 5.9 | 3.4 |  | 50.8 | 89 | 0.2998 | 0.0506 | 13.91 | 13.68 | 13.68 | 0 | 0 | 0 | 0 |  | 29.57 | 5.1 | 10.4 | 2019-01-12
2019-01-13 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-01-13
2019-01-14 | Click Here | 0:00 | 6.71 | 5.61 | 5.29 | 5.56 | 5.48 | 6.28 | 7.53 | 1.61 | 1.91 | 1.94 | 1.98 | 55 | 46 | 18 | 1 | 0 | 0 | 0.336 | 0.485 | 0.885 | 0.113 | 0.263 | 0.481 | 14.2 | 32 | 26.3 | 27.7 | 37.3 | 28.4 | 64 | 52.6 | 55.4 | 74.6 | 3.35 | 18.56 | 3.4 | 6.3 | 0.047 | 6.7 | 3.3 | 1.001 | 50.5 | 91.4 | 0.2966 | 0.0391 | 15.168 | 13.134 | 15.087 | 1.953 | 1.644 | 2.453 | 9.037 | 2.961 | 29.08 | 5.1 | 10.4 | 2019-01-14
2019-01-15 | Click Here | 0:00 | 6.5 | 5.45 | 5.58 | 5.44 | 5.41 | 6.24 | 6.72 | 1.65 | 1.96 | 1.9 | 1.94 | 56 | 48 | 17 | 0 | 0 | 0 | 0.368 | 0.477 | 0.804 | 0.096 | 0.241 | 0.376 | 13.5 | 32.7 | 26.2 | 27.5 | 38.1 | 27 | 65.4 | 52.4 | 55 | 76.2 | 3.3 | 19.11 | 3.5 | 6.1 | 0.053 | 5.7 | 3.3 | 1.8489 | 49.7 | 88 | 0.3034 | 0.0553 | 14.085 | 9.339 | 10.32 | 0.981 | 1.66 | 2.417 | 5.262 | 3.8589 | 29.2 | 5 | 10.8 | 2019-01-15
2019-01-16 | Click Here | 0:00 | 5.44 | 5.41 | 5.45 | 5.36 | 5.39 | 6.96 | 6.79 | 1.49 | 1.82 | 1.78 | 1.97 | 55 | 48 | 14 | 1 | 0 | 0 | 0.321 | 0.481 | 1.28 | 0.104 | 0.257 | 0.391 | 14.4 | 33.4 | 26.5 | 27.2 | 38.9 | 28.8 | 66.8 | 53 | 54.4 | 77.8 | 3.36 | 17.59 | 3.3 | 5.8 | 0.062 | 6.7 | 3.3 | 0.65713 | 51.7 | 88.8 | 0.2863 | 0.0514 | 13.96 | 12.88 | 13.89 | 0.96 | 1.639 | 2.41 | 8.831 | 2.4871 | 29.57 | 5 | 11 | 2019-01-16
2019-01-17 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-01-17
2019-01-18 | Click Here | 0:00 | 6.04 | 5.39 | 5.43 | 5.41 | 5.47 | 7.6 | 7.73 | 1.67 | 2.04 | 1.99 | 1.91 | 66 | 54 | 17 | 0 | 0 | 0 | 0.307 | 0.447 | 0.541 | 0.087 | 0.099 | 0.154 | 14.1 | 34.4 | 25.9 | 27.2 | 38.1 | 28.2 | 68.8 | 51.8 | 54.4 | 76.2 | 3.24 | 18.89 | 3.4 | 6.4 | 0.07 | 6.8 | 3.4 | 0.82329 | 51.6 | 90.1 | 0.2868 | 0.0425 | 14.12 | 13.01 | 13.96 | 0.95 | 1.637 | 2.416 | 8.957 | 2.6933 | 30.24 | 5 | 11 | 2019-01-18
2019-01-19 | Click Here | 0:00 | 5.57 | 5.44 | 5.42 | 5.38 | 5.34 | 7.59 | 7.29 | 1.61 | 1.87 | 1.95 | 1.77 | 55 | 47 | 16 | 1 | 0 | 0 | 0.306 | 0.489 | 1.14 | 0.096 | 0.174 | 0.199 | 14.5 | 32.9 | 27.1 | 27 | 35.3 | 29 | 65.8 | 54.2 | 54 | 70.6 | 3.9 | 18.74 | 3.5 | 6 | 0.067 | 6.7 | 3.3 | 0.91849 | 51.9 | 89.4 | 0.2855 | 0.0493 | 14.39 | 13.33 | 14.27 | 0.94 | 1.672 | 2.399 | 9.259 | 2.7785 | 29.34 | 5 | 11 | 2019-01-19
2019-01-20 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-01-20
2019-01-21 | Click Here | 0:00 | 5.61 | 5.44 | 5.44 | 5.38 | 5.42 | 7.2 | 7.78 | 1.5 | 1.83 | 1.9 | 1.92 | 55 | 47 | 17 | 1 | 0 | 0 | 0.289 | 0.435 | 0.843 | 0.183 | 0.293 | 0.435 | 14.6 | 33 | 26.5 | 28 | 39.2 | 29.2 | 66 | 53 | 56 | 78.4 | 3.2 | 18.46 | 3.3 | 6.1 | 0.202 | 7.2 | 3.2 | 0.66968 | 52 | 88.9 | 0.2836 | 0.0507 | 14.25 | 13.11 | 14.04 | 0.93 | 1.659 | 2.47 | 8.981 | 2.5197 | 29.4 | 5 | 11 | 2019-01-21
2019-01-22 | Click Here | 0:00 | 5.32 | 5.34 | 5.44 | 5.39 | 5.41 | 7.07 | 7 | 1.53 | 1.86 | 1.8 | 1.84 | 50 | 43 | 28 | 3 | 0 | 0 | 0.279 | 0.426 | 1.3 | 0.163 | 0.371 | 0.581 | 14.8 | 33.3 | 26.9 | 28.3 | 38.5 | 29.6 | 66.6 | 53.8 | 56.6 | 77 | 3.26 | 16.64 | 3.2 | 5.9 | 0.066 | 7.6 | 3.3 | 0.82548 | 51.8 | 90.5 | 0.2849 | 0.043 | 14.53 | 13.37 | 14.36 | 0.99 | 1.679 | 2.492 | 9.199 | 2.6955 | 29.34 | 5 | 11 | 2019-01-22
2019-01-23 | Click Here | 0:00 | 5.6 | 5.29 | 5.35 | 5.41 | 5.47 | 7 | 6.91 | 1.55 | 1.9 | 1.86 | 1.84 | 52 | 46 | 27 | 1 | 0 | 0 | 0.254 | 0.367 | 1.264 | 0.109 | 0.217 | 0.36 | 14.6 | 32.9 | 26.5 | 27.8 | 37.9 | 29.2 | 65.8 | 53 | 55.6 | 75.8 | 3.36 | 17.36 | 3.4 | 6 | 0.074 | 7.5 | 3.3 | 0.91012 | 52 | 90.7 | 0.2819 | 0.0418 | 15.06 | 13.946 | 14.926 | 0.98 | 1.648 | 2.491 | 9.807 | 2.7801 | 29.82 | 5 | 11 | 2019-01-23
2019-01-24 | Click Here | 0:00 | 6.01 | 5.89 | 5.38 | 6.16 | 6.19 | 7.01 | 6.89 | 1.49 | 1.86 | 1.69 | 1.64 | 49 | 42 | 20 | 2 | 0 | 0 | 0.347 | 0.448 | 0.967 | 0.164 | 0.261 | 0.452 | 14.5 | 33.3 | 25.7 | 27.4 | 38.1 | 29 | 66.6 | 51.4 | 54.8 | 76.2 | 3.49 | 18.34 | 2.4 | 5.6 | 0.98 | 7.1 | 3.5 | 0.90749 | 51.9 | 90.1 | 0.284 | 0.0447 | 14.38 | 13.36 | 14.3 | 0.94 | 1.677 | 2.485 | 9.198 | 2.6975 | 26.86 | 5 | 11 | 2019-01-24
2019-01-25 | Click Here | 0:00 | 6.67 | 5.64 | 5.62 | 5.61 | 5.54 | 6.92 | 6.07 | 1.41 | 1.69 | 1.7 | 1.71 | 53 | 46 | 21 | 3 | 1 | 0 | 0.346 | 0.463 | 1.32 | 0.366 | 0.301 | 0.595 | 14 | 33.8 | 25.8 | 27 | 36.9 | 28 | 67.6 | 51.6 | 54 | 73.8 | 3.35 | 19.15 | 2.6 | 5.8 | 0.084 | 7.5 | 3.5 | 1.0586 | 45.8 | 85.9 | 0.3383 | 0.0658 | 13.999 | 12.843 | 13.823 | 0.98 | 1.675 | 2.459 | 8.709 | 2.7686 | 27.55 | 4.8 | 11 | 2019-01-25
2019-01-26 | Click Here | 0:00 | 6.71 | 5.57 | 5.24 | 5.38 | 5.37 | 5.95 | 6.78 | 1.47 | 1.84 | 1.69 | 1.72 | 52 | 47 | 24 | 2 | 1 | 0 | 0.371 | 0.466 | 1.13 | 0.174 | 0.363 | 0.501 | 13.8 | 34.8 | 27.7 | 28.7 | 37.9 | 27.6 | 69.6 | 55.4 | 57.4 | 75.8 | 3.34 | 17.39 | 2.6 | 5.4 | 0.093 | 6.7 | 3.3 | 1.0884 | 45.7 | 87 | 0.3393 | 0.0602 | 14.34 | 13.27 | 14.25 | 0.98 | 0 | 0 | 0 | 2.8184 | 0 | 4.9 | 11.6 | 2019-01-26
2019-01-27 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 1.4215 | 0 | 0 | 0 | 0 | 15.789 | 13.862 | 15.816 | 1.954 | 1.581 | 2.433 | 9.848 | 3.1415 | 0 | 4.9 | 11.6 | 2019-01-27
2019-01-28 | Click Here | 0:00 | 5.71 | 5.11 | 5.2 | 5.42 | 5.4 | 6.15 | 6.84 | 1.62 | 1.94 | 1.76 | 1.65 | 50 | 43 | 21 | 1 | 0 | 0 | 0.341 | 0.479 | 1.2 | 0.159 | 0.546 | 0.908 | 13.9 | 34.8 | 27.5 | 29.4 | 38 | 27.8 | 69.6 | 55 | 58.8 | 76 | 3.29 | 17.86 | 2.9 | 5.7 | 0.087 | 6.9 | 3.7 | 1.0904 | 46.2 | 89.4 | 0.3353 | 0.0493 | 16.954 | 15.891 | 16.866 | 0.975 | 1.674 | 2.484 | 11.733 | 2.8104 | 30.7 | 4.9 | 11.6 | 2019-01-28
2019-01-29 | Click Here | 0:00 | 5.69 | 5.52 | 5.41 | 5.53 | 5.51 | 6.29 | 7.05 | 1.42 | 1.77 | 1.68 | 2.01 | 54 | 47 | 21 | 1 | 0 | 0 | 0.311 | 0.47 | 3.25 | 0.174 | 0.389 | 0.589 | 13.9 | 35.2 | 28 | 29.1 | 39.2 | 27.8 | 70.4 | 56 | 58.2 | 78.4 | 3.27 | 18.3 | 3.1 | 5.8 | 0.094 | 7.1 | 3.3 | 1.402 | 48.9 | 88.4 | 0.3106 | 0.0536 | 14.79 | 12.65 | 14.09 | 1.44 | 1.677 | 2.514 | 8.459 | 3.482 | 29.64 | 5.2 | 11.8 | 2019-01-29
2019-01-30 | Click Here | 0:00 | 5.84 | 5.37 | 5.48 | 5.3 | 5.33 | 6.22 | 7.18 | 1.86 | 2.11 | 2.16 | 2.22 | 55 | 49 | 24 | 2 | 0 | 0 | 0.306 | 0.409 | 1.67 | 0.152 | 0.326 | 0.474 | 13.9 | 34.5 | 27.5 | 29 | 38.3 | 27.8 | 69 | 55 | 58 | 76.6 | 3.01 | 17.76 | 3.3 | 5.9 | 0.106 | 7.1 | 3.2 | 0.77273 | 48.2 | 81.1 | 0.3169 | 0.0905 | 15.578 | 13.683 | 14.66 | 0.977 | 1.663 | 2.525 | 0 | 3.0127 | 30.44 | 5.2 | 12.4 | 2019-01-30
2019-01-31 | Click Here | 0:00 | 5.81 | 5.22 | 5.35 | 5.31 | 5.3 | 6.36 | 7.31 | 1.38 | 2.07 | 1.89 | 2.01 | 55 | 47 | 16 | 1 | 0 | 0 | 0.361 | 0.443 | 0.703 | 0.146 | 0.317 | 0.585 | 12.8 | 34.3 | 27.5 | 30.2 | 40.3 | 25.6 | 68.6 | 55 | 60.4 | 80.6 | 3.15 | 16.33 | 3.6 | 5.5 | 0.053 | 6.1 | 3.3 | 0.68959 | 47 | 87.6 | 0.3271 | 0.0573 | 14.15 | 13.06 | 14.06 | 1 | 1.682 | 2.515 | 8.863 | 2.9896 | 30.71 | 5.2 | 12.8 | 2019-01-31
2019-02-01 | Click Here | 0:00 | 5.83 | 5.32 | 5.46 | 5.33 | 5.35 | 7.46 | 7.5 | 1.8 | 2 | 1.74 | 2.17 | 58 | 49 | 20 | 4 | 0 | 0 | 0.26 | 0.405 | 0.568 | 0.196 | 0.398 | 0.745 | 13.1 | 32.4 | 27.1 | 27.3 | 40.4 | 26.2 | 64.8 | 54.2 | 54.6 | 80.8 | 2.71 | 14.23 | 3.8 | 4.7 | 0.031 | 6.1 | 3.2 | 0.97348 | 49.2 | 89.9 | 0.3079 | 0.046 | 13.32 | 12.12 | 13.11 | 0.99 | 1.672 | 2.533 | 7.915 | 2.9735 | 30.51 | 5.4 | 13 | 2019-02-01
2019-02-02 | Click Here | 0:00 | 5.87 | 5.23 | 5.32 | 5.39 | 5.5 | 7.93 | 8.22 | 1.84 | 2.04 | 2.07 | 2.04 | 56 | 48 | 16 | 1 | 0 | 0 | 0.256 | 0.39 | 0.541 | 0.182 | 0.196 | 0.302 | 13.2 | 32.2 | 27.4 | 27.5 | 38.8 | 26.4 | 64.4 | 54.8 | 55 | 77.6 | 2.84 | 14.79 | 3.9 | 5 | 0.037 | 6 | 3.1 |  | 49.4 | 90.2 | 0.3061 | 0.0452 | 18.01 | 17.09 | 18.05 | 0.96 | 0 | 0 | 0 |  | 29.81 | 5.4 | 12 | 2019-02-02
2019-02-03 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-02-03
2019-02-04 | Click Here | 0:00 | 6.01 | 5.58 | 5.38 | 5.51 | 5.49 | 6.91 | 7.69 | 1.86 | 2.06 | 2.08 | 2.05 | 56 | 47 | 15 | 0 | 0 | 0 | 0.251 | 0.374 | 0.089 | 0.093 | 0.161 | 0.197 | 13.1 | 31.9 | 27 | 27.7 | 41.4 | 26.2 | 63.8 | 54 | 55.4 | 82.8 | 2.83 | 15.66 | 3.7 | 5.6 | 0.046 | 6.5 | 3.1 | 0.5313 | 51.2 | 89.7 | 0.2908 | 0.0468 | 15.695 | 13.686 | 15.641 | 1.955 | 1.726 | 2.583 | 9.377 | 2.5513 | 29.43 | 5.4 | 11 | 2019-02-04
2019-02-05 | Click Here | 0:00 | 5.84 | 5.39 | 5.39 | 5.41 | 5.46 | 7.25 | 7.47 | 1.8 | 2.02 | 2.01 | 1.99 | 57 | 48 | 18 | 1 | 0 | 0 | 0.298 | 0.367 | 0.76 | 0.086 | 0.131 | 0.176 | 12.4 | 31.7 | 25.6 | 25.9 | 40.4 | 24.8 | 63.4 | 51.2 | 51.8 | 80.8 | 2.8 | 15.17 | 3.4 | 5.9 | 0.057 | 5.5 | 3 | 0.68139 | 47 | 89.7 | 0.3278 | 0.0472 | 14.6 | 14.4 | 14.4 | 0 | 1.715 | 2.661 | 10.024 | 2.7114 | 28.02 | 5.2 | 11 | 2019-02-05
2019-02-06 | Click Here | 0:00 | 5.83 | 5.27 | 5.38 | 5.55 | 5.56 | 8.22 | 7.16 | 1.66 | 2.03 | 1.9 | 1.99 | 59 | 51 | 19 | 2 | 0 | 0 | 0.239 | 0.362 | 0.723 | 0.073 | 0.127 | 0.178 | 13.1 | 32 | 26 | 25.7 | 40.2 | 26.2 | 64 | 52 | 51.4 | 80.4 | 2.84 | 15.68 | 3.3 | 5.7 | 0.049 | 6.7 | 3 | 0.63758 | 47.6 | 90.2 | 0.3218 | 0.0448 | 13.51 | 12.38 | 13.35 | 0.97 | 1.732 | 2.729 | 7.919 | 2.5876 | 29.11 | 5.2 | 11 | 2019-02-06
2019-02-07 | Click Here | 0:00 | 5.81 | 5.39 | 5.29 | 5.54 | 5.58 | 7.85 | 6.64 | 1.66 | 2.03 | 2.12 | 1.77 | 59 | 52 | 20 | 1 | 0 | 0 | 0.232 | 0.358 | 0.852 | 0.071 | 0.184 | 0.276 | 13.2 | 30.3 | 26.3 | 26.2 | 39.2 | 26.4 | 60.6 | 52.6 | 52.4 | 78.4 | 3.28 | 16.25 | 3.6 | 6.2 | 0.126 | 6.9 | 3.2 | 0.72771 | 47.8 | 89.6 | 0.3199 | 0.0474 | 14.67 | 13.56 | 13.56 | 0.97 | 1.769 | 2.745 | 9.046 | 2.6577 | 29.57 | 5.2 | 10.3 | 2019-02-07
2019-02-08 | Click Here | 0:00 | 5.9 | 5.26 | 5.23 | 5.47 | 5.5 | 7.21 | 7.33 | 1.7 | 2.1 | 2.01 | 1.97 | 56 | 49 | 12 | 0 | 0 | 0 | 0.267 | 0.351 | 0.496 | 0.068 | 0.147 | 0.243 | 13.2 | 32.4 | 26.3 | 26.6 | 39.5 | 26.4 | 64.8 | 52.6 | 53.2 | 79 | 3.31 | 17.54 | 3.7 | 5.9 | 0.114 | 6.9 | 3.2 | 1.0387 | 50.7 | 91.7 | 0.2949 | 0.0376 | 13.386 | 12.203 | 13.185 | 0.982 | 1.585 | 2.778 | 7.84 | 2.9287 | 30.09 | 5.2 | 10.3 | 2019-02-08
2019-02-09 | Click Here | 0:00 | 5.87 | 5.37 | 5.25 | 5.41 | 5.5 | 7.2 | 7.35 | 1.77 | 2.09 | 1.95 | 1.95 | 51 | 45 | 12 | 0 | 0 | 0 | 0.261 | 0.347 | 0.312 | 0.047 | 0.107 | 0.192 | 13.4 | 32.7 | 26.4 | 26.9 | 40.2 | 26.8 | 65.4 | 52.8 | 53.8 | 80.4 | 3.23 | 18.11 | 3.4 | 5.9 | 0.096 | 7 | 3.3 | 0.92259 | 50.5 | 92.1 | 0.2954 | 0.0327 | 14.05 | 12.94 | 13.92 | 0.98 | 0 | 0 | 0 | 2.8626 | 30.21 | 5.2 | 10.3 | 2019-02-09
2019-02-10 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-02-10
2019-02-11 | Click Here | 0:00 | 5.82 | 5.54 | 5.25 | 5.56 | 5.61 | 7.85 | 7.26 | 1.87 | 2 | 2.05 | 1.94 | 59 | 52 | 20 | 1 | 0 | 0 | 0.237 | 0.345 | 0.676 | 0.068 | 0.151 | 0.205 | 13.3 | 32.4 | 26.1 | 26.7 | 39.4 | 26.6 | 64.8 | 52.2 | 53.4 | 78.8 | 3.19 | 18.69 | 3.2 | 7.8 | 0.156 | 6.1 | 3.2 | 0.53435 | 58 | 89.9 | 0.3186 | 0.0463 | 14.54 | 13.43 | 14.39 | 0.96 | 1.656 | 2.834 | 8.94 | 2.5344 | 30.04 | 5.2 | 10.3 | 2019-02-11
2019-02-12 | Click Here | 0:00 | 5.84 | 5.13 | 5.52 | 5.48 | 5.54 | 7.66 | 7.8 | 1.92 | 2.04 | 2.11 | 1.96 | 56 | 49 | 17 | 0 | 0 | 0 | 0.228 | 0.337 | 0.78 | 0.071 | 0.21 | 0.241 | 13.4 | 33.1 | 26.3 | 26.4 | 39.1 | 26.8 | 66.2 | 52.6 | 52.8 | 78.2 | 3.03 | 17.72 | 3.3 | 6.8 | 0.135 | 6.8 | 3.4 | 0.86415 | 48.3 | 89.5 | 0.316 | 0.0478 | 14.37 | 13.26 | 14.23 | 0.97 | 1.56 | 2.838 | 8.862 | 2.9442 | 30.51 | 5.2 | 10.3 | 2019-02-12
2019-02-13 | Click Here | 0:00 | 5.91 | 5.2 | 5.13 | 5.44 | 5.51 | 7.47 | 7.65 | 1.9 | 2.17 | 2.2 | 2.26 | 54 | 47 | 14 | 0 | 0 | 0 | 0.267 | 0.34 | 0.614 | 0.063 | 0.179 | 0.243 | 13.4 | 33.3 | 26.5 | 26.7 | 39.5 | 26.8 | 66.6 | 53 | 53.4 | 79 | 3.21 | 18.24 | 3.2 | 6.6 | 0.114 | 6.7 | 3.5 | 0.63972 | 49.8 | 99.3 | 0.3022 | 0.003 | 14.91 | 13.749 | 14.722 | 0.973 | 1.556 | 2.836 | 9.357 | 2.8097 | 29.94 | 5.2 | 10.3 | 2019-02-13
2019-02-14 | Click Here | 0:00 | 5.9 | 5.53 | 5.13 | 5.44 | 5.47 | 7 | 7.43 | 1.86 | 2.07 | 2.14 | 2.19 | 49 | 41 | 12 | 0 | 0 | 0 | 0.247 | 0.331 | 0.504 | 0.098 | 0.1 | 0.147 | 13.4 | 33.1 | 26.6 | 27 | 40.2 | 26.8 | 66.2 | 53.2 | 54 | 80.4 | 3.3 | 16.86 | 3.4 | 6 | 0.109 | 6.8 | 3.4 | 0.72564 | 49.2 | 90.6 | 0.3072 | 0.0426 | 14.62 | 13.51 | 14.48 | 0.97 | 0 | 0 | 0 | 2.8856 | 29.71 | 5.2 | 10.3 | 2019-02-14
2019-02-15 | Click Here | 0:00 | 5.96 | 5.57 | 5.53 | 5.47 | 5.49 | 6.83 | 6.94 | 1.82 | 2.01 | 2.04 | 1.99 | 50 | 43 | 14 | 1 | 0 | 0 | 0.249 | 0.337 | 0.742 | 0.094 | 0.214 | 0.386 | 13.6 | 33.8 | 27.7 | 26.8 | 39.8 | 27.2 | 67.6 | 55.4 | 53.6 | 79.6 | 3.21 | 16.36 | 3.1 | 6.3 | 0.081 | 7 | 3.3 | 0.77776 | 47.5 | 88.9 | 0.323 | 0.051 | 13.986 | 12.852 | 13.823 | 0.971 | 1.62 | 2.842 | 8.39 | 2.9278 | 29.62 | 5.2 | 10.3 | 2019-02-15
2019-02-16 | Click Here | 0:00 | 5.93 | 5.4 | 5.53 | 5.44 | 5.46 | 6.75 | 6.91 | 1.95 | 2.19 | 2.2 | 2.24 | 49 | 44 | 12 | 0 | 0 | 0 | 0.238 | 0.331 | 0.758 | 0.084 | 0.221 | 0.391 | 13.6 | 33.8 | 26.5 | 26.7 | 39.9 | 27.2 | 67.6 | 53 | 53.4 | 79.8 | 2.95 | 16.69 | 3.2 | 6 | 0.072 | 6.9 | 3.3 | 0.66341 | 49.7 | 90.6 | 0.3196 | 0.0429 | 14.57 | 13.48 | 14.44 | 0.96 | 0 | 0 | 0 | 2.8934 | 29.97 | 5.2 | 10.3 | 2019-02-16
2019-02-17 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.74512 | 0 | 0 | 0 | 0 | 14.539 | 13.417 | 14.392 | 0.975 | 1.588 | 2.82 | 9.008 | 2.9151 | 0 | 5.2 | 10.3 | 2019-02-17
2019-02-18 | Click Here | 0:00 | 5.94 | 5.39 | 5.43 | 5.4 | 5.52 | 7.02 | 6.95 | 1.87 | 2.14 | 2.04 | 2.1 | 47 | 40 | 13 | 0 | 0 | 0 | 0.204 | 0.334 | 0.614 | 0.072 | 0.221 | 0.352 | 13.5 | 33.9 | 26.7 | 27 | 40.2 | 27 | 67.8 | 53.4 | 54 | 80.4 | 3.15 | 17.92 | 3.3 | 5.9 | 0.069 | 6.9 | 3.4 | 0.7604 | 49.9 | 90.8 | 0.3184 | 0.0418 | 14.755 | 13.576 | 14.558 | 0.982 | 1.648 | 2.808 | 9.12 | 2.9104 | 29.82 | 5.2 | 10.3 | 2019-02-18
2019-02-19 | Click Here | 0:00 | 6 | 5.37 | 5.43 | 5.43 | 5.5 | 7.09 | 6.99 | 1.9 | 2.17 | 2.16 | 2.19 | 50 | 42 | 16 | 0 | 0 | 0 | 0.212 | 0.327 | 0.61 | 0.079 | 0.174 | 0.291 | 14.1 | 34.2 | 26.8 | 27.2 | 39.9 | 28.2 | 68.4 | 53.6 | 54.4 | 79.8 | 3.36 | 18 | 3.4 | 5.9 | 0.112 | 6.6 | 3.3 | 0.68895 | 50.1 | 91.9 | 0.3152 | 0.0374 | 14.89 | 13.8 | 14.78 | 0.98 | 1.668 | 2.693 | 9.438 | 2.8289 | 29.02 | 5.2 | 10.3 | 2019-02-19
2019-02-20 | Click Here | 0:00 | 5.97 | 5.74 | 5.4 | 5.57 | 5.54 | 6.71 | 6.91 | 1.94 | 2.18 | 2.18 | 2.2 | 51 | 46 | 18 | 1 | 0 | 0 | 0.224 | 0.326 | 0.718 | 0.093 | 0.264 | 1 | 13.3 | 32.4 | 26.8 | 24.9 | 39.6 | 26.6 | 64.8 | 53.6 | 49.8 | 79.2 | 3.19 | 16.32 | 3.2 | 6.1 | 0.091 | 6.7 | 3.4 | 0.8287 | 50.3 | 91.6 | 0.315 | 0.0371 | 13.984 | 12.73 | 13.71 | 0.98 | 1.682 | 2.656 | 8.392 | 2.9387 | 28.94 | 5.2 | 10.3 | 2019-02-20
2019-02-21 | Click Here | 0:00 | 5.85 | 5.65 | 5.58 | 5.55 | 5.51 | 6.76 | 6.93 | 1.76 | 2.08 | 2.2 | 2.24 | 50 | 45 | 20 | 2 | 0 | 0 | 0.217 | 0.326 | 0.718 | 0.077 | 0.217 | 0.351 | 13.8 | 30.2 | 26 | 26.8 | 40.7 | 27.6 | 60.4 | 52 | 53.6 | 81.4 | 3.12 | 16.71 | 3.4 | 5.8 | 0.094 | 3.4 | 5.8 | 0.7137 | 45.9 | 91.2 | 0.3373 | 0.0401 | 14.84 | 13.73 | 14.71 | 0.98 | 1.72 | 2.664 | 9.346 | 2.8437 | 27.85 | 5.2 | 10.3 | 2019-02-21
2019-02-22 | Click Here | 0:00 | 5.95 | 5.45 | 5.58 | 5.51 | 5.52 | 7.43 | 6.92 | 1.72 | 1.91 | 2.09 | 2.23 | 52 | 46 | 18 | 0 | 0 | 0 | 0.225 | 0.33 | 0.953 | 0.102 | 0.277 | 0.358 | 14.2 | 31.5 | 26.2 | 26.6 | 39.5 | 28.4 | 63 | 52.4 | 53.2 | 79 | 3.37 | 17.74 | 3.5 | 6 | 0.038 | 6.5 | 3.2 | 0.69036 | 48.5 | 88.6 | 0.3142 | 0.0522 | 15.45 | 14.35 | 15.3 | 0.95 | 1.695 | 2.669 | 9.986 | 2.8604 | 29.57 | 5.1 | 10.3 | 2019-02-22
2019-02-23 | Click Here | 0:00 | 5.86 | 5.46 | 5.44 | 5.54 | 5.59 | 7.38 | 7.42 | 1.73 | 1.96 | 2.11 | 2.14 | 51 | 45 | 17 | 0 | 0 | 0 | 0.223 | 0.329 | 0.927 | 0.096 | 0.286 | 0.38 | 14.3 | 30.9 | 27 | 26.5 | 40.1 | 28.6 | 61.8 | 54 | 53 | 80.2 | 3.19 | 17.51 | 3.6 | 5.8 | 0.046 | 6.5 | 3.2 |  | 48.4 | 89.7 | 0.3146 | 0.0488 | 14.35 | 14.1 | 14.1 | 0 | 0 | 0 | 0 |  | 29.57 | 5.1 | 10.3 | 2019-02-23
2019-02-24 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-02-24
2019-02-25 | Click Here | 0:00 | 5.91 | 5.87 | 5.47 | 5.74 | 5.67 | 6.79 | 7.66 | 1.688 | 2 | 2.06 | 2.09 | 50 | 44 | 20 | 1 | 0 | 0 | 0.236 | 0.324 | 0.918 | 0.249 | 0.264 | 0.371 | 14.3 | 33.7 | 26.3 | 27.4 | 41.1 | 28.6 | 67.4 | 52.6 | 54.8 | 82.2 | 3.03 | 17.03 | 3.5 | 5.9 | 0.092 | 6.5 | 3.3 | 0.81561 | 48.2 | 90.6 | 0.3167 | 0.0428 | 15.182 | 14.005 | 14.986 | 0.981 | 1.667 | 2.708 | 9.63 | 2.8556 | 26.77 | 5.1 | 10.3 | 2019-02-25
2019-02-26 | Click Here | 0:00 | 5.89 | 5.53 | 5.41 | 5.49 | 5.53 | 6.91 | 6.71 | 1.67 | 1.96 | 1.96 | 2.02 | 51 | 46 | 20 | 1 | 0 | 0 | 0.236 | 0.337 | 1.08 | 0.104 | 0.246 | 0.327 | 14.7 | 33.1 | 26.7 | 26.9 | 40.6 | 29.4 | 66.2 | 53.4 | 53.8 | 81.2 | 3.16 | 16.93 | 4.4 | 7.3 | 0.044 | 6.5 | 3.3 | 0.90045 | 46.4 | 89.2 | 0.3333 | 0.0494 | 15.13 | 13.95 | 14.91 | 0.96 | 1.666 | 2.702 | 9.582 | 2.8705 | 29.23 | 4.8 | 10.3 | 2019-02-26
2019-02-27 | Click Here | 0:00 | 5.79 | 5.48 | 5.62 | 5.57 | 5.57 | 7.59 | 6.87 | 1.66 | 1.89 | 1.99 | 1.96 | 50 | 43 | 16 | 0 | 0 | 0 | 0.232 | 0.341 | 1.05 | 0.12 | 0.293 | 0.406 | 14.8 | 34 | 26.9 | 27.5 | 41.4 | 29.6 | 68 | 53.8 | 55 | 82.8 | 3.47 | 17.69 | 3.7 | 6.2 | 0.057 | 7.1 | 3.4 | 0.39614 | 48.4 | 90.3 | 0.3161 | 0.0435 | 15.31 | 14.02 | 14.99 | 0.97 | 1.642 | 2.736 | 9.642 | 2.3561 | 30.04 | 4.8 | 10.6 | 2019-02-27
2019-02-28 | Click Here | 0:00 | 5.82 | 5.25 | 5.56 | 5.47 | 5.49 | 7.6 | 7.6 | 1.69 | 1.87 | 1.96 | 1.84 | 50 | 54 | 22 | 0 | 0 | 0 | 0.234 | 0.335 | 1.04 | 0.113 | 0.271 | 0.357 | 14.6 | 30.9 | 26.8 | 27.6 | 41 | 29.2 | 61.8 | 53.6 | 55.2 | 82 | 3.95 | 1.97 | 3.8 | 6.3 | 0.141 | 6.4 | 3.4 | 0.52548 | 45.7 | 84.1 | 0.3393 | 0.0751 | 15.35 | 14.27 | 15.23 | 0.96 | 1.672 | 2.724 | 9.874 | 2.4555 | 29.81 | 4.8 | 10.6 | 2019-02-28
2019-03-01 | Click Here | 0:00 | 5.94 | 5.19 | 5.23 | 5.42 | 5.46 | 7.54 | 7.77 | 1.7 | 1.94 | 1.99 | 1.95 | 51 | 47 | 24 | 0 | 0 | 0 | 0.194 | 0.126 | 0.894 | 0.107 | 0.219 | 0.417 | 14.3 | 31.4 | 26.1 | 26.5 | 40.7 | 28.6 | 62.8 | 52.2 | 53 | 81.4 | 3.27 | 15.26 | 3.4 | 5.9 | 0.126 | 6.4 | 3.3 | 0.90872 | 48.9 | 90 | 0.3074 | 0.0449 | 15.57 | 14.448 | 15.43 | 0.982 | 1.652 | 2.723 | 10.073 | 2.8887 | 29.5 | 4.8 | 10.6 | 2019-03-01
2019-03-02 | Click Here | 0:00 | 5.8 | 5.23 | 5.19 | 5.5 | 5.59 | 7.6 | 7.79 | 1.64 | 1.89 | 1.94 | 1.9 | 50 | 43 | 17 | 0 | 0 | 0 | 0.179 | 0.174 | 0.91 | 0.126 | 0.186 | 0.336 | 13.9 | 32.1 | 26.5 | 27.2 | 41.4 | 27.8 | 64.2 | 53 | 54.4 | 82.8 | 3 | 12.59 | 4 | 6.4 | 0.072 | 6.4 | 3.3 | 0.95901 | 48.6 | 89.8 | 0.309 | 0.0482 | 15.23 | 14.11 | 15.07 | 0.96 | 0 | 0 | 0 | 2.909 | 29.64 | 4.8 | 10.6 | 2019-03-02
2019-03-03 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-03-03
2019-03-04 | Click Here | 0:00 | 5.75 | 5.41 | 5.16 | 5.39 | 5.46 | 7.48 | 7.66 | 1.74 | 1.94 | 2.01 | 1.93 | 60 | 53 | 27 | 2 | 0 | 0 | 0.237 | 0.241 | 1.11 | 0.173 | 0.304 | 0.511 | 14.8 | 34.6 | 27.1 | 26.3 | 41.1 | 29.6 | 69.2 | 54.2 | 52.6 | 82.2 | 2.76 | 1.78 | 3.8 | 10.2 | 0.126 | 6.9 | 3.6 | 0.66729 | 45.7 | 84.3 | 0.3401 | 0.0741 | 15.39 | 14.26 | 15.26 | 1 | 1.722 | 2.72 | 9.818 | 2.5973 | 29.57 | 4.8 | 10.6 | 2019-03-04
2019-03-05 | Click Here | 0:00 | 5.9 | 5.47 | 5.4 | 5.55 | 5.61 | 7.55 | 7.44 | 1.62 | 1.99 | 2.04 | 1.92 | 60 | 52 | 29 | 1 | 0 | 0 | 0.225 | 0.33 | 1.12 | 0.111 | 0.327 | 0.512 | 15.5 | 35.2 | 27.1 | 28 | 40.8 | 31 | 40.4 | 54.2 | 56 | 81.6 | 2.47 | 1.75 | 3.8 | 10 | 0.058 | 7.4 | 3.6 | 0.82043 | 47.9 | 86.8 | 0.319 | 0.0612 | 15.48 | 14.4 | 15.33 | 0.93 | 1.855 | 2.714 | 9.831 | 2.8504 | 30.51 | 4.8 | 10.6 | 2019-03-05
2019-03-06 | Click Here | 0:00 | 6.01 | 5.38 | 5.49 | 5.47 | 5.54 | 7.41 | 7.58 | 1.7 | 2.01 | 1.98 | 2 | 49 | 42 | 51 | 1 | 0 | 0 | 0.219 | 0.336 | 2.67 | 0.24 | 0.4 | 0.886 | 15.4 | 34.4 | 27.2 | 27.7 | 41.1 | 30.8 | 68.8 | 54.4 | 55.4 | 82.2 | 2.64 | 7.71 | 3.7 | 8.6 | 0.074 | 7.4 | 3.5 | 0.81703 | 47.7 | 88.3 | 0.3212 | 0.0538 | 16.97 | 15.01 | 15.98 | 0.97 | 1.954 | 2.721 | 0 | 2.887 | 29.92 | 4.8 | 10.6 | 2019-03-06
2019-03-07 | Click Here | 0:00 | 5.92 | 5.36 | 5.51 | 5.49 | 5.57 | 7.54 | 7.64 | 1.77 | 2.09 | 2.05 | 2.08 | 49 | 43 | 26 | 1 | 0 | 0 | 0.243 | 0.331 | 1.94 | 0.187 | 0.192 | 0.568 | 15.4 | 43.7 | 26.9 | 28.2 | 41.4 | 30.8 | 69.4 | 53.8 | 56.4 | 82.8 | 2.68 | 12.16 | 4.7 | 6.9 | 0.091 | 6.9 | 3.7 | 0.79782 | 48.1 | 89.2 | 0.319 | 0.0465 | 16.77 | 14.61 | 15.58 | 0.97 | 1.984 | 2.719 | 9.907 | 2.8778 | 30.06 | 4.8 | 10.6 | 2019-03-07
2019-03-08 | Click Here | 0:00 | 5.72 | 5.53 | 5.36 | 5.5 | 5.53 | 6.54 | 7.64 | 1.72 | 2.01 | 2.02 | 2 | 50 | 44 | 16 | 1 | 0 | 0 | 0.236 | 0.336 | 1.07 | 0.113 | 0.206 | 0.474 | 15 | 36.1 | 27.1 | 28.2 | 41.5 | 30 | 72.2 | 54.2 | 56.4 | 83 | 2.79 | 14.31 | 4.4 | 6.7 | 0.083 | 6.6 | 3.6 | 0.85304 | 48.3 | 87.5 | 0.3188 | 0.0572 | 15.25 | 14.1 | 15.09 | 0.99 | 0 | 0 | 0 | 2.893 | 32.08 | 4.8 | 10.6 | 2019-03-08
2019-03-09 | Click Here | 0:00 | 6.22 | 5.51 | 5.49 | 5.63 | 5.6 | 6.68 | 7.24 | 1.61 | 1.78 | 1.81 | 1.74 | 50 | 43 | 18 | 2 | 0 | 0 | 0.263 | 0.341 | 0.781 | 0.071 | 0.206 | 0.454 | 15.2 | 36.1 | 28.6 | 29.2 | 41.3 | 30.4 | 72.2 | 57.2 | 58.4 | 82.6 | 2.89 | 13.1 | 4.3 | 6.2 | 0.061 | 6.9 | 3.6 | 0.92514 | 46.7 | 86.5 | 0.33 | 0.0627 | 15.72 | 14.56 | 15.54 | 0.98 | 0 | 0 | 0 | 2.9151 | 30.99 | 4.6 | 10.6 | 2019-03-09
2019-03-10 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.87082 | 0 | 0 | 0 | 0 | 15.895 | 14.715 | 15.685 | 0.97 | 1.907 | 2.727 | 10.081 | 2.8008 | 0 | 4 | 10.6 | 2019-03-10
2019-03-11 | Click Here | 0:00 | 5.92 | 5.26 | 5.48 | 5.44 | 5.47 | 7.11 | 7.23 | 1.67 | 2.06 | 1.94 | 1.88 | 52 | 46 | 14 | 1 | 0 | 0 | 0.286 | 0.341 | 0.699 | 0.106 | 0.642 | 0.904 | 15.4 | 33 | 27.4 | 28.5 | 39.8 | 30.8 | 66 | 54.8 | 57 | 79.6 | 2.79 | 13.82 | 3.9 | 6.9 | 0.074 | 6.7 | 3.6 | 1.0787 | 48.8 | 88.3 | 0.3209 | 0.0538 | 17.071 | 15.939 | 16.91 | 0.971 | 1.84 | 2.726 | 11.373 | 2.9287 | 30.34 | 4 | 10.6 | 2019-03-11
2019-03-12 | Click Here | 0:00 | 6.1 | 5.49 | 5.21 | 5.67 | 5.92 | 7.5 | 7.18 | 1.57 | 1.88 | 1.86 | 1.84 | 49 | 44 | 14 | 0 | 0 | 0 | 0.296 | 0.346 | 0.674 | 0.123 | 0.217 | 0.51 | 15.6 | 35.2 | 28.3 | 29.4 | 40.3 | 31.2 | 70.4 | 56.6 | 58.8 | 80.6 | 3.37 | 21.6 | 4.9 | 6.7 | 0.036 | 7.2 | 3.9 | 1.0406 | 48.5 | 87.7 | 0.322 | 0.0567 | 15.58 | 14.45 | 15.42 | 0.97 | 1.699 | 2.718 | 10.033 | 2.8406 | 30.78 | 4 | 10.6 | 2019-03-12
2019-03-13 | Click Here | 0:00 | 5.81 | 5.33 | 5.4 | 5.3 | 5.35 | 6.89 | 7.48 | 1.63 | 1.97 | 1.8 | 1.79 | 50 | 43 | 17 | 1 | 0 | 0 | 0.274 | 0.332 | 0.851 | 0.072 | 0.226 | 0.553 | 15.7 | 35 | 28.4 | 29.2 | 40.2 | 31.4 | 70 | 56.8 | 58.4 | 80.4 | 3.27 | 19.11 | 4.7 | 6.5 | 0.078 | 7.6 | 3.7 | 1.1096 | 46.2 | 87.5 | 0.335 | 0.0576 | 14.703 | 13.558 | 14.535 | 0.977 | 1.671 | 2.72 | 9.167 | 2.9196 | 29.2 | 3.8 | 10.6 | 2019-03-13
2019-03-14 | Click Here | 0:00 | 6.16 | 5.42 | 5.39 | 5.43 | 5.49 | 6.69 | 6.92 | 1.59 | 1.9 | 1.94 | 1.93 | 48 | 44 | 16 | 1 | 0 | 0 | 0.252 | 0.347 | 0.788 | 0.093 | 0.271 | 0.52 | 15.5 | 31.6 | 26.4 | 26.7 | 39.1 | 31 | 63.2 | 52.8 | 53.4 | 78.2 | 3.19 | 20.91 | 4.3 | 5.9 | 0.058 | 7.2 | 3.6 | 1.143 | 48.9 | 88.5 | 0.3208 | 0.0536 | 14.97 | 13.76 | 14.73 | 0.97 | 1.659 | 2.716 | 9.385 | 2.983 | 29.03 | 3.8 | 10.6 | 2019-03-14
2019-03-15 | Click Here | 0:00 | 5.82 | 5.31 | 5.31 | 5.32 | 5.45 | 7.38 | 6.91 | 1.64 | 1.93 | 1.88 | 1.69 | 56 | 49 | 23 | 0 | 0 | 0 | 0.236 | 0.342 | 1.03 | 0.099 | 0.315 | 0.509 | 15.8 | 32.9 | 26.5 | 26.8 | 38.9 | 31.6 | 65.8 | 53 | 53.6 | 77.8 | 2.45 | 1.82 | 3.8 | 8.4 | 0.185 | 7.7 | 3.7 | 1.3345 | 47.4 | 87.9 | 0.3237 | 0.0559 | 14.85 | 13.69 | 14.69 | 1 | 1.632 | 2.718 | 9.34 | 3.1445 | 29.57 | 3.8 | 10.6 | 2019-03-15
2019-03-16 | Click Here | 0:00 | 5.86 | 5.32 | 5.3 | 5.41 | 5.49 | 7.3 | 7.21 | 1.61 | 1.79 | 1.87 | 1.8 | 55 | 47 | 21 | 0 | 0 | 0 | 0.229 | 0.344 | 0.961 | 0.094 | 0.323 | 0.512 | 15.6 | 32.4 | 27.1 | 26.5 | 38.1 | 31.2 | 64.8 | 54.2 | 53 | 76.2 | 2.94 | 1.95 | 3.7 | 7.8 | 0.141 | 7.7 | 3.7 |  | 49.1 | 88.4 | 0.3189 | 0.0513 | 14.8 | 13.64 | 14.6 | 0.96 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-03-16
2019-03-17 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-03-17
2019-03-18 | Click Here | 0:00 | 5.88 | 5.56 | 5.33 | 5.43 | 5.46 | 6.89 | 7.32 | 1.03 | 1.82 | 1.89 | 1.87 | 54 | 45 | 19 | 1 | 0 | 0 | 0.224 | 0.316 | 0.837 | 0.104 | 0.31 | 0.497 | 15.9 | 32.6 | 26.4 | 27.2 | 38.5 | 31.8 | 65.2 | 52.8 | 54.4 | 77 | 2.92 | 15.31 | 3.5 | 7.3 | 0.083 | 6.4 | 3.1 | 1.2529 | 49.3 | 88.6 | 0.3187 | 0.0511 | 15.61 | 13.59 | 15.56 | 1.97 | 1.648 | 2.812 | 9.13 | 3.1329 | 26 | 3.8 | 10.3 | 2019-03-18
2019-03-19 | Click Here | 0:00 | 5.8 | 5.07 | 5.28 | 5.14 | 5.17 | 6.01 | 6.73 | 1.88 | 2.12 | 1.97 | 1.95 | 54 | 48 | 21 | 4 | 2 | 0 | 0.241 | 0.315 | 0.585 | 0.066 | 0.241 | 0.592 | 16.4 | 37.1 | 29.1 | 29.2 | 39.3 | 32.8 | 74.2 | 58.2 | 58.4 | 78.6 | 2.81 | 1.58 | 4 | 6 | 0.113 | 7 | 3.2 | 0.68139 | 51.3 | 90.3 | 0.2899 | 0.0444 | 14.5 | 14.24 | 14.24 | 0 | 1.574 | 2.813 | 9.853 | 2.6714 | 31.36 | 3.8 | 10.3 | 2019-03-19
2019-03-20 | Click Here | 0:00 | 5.93 | 5.25 | 5.23 | 5.36 | 5.4 | 6.86 | 6.73 | 1.74 | 1.96 | 1.71 | 1.6 | 58 | 50 | 18 | 0 | 0 | 0 | 0.24 | 0.361 | 0.591 | 0.064 | 0.305 | 0.502 | 16.1 | 37.2 | 28.9 | 29.2 | 39.4 | 32.2 | 74.4 | 57.8 | 58.4 | 78.8 | 2.56 | 1.86 | 4.1 | 7.3 | 0.249 | 7.4 | 3.4 | 0.70373 | 49.6 | 89.1 | 0.3039 | 0.05 | 14.29 | 13.21 | 14.06 | 0.95 | 1.581 | 2.803 | 8.826 | 2.8037 | 33.33 | 3.9 | 10.7 | 2019-03-20
2019-03-21 | Click Here | 0:00 | 5.8 | 5.25 | 5.17 | 5.34 | 5.36 | 6.93 | 6.84 | 1.73 | 2 | 1.88 | 2.19 | 56 | 49 | 16 | 0 | 0 | 0 | 0.246 | 0.373 | 0.558 | 0.061 | 0.312 | 0.527 | 15.3 | 33.3 | 28.3 | 28.2 | 38.4 | 30.6 | 66.6 | 56.8 | 56.4 | 76.8 | 3.05 | 1.92 | 4.2 | 7.1 | 0.237 | 6.2 | 3.2 | 0.55694 | 49.7 | 89.3 | 0.3035 | 0.0491 | 14.96 | 13.81 | 14.78 | 0.97 | 0 | 0 | 0 | 2.5369 | 31.45 | 3.9 | 10.7 | 2019-03-21
2019-03-22 | Click Here | 0:00 | 5.92 | 5.19 | 5.25 | 5.39 | 5.42 | 7.14 | 7.22 | 1.69 | 1.99 | 1.94 | 1.77 | 55 | 49 | 19 | 0 | 0 | 0 | 0.219 | 0.011 | 0.514 | 0.139 | 0.301 | 0.496 | 15.6 | 31 | 25.4 | 25.9 | 37.4 | 31.2 | 62 | 50.8 | 51.8 | 74.8 | 3.07 | 1.88 | 3.9 | 6.8 | 0.186 | 7.5 | 3.2 |  | 48.5 | 87.5 | 0.314 | 0.0579 | 14.509 | 13.237 | 14.218 | 0.981 | 1.598 | 2.8 | 8.839 |  | 26.48 | 3.9 | 10.7 | 2019-03-22
2019-03-23 | Click Here | 0:00 | 5.88 | 5.24 | 5.32 | 5.33 | 5.39 | 7.14 | 7.25 | 1.78 | 2.07 | 1.99 | 1.91 | 54 | 47 | 14 | 0 | 0 | 0 | 0.226 | 0 | 0.49 | 0.104 | 0.332 | 0.506 | 15.2 | 31.4 | 24.8 | 25.1 | 38.6 | 30.4 | 62.8 | 49.6 | 50.2 | 77.2 | 2.72 | 1.9 | 4 | 6.9 | 0.154 | 7.4 | 3.3 | 0.88195 | 48.7 | 90.1 | 0.3129 | 0.0442 | 14.29 | 13.08 | 14.07 | 0.99 | 0 | 0 | 0 | 2.8319 | 29.44 | 3.9 | 10.7 | 2019-03-23
2019-03-24 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-03-24
2019-03-25 | Click Here | 0:00 | 5.84 | 5.38 | 5.3 | 5.48 | 5.49 | 6.91 | 7.07 | 1.61 | 1.89 | 1.75 | 1.94 | 59 | 51 | 27 | 2 | 0 | 0 | 0.238 | 0.384 | 0.918 | 0.099 | 0.291 | 0.443 | 16.2 | 33.3 | 26.7 | 27 | 38.4 | 32.4 | 66.6 | 53.4 | 54 | 76.8 | 3.02 | 1.86 | 3.8 | 6.8 | 0.183 | 7.4 | 3.3 | 0.24131 | 48.4 | 87.9 | 0.3145 | 0.0559 | 14.69 | 13.52 | 14.48 | 0.96 | 1.676 | 2.781 | 9.063 | 2.2213 | 28.17 | 3.9 | 10.7 | 2019-03-25
2019-03-26 | Click Here | 0:00 | 5.85 | 5.44 | 5.38 | 5.43 | 5.45 | 7 | 7.11 | 1.7 | 1.95 | 1.91 | 2.07 | 63 | 55 | 31 | 3 | 0 | 0 | 0.234 | 0.366 | 0.995 | 0.103 | 0.36 | 0.624 | 15.8 | 32.9 | 26.6 | 26.9 | 38.3 | 31.6 | 65.8 | 53.2 | 53.8 | 76.6 | 3.13 | 2.04 | 4.3 | 8.6 | 0.182 | 7.3 | 3.4 | 0.63712 | 48.3 | 88.3 | 0.3147 | 0.0547 | 14.7 | 13.49 | 14.47 | 0.98 | 1.61 | 2.777 | 9.103 | 2.5971 | 28.64 | 3.9 | 10.7 | 2019-03-26
2019-03-27 | Click Here | 0:00 | 5.94 | 5.39 | 5.44 | 5.41 | 5.47 | 7.14 | 7.2 | 1.67 | 1.92 | 1.92 | 1.87 | 59 | 51 | 22 | 1 | 0 | 0 | 0.21 | 0.367 | 0.724 | 0.126 | 0.211 | 0.429 | 15.4 | 33.1 | 26.7 | 27.2 | 39.2 | 30.8 | 66.2 | 53.4 | 54.4 | 78.4 | 3.31 | 2.14 | 4.5 | 7.9 | 0.174 | 7.2 | 3.3 | 1.0279 | 48.6 | 89.2 | 0.3127 | 0.0499 | 14.78 | 13.63 | 14.59 | 0.96 | 1.598 | 2.768 | 9.264 | 2.8879 | 27.87 | 3.9 | 10.7 | 2019-03-27
2019-03-28 | Click Here | 0:00 | 6.02 | 5.79 | 5.39 | 5.54 | 5.62 | 7.56 | 7.07 | 1.72 | 1.98 | 1.99 | 1.84 | 59 | 52 | 16 | 0 | 0 | 0 | 0.184 | 0.362 | 0.619 | 0.112 | 0.211 | 0.482 | 15.1 | 33.3 | 25.9 | 26.2 | 36.2 | 30.2 | 66.6 | 51.8 | 52.4 | 72.4 | 3.13 | 2.87 | 4 | 6.7 | 0.141 | 7.4 | 4 | 0.98162 | 47.2 | 90.2 | 0.3254 | 0.0448 | 14.4 | 13.34 | 14.31 | 0.97 | 1.576 | 2.768 | 8.996 | 2.8516 | 29.19 | 3.9 | 10.7 | 2019-03-28
2019-03-29 | Click Here | 0:00 | 6.03 | 5.29 | 5.72 | 5.18 | 5.2 | 6.02 | 7.29 | 1.75 | 2 | 1.92 | 1.86 | 58 | 53 | 17 | 1 | 0 | 0 | 0.191 | 0.342 | 0.891 | 0.102 | 0.217 | 0.643 | 15 | 31.8 | 29.8 | 29.4 | 37.2 | 30 | 63.6 | 59.6 | 58.8 | 0 | 3.02 | 1.91 | 4.1 | 6.5 | 0.136 | 7.4 | 3.9 | 0.90483 | 46.5 | 84.4 | 0.3325 | 0.0714 | 14.249 | 13.447 | 14.108 | 0.661 | 1.584 | 2.697 | 9.166 | 2.7948 | 30.03 | 3.8 | 10.7 | 2019-03-29
2019-03-30 | Click Here | 0:00 | 5.69 | 5.12 | 5.33 | 5.17 | 5.16 | 6.36 | 7.45 | 1.59 | 1.94 | 1.9 | 1.88 | 59 | 53 | 18 | 2 | 0 | 0 | 0.237 | 0.381 | 0.885 | 0.093 | 0.248 | 0.679 | 14.8 | 29.3 | 28.3 | 28.2 | 37.3 | 29.6 | 58.6 | 56.6 | 56.4 | 74.6 | 2.78 | 2.63 | 4.3 | 6.2 | 0.145 | 7.3 | 3.6 | 0.95202 | 44.7 | 87.1 | 0.3497 | 0.0599 | 14.32 | 13.13 | 14.09 | 0.96 | 0 | 0 | 0 | 2.882 | 37.95 | 4.1 | 10.7 | 2019-03-30
2019-03-31 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.92483 | 0 | 0 | 0 | 0 | 14.286 | 13.166 | 14.1 | 0.934 | 1.624 | 2.664 | 8.878 | 2.8748 | 0 | 4.1 | 10.7 | 2019-03-31
2019-04-01 | Click Here | 0:00 | 5.81 | 5.08 | 5.03 | 5.21 | 5.24 | 6.92 | 6.79 | 1.69 | 1.98 | 2.01 | 1.97 | 54 | 48 | 16 | 1 | 0 | 0 | 0.227 | 0.394 | 0.824 | 0.082 | 0.211 | 0.692 | 15 | 30.4 | 28.6 | 28.3 | 37.9 | 30 | 60.8 | 57.2 | 56.6 | 75.8 | 2.91 | 2.59 | 4.1 | 6.1 | 0.126 | 7.4 | 3.7 | 0.91338 | 45.1 | 88.8 | 0.3425 | 0 | 14.94 | 13.78 | 14.76 | 0.98 | 1.646 | 2.671 | 9.463 | 2.8334 | 34.29 | 4.1 | 10.7 | 2019-04-01
2019-04-02 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-04-02
2019-04-03 | Click Here | 0:00 | 5.67 | 5.13 | 5.08 | 5.05 | 5.06 | 6.08 | 6.9 | 1.79 | 1.97 | 1.95 | 1.96 | 55 | 48 | 19 | 2 | 0 | 0 | 0.261 | 0.426 | 0.898 | 0.107 | 0.281 | 0.543 | 14.7 | 34.7 | 28.4 | 28.5 | 38.1 | 29.4 | 69.4 | 56.8 | 57 | 76.2 | 3 | 2.41 | 4.3 | 5.9 | 0.119 | 8.3 | 3.6 | 0.82006 | 49 | 90 | 0.3092 | 0.0455 | 14.18 | 13.01 | 13.98 | 0.97 | 1.621 | 2.615 | 8.774 | 2.7701 | 27.61 | 4.1 | 10.9 | 2019-04-03
2019-04-04 | Click Here | 0:00 | 5.88 | 5.23 | 5.33 | 5.21 | 5.26 | 6.16 | 6.77 | 1.62 | 1.95 | 1.9 | 1.89 | 57 | 49 | 21 | 2 | 0 | 0 | 0.241 | 0.396 | 0.896 | 0.094 | 0.263 | 0.541 | 13.9 | 31.5 | 26.6 | 26.8 | 36.5 | 27.8 | 63 | 53.2 | 53.6 | 73 | 3.09 | 2.51 | 4.2 | 6 | 0.098 | 6.9 | 3.6 | 1.0006 | 43.6 | 86.9 | 0.3596 | 0.0609 | 14.25 | 13.16 | 14.15 | 0.99 | 1.633 | 2.656 | 8.871 | 2.8906 | 30.07 | 4.1 | 11.3 | 2019-04-04
2019-04-05 | Click Here | 0:00 | 5.62 | 5.22 | 5.23 | 5.27 | 5.32 | 0 | 6.98 | 1.6 | 1.87 | 1.86 | 1.92 | 64 | 56 | 20 | 1 | 0 | 0 | 0.249 | 0.408 | 1.08 | 0.103 | 0.304 | 0.526 | 14 | 31.6 | 26.8 | 27.1 | 38.7 | 28 | 63.2 | 53.6 | 54.2 | 77.4 | 3.41 | 2.69 | 4 | 6.3 | 0.138 | 7.4 | 3.7 | 0.62071 | 46.6 | 86 | 0.3309 | 0.0653 | 13.94 | 12.8 | 13.98 | 0.98 | 1.635 | 2.68 | 8.485 | 2.5807 | 30.51 | 4.5 | 11.7 | 2019-04-05
2019-04-06 | Click Here | 0:00 | 5.78 | 5.28 | 5.18 | 5.29 | 5.34 | 6.99 | 6.81 | 1.46 | 1.84 | 1.9 | 1.95 | 66 | 58 | 33 | 4 | 0 | 0 | 0.254 | 0.412 | 1.31 | 0.081 | 0.345 | 0.579 | 13.7 | 32.6 | 26.8 | 26.9 | 36.9 | 27.4 | 65.2 | 53.6 | 53.8 | 73.8 | 3.35 | 2.56 | 3.8 | 5.9 | 0.234 | 7.9 | 3.8 |  | 45.9 | 87.2 | 0.338 | 0.0593 | 14.44 | 13.4 | 14.37 | 0.97 | 0 | 0 | 0 |  | 30.04 | 4.5 | 11.7 | 2019-04-06
2019-04-07 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-04-07
2019-04-08 | Click Here | 0:00 | 5.88 | 5.15 | 5.25 | 5.19 | 5.2 | 6.23 | 7.02 | 1.57 | 1.9 | 1.92 | 1.94 | 64 | 57 | 19 | 2 | 0 | 0 | 0.251 | 0.416 | 0.936 | 0.113 | 0.363 | 0.871 | 17.2 | 33.7 | 27.1 | 27.5 | 37.6 | 34.4 | 67.4 | 54.2 | 55 | 75.2 | 3.22 | 2.64 | 4 | 5.7 | 0.136 | 8.2 | 3.6 | 1.1559 | 49.6 | 88 | 0.3044 | 0.0551 | 15.001 | 12.948 | 14.899 | 1.951 | 1.751 | 2.69 | 8.507 | 3.1259 | 30.13 | 4.5 | 11.7 | 2019-04-08
2019-04-09 | Click Here | 0:00 | 5.81 | 5.15 | 5.27 | 5.21 | 5.23 | 6.32 | 7.05 | 1.58 | 1.88 | 1.96 | 1.99 | 64 | 56 | 39 | 5 | 2 | 0 | 0.246 | 0.413 | 1.72 | 0.121 | 0.391 | 0.627 | 13 | 33.1 | 26.5 | 27.1 | 37.6 | 26 | 66.2 | 53 | 54.2 | 75.2 | 3.19 | 2.61 | 4.1 | 6.2 | 0.168 | 8 | 3.6 | 0.76374 | 45.7 | 87.4 | 0.3379 | 0.0592 | 14.08 | 13.28 | 13.28 | 0 | 1.735 | 2.69 | 8.855 | 2.7137 | 31.85 | 4.7 | 12 | 2019-04-09
2019-04-10 | Click Here | 0:00 | 5.59 | 5.2 | 5.37 | 5.31 | 5.31 | 7.53 | 6.91 | 1.78 | 1.98 | 1.88 | 1.99 | 58 | 51 | 28 | 0 | 0 | 0 | 0.238 | 0.396 | 1.23 | 0.181 | 0.339 | 0.585 | 13.2 | 32.2 | 26.8 | 27.4 | 38.1 | 26.4 | 64.4 | 53.6 | 54.8 | 76.2 | 2.74 | 2.34 | 3.3 | 7 | 0.184 | 8.2 | 3.6 | 0.74739 | 47.1 | 82.6 | 0.3265 | 0.0826 | 14.36 | 12.66 | 13.64 | 0.98 | 1.627 | 2.677 | 8.356 | 2.7674 | 31.45 | 5 | 12.4 | 2019-04-10
2019-04-11 | Click Here | 0:00 | 5.84 | 5.25 | 5.24 | 5.27 | 5.28 | 7.57 | 7.73 | 1.74 | 2.05 | 2.11 | 2.2 | 56 | 48 | 25 | 0 | 0 | 0 | 0.186 | 0.322 | 0.597 | 0.143 | 0.29 | 0.512 | 13.3 | 31.9 | 26.5 | 27.6 | 37.8 | 26.6 | 63.8 | 53 | 55.2 | 75.6 | 2.96 | 2.45 | 3.2 | 6.8 | 0.163 | 8.3 | 3.6 | 0.70489 | 47.3 | 83.4 | 0.3248 | 0.0796 | 15.17 | 14.13 | 15.11 | 0.98 | 1.64 | 2.654 | 9.836 | 2.9049 | 29.57 | 5.5 | 12.4 | 2019-04-11
2019-04-12 | Click Here | 0:00 | 6.05 | 5.37 | 5.27 | 5.34 | 5.35 | 6.67 | 6.97 | 1.81 | 2.14 | 2.18 | 2.2 | 56 | 47 | 17 | 0 | 0 | 0 | 0.189 | 0.347 | 0.68 | 0.063 | 0.24 | 0.441 | 12.3 | 30.1 | 26.4 | 26.8 | 38.1 | 24.6 | 60.2 | 52.8 | 53.6 | 76.2 | 2.94 | 2.56 | 3.4 | 6.6 | 0.113 | 7.2 | 3.6 | 0.63045 | 47.5 | 90.2 | 0.3246 | 0.0445 | 13.33 | 12.33 | 13.29 | 0.96 | 1.636 | 2.655 | 8.039 | 2.7605 | 0 | 5.6 | 12.6 | 2019-04-12
2019-04-13 | Click Here | 0:00 | 5.95 | 5.41 | 5.34 | 5.31 | 5.29 | 6.56 | 7.16 | 1.76 | 2 | 2.02 | 2.04 | 56 | 48 | 19 | 0 | 0 | 0 | 0.196 | 0.357 | 0.986 | 0.073 | 0.224 | 0.428 | 12.1 | 30.4 | 25.9 | 26.2 | 38.1 | 24.2 | 60.8 | 51.8 | 52.4 | 76.2 | 2.87 | 2.61 | 3.1 | 6.1 | 0.124 | 7.1 | 3.6 | 0.83164 | 46.6 | 88.9 | 0.3315 | 0.0508 | 13.86 | 12.81 | 13.79 | 0.98 | 0 | 0 | 0 | 2.8916 | 29.22 | 5.6 | 12.8 | 2019-04-13
2019-04-14 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-04-14
2019-04-15 | Click Here | 0:00 | 5.72 | 5.4 | 5.38 | 5.35 | 5.36 | 7.74 | 7.24 | 1.78 | 1.95 | 1.97 | 2.05 | 58 | 50 | 22 | 1 | 0 | 0 | 0.215 | 0.346 | 0.725 | 0.12 | 0.238 | 0.47 | 13.2 | 31.1 | 26 | 26.7 | 38.9 | 26.4 | 62.2 | 52 | 53.4 | 77.8 | 3.02 | 1.95 | 3.7 | 8.5 | 0.105 | 8.5 | 3.8 | 0.30883 | 48.6 | 88 | 0.3133 | 0.0524 | 14.42 | 13.41 | 14.39 | 0.98 | 1.643 | 2.594 | 9.173 | 2.3888 | 28.87 | 5.6 | 13 | 2019-04-15
2019-04-16 | Click Here | 0:00 | 5.46 | 5.37 | 5.25 | 5.26 | 5.29 | 7.67 | 6.67 | 1.6 | 1.86 | 1.68 | 1.96 | 57 | 49 | 19 | 0 | 0 | 0 | 0.218 | 0.363 | 0.828 | 0.119 | 0.124 | 0.383 | 12.8 | 31.4 | 26 | 26.5 | 38.7 | 25.6 | 62.8 | 52 | 53 | 77.4 | 3.17 | 2.04 | 3.6 | 8.3 | 0.096 | 7.7 | 3.7 | 0.83097 | 48.8 | 88.4 | 0.3089 | 0.0515 | 13.61 | 12.56 | 13.55 | 0.99 | 1.664 | 2.566 | 8.33 | 2.471 | 28.64 | 5.6 | 13 | 2019-04-16
2019-04-17 | Click Here | 0:00 | 5.65 | 4.91 | 5.18 | 5.21 | 5.26 | 7.82 | 6.56 | 1.56 | 1.92 | 1.9 | 1.71 | 62 | 54 | 25 | 2 | 0 | 0 | 0.206 | 0.336 | 0.682 | 0.067 | 0.244 | 0.351 | 12.5 | 31.6 | 25.8 | 25.5 | 36.6 | 25 | 63.2 | 51.6 | 51 | 73.2 | 3.11 | 2.07 | 3.6 | 8.4 | 0.109 | 8.8 | 3.7 | 0.85424 | 48.7 | 89.3 | 0.3119 | 0.049 | 13.21 | 13.12 | 13.12 | 0 | 1.772 | 2.567 | 8.781 | 2.5942 | 28.87 | 5.6 | 13 | 2019-04-17
2019-04-18 | Click Here | 0:00 | 5.63 | 5.38 | 5 | 5.29 | 5.32 | 7.43 | 7.92 | 1.73 | 1.87 | 1.86 | 1.73 | 62 | 54 | 26 | 3 | 0 | 0 | 0.203 | 0.331 | 0.837 | 0.092 | 0.323 | 0.531 | 12.6 | 32 | 25.9 | 26.7 | 37.9 | 25.2 | 64 | 51.8 | 53.4 | 75.8 | 2.94 | 2.27 | 3.5 | 8.2 | 0.144 | 9.1 | 3.7 | 0.84012 | 47.2 | 88 | 0.3261 | 0.0551 | 13.87 | 12.88 | 13.82 | 0.94 | 1.72 | 2.599 | 8.561 | 2.7201 | 29.34 | 5.8 | 13 | 2019-04-18
2019-04-19 | Click Here | 0:00 | 5.83 | 5.02 | 5.34 | 5.07 | 5.1 | 6.17 | 6.93 | 1.78 | 1.97 | 1.93 | 1.91 | 61 | 56 | 19 | 1 | 0 | 0 | 0.201 | 0.326 | 0.895 | 0.078 | 0.237 | 0.374 | 12.5 | 32.9 | 26.1 | 26.5 | 34.6 | 25 | 65.8 | 52.2 | 53 | 69.2 | 2.98 | 2.31 | 3.6 | 7.9 | 0.113 | 9.1 | 3.8 | 1.0343 | 47.4 | 88.1 | 0.3259 | 0.0546 | 13.85 | 12.92 | 13.86 | 0.94 | 1.653 | 2.583 | 8.684 | 2.9443 | 31.07 | 5.8 | 13 | 2019-04-19
2019-04-20 | Click Here | 0:00 | 6.01 | 5.14 | 5.07 | 5.21 | 5.22 | 6.4 | 7.12 | 1.74 | 1.95 | 1.94 | 1.92 | 63 | 57 | 16 | 1 | 0 | 0 | 0.206 | 0.313 | 0.688 | 0.063 | 0.239 | 0.463 | 12.1 | 34.5 | 26.9 | 27 | 36.9 | 24.4 | 69 | 53.8 | 54 | 73.8 | 2.87 | 2.43 | 3.4 | 7.1 | 0.119 | 9.2 | 3.8 | 0.98359 | 46.2 | 89.7 | 0.3352 | 0.0469 | 13.76 | 12.67 | 13.68 | 1.01 | 0 | 0 | 0 | 2.9236 | 33.6 | 5.9 | 13.3 | 2019-04-20
2019-04-21 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-04-21
2019-04-22 | Click Here | 0:00 | 5.68 | 5.07 | 5.21 | 4.9 | 4.97 | 4.98 | 5.23 | 1.83 | 2.09 | 2.06 | 2.07 | 56 | 48 | 18 | 0 | 0 | 0 | 0.212 | 0.289 | 0.586 | 0.074 | 0.096 | 0.133 | 12.5 | 34 | 28.2 | 28 | 29.6 | 25 | 68 | 56.4 | 56 | 59.2 | 3.2 | 2.51 | 3.8 | 3 | 0.25 | 9.8 | 3.8 | 0.81842 | 50.1 | 89.3 | 0.3 | 0.049 | 13.8 | 12.78 | 13.77 | 0.99 | 1.695 | 2.621 | 8.464 | 2.8984 | 32.39 | 5.9 | 0 | 2019-04-22
2019-04-23 | Click Here | 0:00 | 5.78 | 5.34 | 5.12 | 5.32 | 5.31 | 7.31 | 7.52 | 1.82 | 2.1 | 1.81 | 2.06 | 55 | 48 | 16 | 0 | 0 | 0 | 0.199 | 0.334 | 0.625 | 0.075 | 0.247 | 0.399 | 11.7 | 30.6 | 27.4 | 28 | 38.2 | 23.4 | 61.2 | 54.8 | 56 | 76.4 | 3 | 2.32 | 3.6 | 6.8 | 0.151 | 8.6 | 3.7 | 0.74386 | 50.3 | 90 | 0.2994 | 0.0482 | 14.71 | 13.8 | 14.77 | 0.97 | 1.697 | 2.55 | 9.553 | 2.6839 | 31.92 | 5.9 | 11.5 | 2019-04-23
2019-04-24 | Click Here | 0:00 | 5.8 | 5.29 | 5.36 | 5.12 | 5.18 | 4.96 | 5.84 | 1.71 | 1.89 | 1.83 | 1.86 | 56 | 47 | 17 | 1 | 0 | 0 | 0.201 | 0.356 | 0.652 | 0.079 | 0.116 | 0.104 | 11.1 | 30.7 | 27 | 26.8 | 28.6 | 22.2 | 61.4 | 54 | 53.6 | 57.2 | 2.99 | 2.36 | 3.8 | 5.8 | 0.131 | 8.2 | 4 | 0.94323 | 50.5 | 90.2 | 0.2992 | 0.048 | 13.54 | 12.67 | 13.61 | 0.94 | 1.697 | 2.55 | 8.423 | 2.9232 | 28.18 | 5.9 | 11.5 | 2019-04-24
2019-04-25 | Click Here | 0:00 | 5.91 | 5.07 | 5.36 | 5.14 | 5.13 | 6.51 | 7.64 | 1.79 | 2.06 | 2.11 | 2.28 | 55 | 46 | 15 | 0 | 0 | 0 | 0.211 | 0.297 | 0.659 | 0.066 | 0.141 | 0.274 | 11.4 | 32.2 | 26.5 | 26.9 | 37.4 | 22.8 | 64.4 | 53 | 53.8 | 74.8 | 2.91 | 2.47 | 3.6 | 6.1 | 0.029 | 9.2 | 4.1 | 0.61816 | 47 | 89.9 | 0.3271 | 0.0459 | 13.79 | 12.87 | 13.81 | 0.94 | 1.606 | 2.587 | 8.677 | 2.8782 | 29.18 | 5.9 | 11.5 | 2019-04-25
2019-04-26 | Click Here | 0:00 | 5.83 | 5.35 | 5.27 | 5.38 | 5.4 | 7.67 | 7.14 | 1.56 | 1.77 | 2.02 | 2.18 | 59 | 50 | 20 | 2 | 0 | 0 | 0.194 | 0.294 | 0.739 | 0.059 | 0.218 | 0.247 | 11.4 | 31.1 | 26.6 | 26.9 | 38.1 | 22.8 | 62.2 | 53.2 | 53.8 | 76.2 | 2.93 | 2.1 | 3.4 | 6.3 | 0.029 | 8.8 | 4.1 | 0.63926 | 49.2 | 88.9 | 0.308 | 0.0511 | 13.71 | 12.79 | 13.77 | 0.98 | 1.576 | 2.652 | 8.562 | 2.7393 | 30.51 | 5.9 | 11.8 | 2019-04-26
2019-04-27 | Click Here | 0:00 | 5.73 | 5.13 | 5.23 | 5.16 | 5.21 | 6.76 | 7.14 | 1.63 | 1.92 | 2.04 | 2.06 | 59 | 52 | 18 | 1 | 0 | 0 | 0.191 | 0.287 | 0.777 | 0.057 | 0.226 | 0.301 | 11.3 | 31.7 | 26.7 | 26.3 | 33.4 | 22.6 | 63.4 | 53.4 | 52.6 | 66.8 | 2.92 | 2.26 | 3.2 | 6.5 | 0.031 | 8.2 | 4.2 | 0.5617 | 49.4 | 90 | 0.3078 | 0.0458 | 13.52 | 13.52 | 13.52 | 0 | 1.558 | 2.656 | 9.306 | 2.5917 | 29.17 | 5.9 | 11.8 | 2019-04-27
2019-04-28 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-04-28
2019-04-29 | Click Here | 0:00 | 5.89 | 4.88 | 5.2 | 5 | 5.05 | 5.72 | 6.22 | 1.49 | 1.91 | 1.89 | 1.94 | 61 | 54 | 24 | 3 | 1 | 0 | 0.187 | 0.241 | 1.26 | 0.083 | 0.317 | 0.586 | 10.6 | 33.2 | 24.7 | 24.2 | 28.9 | 21.2 | 66.4 | 49.4 | 48.4 | 57.8 | 2.95 | 2.43 | 3.1 | 5.6 | 0.029 | 8.3 | 4.2 | 0.87247 | 48 | 86.1 | 0.3187 | 0.0648 | 13.86 | 13.03 | 13.96 | 0.93 | 1.673 | 2.642 | 8.715 | 2.8425 | 36.42 | 6 | 12.2 | 2019-04-29
2019-04-30 | Click Here | 0:00 | 6.08 | 5.18 | 5.19 | 5.09 | 5.12 | 6.67 | 7.14 | 1.76 | 1.97 | 1.99 | 2.03 | 60 | 53 | 19 | 1 | 0 | 0 | 0.193 | 0.254 | 0.637 | 0.068 | 0.246 | 0.314 | 9.8 | 29.5 | 26 | 26.3 | 36.1 | 19.8 | 59 | 52 | 52.6 | 72.2 | 2.97 | 2.37 | 3.3 | 6.2 | 0.041 | 8.8 | 4.1 | 0.9062 | 47.6 | 87.9 | 0.3219 | 0.0559 | 13.85 | 13 | 13.96 | 0.96 | 1.663 | 2.644 | 8.693 | 2.9262 | 26.44 | 6 | 13 | 2019-04-30
2019-05-01 | Click Here | 0:00 | 5.69 | 5.21 | 5.21 | 5.36 | 5.38 | 8.27 | 7.95 | 1.74 | 1.94 | 2.01 | 2.01 | 58 | 50 | 17 | 0 | 0 | 0 | 0.197 | 0.301 | 0.751 | 0.067 | 0.136 | 0.182 | 10.6 | 29.7 | 24.3 | 24.3 | 37.3 | 21.2 | 59.4 | 48.6 | 48.6 | 74.6 | 3.13 | 2.29 | 3.5 | 6.3 | 0.038 | 9 | 4 | 0.48835 | 50.7 | 91.1 | 0.2945 | 0.0404 | 13.6 | 12.67 | 13.65 | 0.98 | 1.665 | 2.645 | 8.36 | 2.5284 | 29.11 | 6 | 13.4 | 2019-05-01
2019-05-02 | Click Here | 0:00 | 5.69 | 5.32 | 5.3 | 5.25 | 5.28 | 7.56 | 7.03 | 1.49 | 1.88 | 1.87 | 1.92 | 57 | 49 | 18 | 0 | 0 | 0 | 0.202 | 0.316 | 0.731 | 0.063 | 0.198 | 0.341 | 10.7 | 28.9 | 25.1 | 26.3 | 37.4 | 21.4 | 57.8 | 50.2 | 52.6 | 74.8 | 3.13 | 2.4 | 3.3 | 6.2 | 0.035 | 9 | 4 | 0.89308 | 50.9 | 91.3 | 0.2938 | 0.04 | 13.42 | 12.5 | 13.47 | 0.97 | 1.665 | 2.645 | 8.19 | 2.8831 | 28.17 | 6 | 11.5 | 2019-05-02
2019-05-03 | Click Here | 0:00 | 5.89 | 5.27 | 5.33 | 5.41 | 5.42 | 7.09 | 7.04 | 1.62 | 1.94 | 1.94 | 2.01 | 54 | 47 | 15 | 0 | 0 | 0 | 0.241 | 0.006 | 0.628 | 0.049 | 0.17 | 0.346 | 11.4 | 30.2 | 24.9 | 26.2 | 36.8 | 22.8 | 60.4 | 49.8 | 52.4 | 73.6 | 3.2 | 2.44 | 3.6 | 5.9 | 0.038 | 8.9 | 4.1 | 0.85612 | 51 | 91.8 | 0.2918 | 0.0386 | 13.022 | 12.033 | 13.004 | 0.971 | 1.672 | 2.629 | 7.721 | 2.8961 | 27.08 | 6 | 11.5 | 2019-05-03
2019-05-04 | Click Here | 0:00 | 5.92 | 5.33 | 5.31 | 5.34 | 5.59 | 7.24 | 7.08 | 1.72 | 2.01 | 2.04 | 2.09 | 52 | 41 | 15 | 0 | 0 | 0 | 0.214 | 0.003 | 0.644 | 0.054 | 0.199 | 0.401 | 11.1 | 29.1 | 25.5 | 26.7 | 37.7 | 22.2 | 58.2 | 51 | 53.4 | 75.4 | 3.26 | 2.49 | 3.6 | 6.7 | 0.042 | 8.9 | 4.1 | 0.89199 | 50.2 | 92 | 0.2984 | 0.0374 | 12.69 | 11.79 | 12.75 | 0.96 | 0 | 0 | 0 | 2.972 | 29.98 | 6 | 11.5 | 2019-05-04
2019-05-05 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-05-05
2019-05-06 | Click Here | 0:00 | 5.79 | 5.13 | 5.24 | 5.33 | 5.31 | 7.65 | 6.95 | 1.82 | 1.97 | 2.01 | 2.08 | 50 | 40 | 13 | 0 | 0 | 0 | 0.223 | 0.017 | 0.65 | 0.065 | 0.279 | 0.503 | 11 | 31.6 | 26.5 | 26.1 | 34.5 | 22 | 63.2 | 53 | 52.2 | 69 | 3.15 | 2.08 | 3.4 | 6.3 | 0.044 | 10.4 | 4.7 | 0.55023 | 52.3 | 82.9 | 0.2808 | 0.0813 | 14.01 | 13.17 | 14.12 | 0.95 | 1.649 | 2.531 | 8.99 | 2.6602 | 30.98 | 6 | 11.5 | 2019-05-06
2019-05-07 | Click Here | 0:00 | 5.91 | 5.26 | 5.13 | 5.3 | 5.33 | 7.6 | 6.96 | 1.53 | 1.9 | 2 | 2.06 | 55 | 47 | 26 | 3 | 0 | 0 | 0.193 | 0.12 | 0.671 | 0.094 | 0.24 | 0.266 | 10.7 | 32 | 26.6 | 26.3 | 34.4 | 21.4 | 64 | 53.2 | 52.6 | 68.8 | 2.96 | 2.89 | 2.3 | 5.2 | 0.011 | 10.5 | 4.8 | 0.88005 | 53.9 | 88.9 | 0.2677 | 0.0511 | 13.51 | 12.68 | 13.66 | 0.98 | 1.651 | 2.454 | 8.575 | 3.0001 | 30.98 | 6 | 11.5 | 2019-05-07
2019-05-08 | Click Here | 0:00 | 6 | 5.19 | 5.24 | 5.44 | 5.47 | 7.81 | 7.97 | 1.67 | 1.98 | 2.04 | 2.03 | 51 | 46 | 19 | 1 | 0 | 0 | 0.198 | 0.124 | 0.477 | 0.059 | 0.129 | 0.176 | 10.9 | 32.4 | 25.9 | 25.4 | 35.3 | 21.8 | 64.8 | 51.8 | 50.8 | 70.6 | 3.05 | 2.97 | 3.1 | 5.9 | 0.027 | 10.6 | 5.9 | 0.81011 | 54.4 | 91.7 | 0.2646 | 0.0389 | 14.2 | 13.436 | 14.412 | 0.976 | 1.633 | 2.39 | 9.413 | 2.8701 | 30.72 | 6 | 11.5 | 2019-05-08
2019-05-09 | Click Here | 0:00 | 6 | 5.31 | 5.25 | 5.4 | 5.42 | 7.86 | 7.93 | 1.77 | 2.03 | 2.09 | 2.04 | 52 | 44 | 19 | 0 | 0 | 0 | 0.243 | 0.021 | 0.491 | 0.062 | 0.094 | 0.118 | 9.7 | 28.6 | 23.2 | 23 | 33.1 | 0 | 57.2 | 46.4 | 46 | 66.2 | 3.24 | 2.88 | 3 | 6 | 0.021 | 10.6 | 5.8 | 0.81668 | 52.8 | 90.1 | 0.277 | 0.0474 | 16.2 | 15.47 | 16.47 | 1 | 1.645 | 2.415 | 11.41 | 2.9767 | 29.03 | 6 | 10.8 | 2019-05-09
2019-05-10 | Click Here | 0:00 | 5.74 | 5.33 | 5.28 | 5.32 | 5.33 | 6.5 | 7.69 | 1.74 | 2 | 2 | 1.98 | 54 | 47 | 21 | 1 | 0 | 0 | 0.256 | 0.019 | 0.601 | 0.093 | 0.113 | 0.214 | 10.6 | 28.7 | 23 | 23.2 | 32.9 | 21.2 | 57.4 | 46 | 46.4 | 65.8 | 3.09 | 2.56 | 3.3 | 6.3 | 0.032 | 9.3 | 5 |  | 0 | 0 | 0 | 0 | 14.274 | 13.449 | 14.417 | 0.968 | 1.561 | 2.478 | 9.41 |  | 25.74 | 6 | 10.6 | 2019-05-10
2019-05-11 | Click Here | 0:00 | 5.92 | 5.04 | 5.26 | 5.21 | 5.28 | 6.52 | 7.41 | 1.79 | 2.08 | 2.14 | 2.12 | 53 | 47 | 15 | 0 | 0 | 0 | 0.241 | 0.006 | 0.601 | 0.053 | 0.131 | 0.287 | 10.4 | 31.5 | 24.6 | 24.4 | 33.1 | 20.8 | 63 | 49.2 | 48.8 | 66.2 | 2.92 | 2.61 | 3.2 | 6.4 | 0.037 | 10.7 | 5.1 | 0.68033 | 54.7 | 88.9 | 0.2617 | 0.0507 | 13 | 12.16 | 13.13 | 0.97 | 0 | 0 | 0 | 2.8203 | 30.36 | 6 | 10.6 | 2019-05-11
2019-05-12 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.7218 | 0 | 0 | 0 | 0 | 12.038 | 11.116 | 12.097 | 0.981 | 1.401 | 2.428 | 7.287 | 2.8618 | 0 | 6 | 10.8 | 2019-05-12
2019-05-13 | Click Here | 0:00 | 6.04 | 5.19 | 5.25 | 5.26 | 5.3 | 7.04 | 6.9 | 1.84 | 2.11 | 2.19 | 2.22 | 50 | 41 | 13 | 0 | 0 | 0 | 0.217 | 0.04 | 0.547 | 0.046 | 0.174 | 0.224 | 10.7 | 30.9 | 24.1 | 23.8 | 32.7 | 21.4 | 61.8 | 48.2 | 47.6 | 65.4 | 3.09 | 2.49 | 2.9 | 5.7 | 0.042 | 10.8 | 5.2 | 0.88627 | 55 | 90.9 | 0.258 | 0.0434 | 13.685 | 11.808 | 13.741 | 1.933 | 1.569 | 2.417 | 7.822 | 3.0663 | 30.39 | 6 | 10.8 | 2019-05-13
2019-05-14 | Click Here | 0:00 | 5.88 | 5.29 | 5.24 | 5.31 | 5.37 | 7.1 | 7.02 | 1.78 | 2.06 | 2.09 | 2.16 | 53 | 47 | 15 | 0 | 0 | 0 | 0.247 | 0.04 | 0.521 | 0.037 | 0.134 | 0.236 | 10.9 | 31.4 | 23.8 | 23.4 | 33.8 | 21.8 | 62.8 | 47.6 | 46.8 | 67.6 | 3.15 | 2.36 | 3.3 | 6.1 | 0.036 | 11 | 5.4 | 0.46805 | 54.7 | 91.7 | 0.2597 | 0.0387 | 14.3 | 14.42 | 14.42 | 0 | 1.566 | 2.504 | 10.38 | 2.638 | 30.29 | 6 | 10.8 | 2019-05-14
2019-05-15 | Click Here | 0:00 | 5.61 | 4.85 | 5.2 | 4.95 | 5.04 | 7.01 | 6.58 | 1.59 | 1.83 | 1.97 | 2.19 | 51 | 43 | 16 | 0 | 0 | 0 | 0.231 | 0.008 | 0.589 | 0.058 | 0.152 | 0.305 | 10.8 | 30.9 | 25 | 24.5 | 33.7 | 21.6 | 61.8 | 50 | 49 | 67.4 | 3.19 | 2.72 | 3.1 | 6.2 | 0.052 | 10.9 | 0 | 0.55522 | 55.2 | 90.3 | 0.2576 | 0.0494 | 13.103 | 12.213 | 13.192 | 0.979 | 1.557 | 2.494 | 8.162 | 2.8352 | 28.87 | 6 | 10.8 | 2019-05-15
2019-05-16 | Click Here | 0:00 | 5.74 | 5.04 | 4.97 | 5.14 | 5.19 | 7.19 | 7.21 | 1.86 | 2.2 | 2.2 | 2.52 | 57 | 50 | 19 | 0 | 0 | 0 | 0.311 | 0.021 | 0.568 | 0.061 | 0.128 | 0.289 | 11.1 | 31.4 | 24.9 | 24.3 | 34.3 | 22.2 | 62.8 | 49.8 | 48.6 | 68.8 | 3.34 | 2.59 | 3 | 6.2 | 0.046 | 10.8 | 5.3 | 0.52039 | 54.9 | 90.7 | 0.2597 | 0.0477 | 13.68 | 12.86 | 13.8 | 0.94 | 1.403 | 2.504 | 8.953 | 2.8804 | 30.06 | 6.6 | 11.2 | 2019-05-16
2019-05-17 | Click Here | 0:00 | 5.85 | 5.06 | 5.3 | 5.14 | 5.16 | 7.45 | 7.12 | 1.69 | 1.98 | 1.97 | 2.34 | 47 | 40 | 24 | 4 | 0 | 0 | 0.193 | 0.01 | 0.293 | 0.064 | 0.234 | 0.304 | 11.6 | 36.8 | 30.6 | 30.4 | 36.3 | 23.2 | 73.6 | 61.2 | 60.8 | 72.6 | 3.31 | 2.44 | 2.8 | 4.9 | 0.015 | 12.6 | 6.2 | 0.44626 | 58.4 | 85.9 | 0.2334 | 0.0659 | 12.95 | 12.96 | 12.96 | 0 | 1.467 | 2.467 | 9.026 | 2.6263 | 35.21 | 6.6 | 11.2 | 2019-05-17
2019-05-18 | Click Here | 0:00 | 5.78 | 5.12 | 5.09 | 5.16 | 5.22 | 7.58 | 7.66 | 1.59 | 1.94 | 1.98 | 2.02 | 45 | 38 | 18 | 2 | 0 | 0 | 0.196 | 1.322 | 0.287 | 0.061 | 0.186 | 0.232 | 11.5 | 36.4 | 31.2 | 28.9 | 35.5 | 23 | 72.8 | 62.4 | 57.8 | 71 | 3.17 | 2.41 | 2.9 | 5.2 | 0.021 | 12.7 | 6.3 |  | 58.5 | 86.2 | 0.2331 | 0.0638 | 12.95 | 12.96 | 12.96 | 0 | 0 | 0 | 0 |  | 34.27 | 6.6 | 11.2 | 2019-05-18
2019-05-19 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-05-19
2019-05-20 | Click Here | 0:00 | 6.22 | 5.36 | 5.07 | 5.12 | 5.1 | 6.5 | 7.96 | 1.71 | 2.07 | 2.14 | 2.2 | 44 | 39 | 17 | 1 | 0 | 0 | 0.214 | 1.906 | 0.299 | 0.058 | 0.164 | 0.216 | 11.6 | 31.7 | 29.7 | 30.2 | 37.2 | 23.2 | 63.4 | 59.4 | 60.4 | 74.4 | 3.16 | 2.57 | 3 | 5.6 | 0.028 | 12.2 | 7 | 0.69957 | 58.7 | 92.5 | 0.2329 | 0.0339 | 13.634 | 12.74 | 13.716 | 0.976 | 1.36 | 2.386 | 8.994 | 2.7896 | 26.57 | 6.6 | 11.2 | 2019-05-20
2019-05-21 | Click Here | 0:00 | 6.14 | 5.32 | 5.28 | 5.21 | 5.2 | 6.16 | 7.31 | 1.62 | 1.84 | 1.89 | 1.86 | 45 | 38 | 16 | 1 | 0 | 0 | 0.217 | 0.324 | 0.306 | 0.062 | 0.096 | 0.103 | 10.8 | 31.8 | 26.4 | 26.7 | 31.1 | 21.6 | 63.6 | 52.8 | 53.4 | 62.2 | 3.14 | 2.61 | 2.9 | 5.8 | 0.022 | 12.5 | 7.4 | 0.90946 | 58.8 | 86.3 | 0.232 | 0.0637 | 13.98 | 13.06 | 14.05 | 0.99 | 1.726 | 2.377 | 8.957 | 2.7595 | 27.65 | 6.6 | 11.4 | 2019-05-21
2019-05-22 | Click Here | 0:00 | 5.96 | 5.36 | 5.33 | 5.22 | 5.28 | 8.01 | 7.44 | 1.71 | 1.86 | 1.99 | 1.69 | 44 | 37 | 14 | 0 | 0 | 0 | 0.202 | 0.344 | 0.312 | 0.059 | 0.064 | 0.081 | 10.9 | 30.2 | 27.2 | 26.9 | 31.3 | 21.8 | 60.4 | 54.4 | 53.8 | 62.6 | 3.23 | 2.56 | 3.3 | 6.1 | 0.025 | 12.5 | 7.4 | 0.33128 | 58.9 | 87.3 | 0.2317 | 0.0586 | 13.32 | 13.34 | 13.34 | 0 | 1.52 | 2.374 | 9.446 | 2.2513 | 28.17 | 6.6 | 11.4 | 2019-05-22
2019-05-23 | Click Here | 0:00 | 5.81 | 5.41 | 5.31 | 5.23 | 5.31 | 7.7 | 7.15 | 1.68 | 1.84 | 1.83 | 2.12 | 50 | 42 | 19 | 0 | 0 | 0 | 0.296 | 0.485 | 0.365 | 0.083 | 0.139 | 0.104 | 10.9 | 26.9 | 26.1 | 26.6 | 35.1 | 21.8 | 53.8 | 52.2 | 53.2 | 70.2 | 3.21 | 4.79 | 2.7 | 5.9 | 0.089 | 11.3 | 7.2 | 0.10923 | 58.7 | 91.6 | 0.2308 | 0.0377 | 13.72 | 12.89 | 13.85 | 0.96 | 1.52 | 2.349 | 9.021 | 2.0192 | 28.4 | 6.6 | 10.8 | 2019-05-23
2019-05-24 | Click Here | 0:00 | 5.89 | 5.39 | 5.41 | 5.29 | 5.4 | 7.64 | 7.78 | 1.7 | 1.9 | 1.88 | 1.92 | 52 | 43 | 21 | 0 | 0 | 0 | 0.31 | 0.389 | 0.404 | 0.092 | 0.109 | 0.104 | 11.3 | 27.4 | 25.9 | 26.7 | 36.1 | 22.6 | 54.8 | 51.8 | 53.4 | 72.2 | 3.21 | 4.58 | 3 | 6.1 | 0.078 | 11.2 | 7.1 | 0.04473 | 58.8 | 92 | 0.23 | 0.0329 | 13.246 | 12.312 | 13.288 | 0.976 | 1.428 | 2.302 | 8.582 | 1.7847 | 29.54 | 6 | 10.5 | 2019-05-24
2019-05-25 | Click Here | 0:00 | 5.95 | 5.32 | 5.38 | 5.29 | 5.37 | 7.57 | 7.74 | 1.59 | 1.88 | 1.83 | 1.79 | 49 | 40 | 17 | 0 | 0 | 0 | 0.268 | 0.412 | 0.439 | 0.052 | 0.104 | 0.139 | 10.7 | 26.8 | 24.7 | 25.4 | 35.5 | 21.4 | 53.6 | 49.4 | 50.8 | 71 | 3.03 | 4.28 | 3.1 | 6.4 | 0.064 | 11.1 | 7.2 | 0.88439 | 58 | 91.8 | 0.2342 | 0.0342 | 12.92 | 12.97 | 12.97 | 0 | 0 | 0 | 0 | 2.6344 | 28.83 | 6 | 10.5 | 2019-05-25
2019-05-26 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-05-26
2019-05-27 | Click Here | 0:00 | 5.78 | 5.36 | 5.33 | 5.2 | 5.27 | 7.9 | 7.64 | 1.52 | 1.77 | 2.01 | 1.87 | 48 | 40 | 32 | 2 | 0 | 0 | 0.259 | 0.424 | 0.671 | 0.123 | 0.896 | 0.753 | 11.7 | 31 | 28.4 | 28.2 | 33.6 | 23.4 | 62 | 56.8 | 56.4 | 67.2 | 3.06 | 2.36 | 2.9 | 5.9 | 0.026 | 14.6 | 8.2 | 0.51766 | 72.1 | 88.9 | 0.1419 | 0.0507 | 14.54 | 13.72 | 14.68 | 0.96 | 1.546 | 2.448 | 9.726 | 2.4077 | 28.64 | 6 | 10.5 | 2019-05-27
2019-05-28 | Click Here | 0:00 | 5.95 | 5.29 | 5.36 | 5.17 | 5.21 | 7.54 | 7.56 | 1.54 | 1.71 | 1.72 | 1.9 | 46 | 39 | 16 | 1 | 0 | 0 | 0.253 | 0.406 | 0.342 | 0.084 | 0.364 | 0.159 | 11.7 | 31.7 | 28.7 | 28.2 | 34.1 | 23.4 | 63.4 | 57.4 | 56.4 | 68.2 | 3.05 | 2.44 | 2.8 | 5.7 | 0.024 | 15 | 8.7 | 1.0069 | 67.9 | 91.2 | 0.1681 | 0.0398 | 14.39 | 13.57 | 14.54 | 0.97 | 1.735 | 3.205 | 8.63 | 2.8769 | 28.87 | 5.7 | 9.8 | 2019-05-28
2019-05-29 | Click Here | 0:00 | 6.02 | 5.25 | 5.29 | 5.2 | 5.28 | 7.54 | 7.4 | 1.59 | 1.88 | 1.92 | 1.84 | 52 | 46 | 17 | 0 | 0 | 0 | 0.264 | 0.388 | 0.496 | 0.052 | 0.149 | 0.227 | 11.7 | 31.7 | 28.5 | 28.4 | 34.1 | 23.4 | 63.4 | 57 | 56.8 | 68.2 | 3.14 | 2.54 | 3.2 | 5.9 | 0.037 | 14.5 | 9.4 | 0.66378 | 59.5 | 92.6 | 0.2254 | 0.0332 | 14.989 | 14.182 | 15.171 | 0.989 | 1.674 | 2.629 | 9.879 | 2.7438 | 29.52 | 5.7 | 9.8 | 2019-05-29
2019-05-30 | Click Here | 0:00 | 5.92 | 5.29 | 5.28 | 5.22 | 5.24 | 7.39 | 7.28 | 1.65 | 1.98 | 2.2 | 2.43 | 50 | 41 | 14 | 0 | 0 | 0 | 0.296 | 0.395 | 0.421 | 0.077 | 0.146 | 0.222 | 11.4 | 31.9 | 28.2 | 27.9 | 34.7 | 22.8 | 63.8 | 56.4 | 55.8 | 69.4 | 3.39 | 4.11 | 3.4 | 6.4 | 0.03 | 14.2 | 9.4 |  | 59.9 | 92.5 | 0.2217 | 0.0339 | 14.49 | 13.75 | 14.68 | 0.93 | 1.655 | 2.613 | 9.482 |  | 31.35 | 5.7 | 9.8 | 2019-05-30
2019-05-31 | Click Here | 0:00 | 6.21 | 5.23 | 5.25 | 5.11 | 5.02 | 6.28 | 7.1 | 1.47 | 1.71 | 1.75 | 1.63 | 52 | 46 | 16 | 1 | 0 | 0 | 0.283 | 0.398 | 0.614 | 0.082 | 0.128 | 0.236 | 11.8 | 30.9 | 28.2 | 28.8 | 34.4 | 23.6 | 61.8 | 56.4 | 57.6 | 68.8 | 3.22 | 2.57 | 3.2 | 6.7 | 0.026 | 15.6 | 9.8 | 1.0533 | 59.7 | 89 | 0.2215 | 0.0506 | 14.201 | 13.662 | 14.317 | 0.655 | 1.641 | 2.647 | 9.126 | 2.7133 | 25.62 | 5.7 | 9.8 | 2019-05-31
2019-06-01 | Click Here | 0:00 | 6.62 | 5.18 | 5.25 | 5.13 | 5.17 | 6.55 | 7.02 | 1.33 | 1.81 | 1.79 | 1.96 | 52 | 46 | 15 | 1 | 0 | 0 | 0.287 | 0.364 | 0.332 | 0.079 | 0.147 | 0.226 | 12.2 | 32.6 | 29.8 | 29.3 | 35.2 | 24.4 | 65.2 | 59.6 | 58.6 | 70.4 | 3.13 | 2.42 | 3.1 | 5.9 | 0 | 15.7 | 9.9 | 0.98335 | 59.8 | 86 | 0.2218 | 0.0651 | 13.81 | 12.93 | 13.93 | 1 | 1.369 | 2.603 | 8.874 | 2.8034 | 27.75 | 5.9 | 11.1 | 2019-06-01
2019-06-02 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.79895 | 0 | 0 | 0 | 0 | 14.08 | 13.205 | 14.179 | 0.974 | 1.369 | 2.603 | 8.874 | 2.799 | 0 | 5.7 | 10.1 | 2019-06-02
2019-06-03 | Click Here | 0:00 | 6.25 | 5.19 | 5.23 | 5.16 | 5.2 | 7 | 7.13 | 1.52 | 1.84 | 1.9 | 2.03 | 53 | 46 | 14 | 0 | 0 | 0 | 0.274 | 0.392 | 0.361 | 0.087 | 0.127 | 0.214 | 12 | 33.2 | 28.8 | 28.5 | 34.9 | 24 | 66.4 | 57.6 | 57 | 69.8 | 3.22 | 2.49 | 3.2 | 6.4 | 0.039 | 15.8 | 9.9 | 1.853 | 60 | 89.8 | 0.2206 | 0.0468 | 14.394 | 9.964 | 10.964 | 0.98 | 1.501 | 2.582 | 9.204 | 3.883 | 29.19 | 5.7 | 10.1 | 2019-06-03
2019-06-04 | Click Here | 0:00 | 6.34 | 5.24 | 5.12 | 5.27 | 5.3 | 7.24 | 7.13 | 1.64 | 1.89 | 1.98 | 2.11 | 49 | 43 | 17 | 0 | 0 | 0 | 0.264 | 0.374 | 0.412 | 0.091 | 0.14 | 0.206 | 11.7 | 33.6 | 29.1 | 28.7 | 35.4 | 23.4 | 67.2 | 58.2 | 57.4 | 70.8 | 3.3 | 2.54 | 2.9 | 5.4 | 0.041 | 15.7 | 9.8 | 0.8605 | 59.7 | 91.9 | 0.224 | 0.0364 | 14.23 | 13.39 | 14.36 | 0.97 | 1.454 | 2.604 | 9.557 | 2.9905 | 29.05 | 5.7 | 10.1 | 2019-06-04
2019-06-05 | Click Here | 0:00 | 6.06 | 5.1 | 5.13 | 4.97 | 4.98 | 6.31 | 7.07 | 1.73 | 1.86 | 1.91 | 2.18 | 50 | 45 | 19 | 2 | 1 | 0 | 0.291 | 0.496 | 0.513 | 0.097 | 0.125 | 0.184 | 12.6 | 33.4 | 31.3 | 30.6 | 36.4 | 25.2 | 66.8 | 62.6 | 61.2 | 72.8 | 3.22 | 2.63 | 3.1 | 5.6 | 0.038 | 17.6 | 11.3 | 0.57966 | 59.9 | 94.1 | 0.2238 | 0.026 | 14.116 | 13.311 | 14.286 | 0.975 | 1.506 | 2.641 | 9.443 | 2.8797 | 26.1 | 5.7 | 10.1 | 2019-06-05
2019-06-06 | Click Here | 0:00 | 6.45 | 5.21 | 5.11 | 5.13 | 5.17 | 6.58 | 7.22 | 1.45 | 1.86 | 1.84 | 2.22 | 49 | 44 | 15 | 0 | 0 | 0 | 0.253 | 0.364 | 0.329 | 0.056 | 0.21 | 0.413 | 12.6 | 34.2 | 32.1 | 31.7 | 37.1 | 25.2 | 68.4 | 64.2 | 63.4 | 74.2 | 3.29 | 2.39 | 3 | 5.5 | 0.04 | 17.7 | 11.8 | 0.6236 | 57.5 | 89.5 | 0.2238 | 0.0479 | 14.34 | 13.54 | 14.52 | 0.98 | 1.528 | 2.584 | 9.428 | 2.8836 | 31.95 | 5.7 | 10.3 | 2019-06-06
2019-06-07 | Click Here | 0:00 | 6.16 | 5.19 | 5.1 | 5.11 | 5.14 | 7.13 | 7.19 | 1.7 | 1.84 | 2.05 | 2.21 | 41 | 34 | 21 | 0 | 0 | 0 | 0.215 | 0.382 | 0.572 | 0.076 | 0.21 | 0.287 | 12.9 | 36.2 | 34.2 | 32.9 | 37.9 | 25.8 | 72.4 | 68.4 | 65.8 | 75.8 | 3.32 | 2.44 | 3.2 | 5.7 | 0.004 | 18 | 12 | 0.18439 | 60.2 | 87.2 | 0.2203 | 0.0591 | 14.18 | 13.35 | 14.34 | 0.99 | 1.502 | 2.517 | 9.809 | 2.4744 | 30.04 | 5.7 | 10.6 | 2019-06-07
2019-06-08 | Click Here | 0:00 | 6.18 | 5.2 | 5.17 | 5.14 | 5.23 | 7.46 | 7.55 | 0 | 0 | 0 | 0 | 40 | 33 | 18 | 0 | 0 | 0 | 0.243 | 0.471 | 0.592 | 0.074 | 0.364 | 0.45 | 12.9 | 35.1 | 33.6 | 30.8 | 37.4 | 25.8 | 70.2 | 67.2 | 61.6 | 74.8 | 3.15 | 2.29 | 3.1 | 6 | 0.018 | 18.1 | 12.1 |  | 60.4 | 88.6 | 0.2189 | 0.0566 | 13.6 | 13.68 | 13.68 | 0 | 1.356 | 2.515 | 9.074 |  | 29.11 | 5.7 | 10.6 | 2019-06-08
2019-06-09 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-06-09
2019-06-10 | Click Here | 0:00 | 6.25 | 5.02 | 5.18 | 4.89 | 4.9 | 6.3 | 7.25 | 1.37 | 1.91 | 2.01 | 2.35 | 42 | 36 | 17 | 1 | 0 | 0 | 0.227 | 0.386 | 0.599 | 0.076 | 0.271 | 0.303 | 13 | 35.7 | 33.8 | 34.2 | 40.1 | 26 | 71.4 | 67.6 | 68.4 | 80.2 | 3.1 | 2.44 | 3 | 5.6 | 0.024 | 17.8 | 12.7 | 0.76997 | 60.1 | 91.9 | 0.2191 | 0.0365 | 14.237 | 12.831 | 14.386 | 1.555 | 1.434 | 2.485 | 9.418 | 3.17 | 29.03 | 5.7 | 10.6 | 2019-06-10
2019-06-11 | Click Here | 0:00 | 6.34 | 5.19 | 5.08 | 5.15 | 5.11 | 6.74 | 7.49 | 1.46 | 1.99 | 2 | 2.33 | 42 | 37 | 22 | 2 | 0 | 0 | 0.221 | 0.405 | 0.992 | 0.094 | 0.141 | 0.198 | 12.8 | 34.7 | 29.6 | 31.1 | 40.3 | 25.6 | 69.4 | 59.2 | 62.2 | 80.6 | 3.03 | 2.31 | 3 | 6.4 | 0.033 | 16.7 | 12.4 | 0.68985 | 60.2 | 89.7 | 0.2191 | 0.0477 | 16.515 | 13.631 | 15.015 | 1.374 | 1.442 | 2.447 | 10 | 3.0699 | 28.09 | 5.7 | 10.9 | 2019-06-11
2019-06-12 | Click Here | 0:00 | 6.29 | 5.14 | 5.09 | 5.11 | 5.08 | 6.88 | 7.07 | 1.69 | 1.97 | 2.14 | 2.4 | 43 | 36 | 17 | 1 | 0 | 0 | 0.198 | 0.336 | 0.421 | 0.074 | 0.101 | 0.136 | 12.5 | 34.6 | 30.1 | 31.6 | 39.9 | 25 | 69.2 | 60.2 | 63.2 | 79.8 | 3.07 | 2.47 | 2.9 | 6.2 | 0.029 | 16.6 | 12.4 | 0.48616 | 60 | 92 | 0.2204 | 0.0364 | 13.63 | 12.79 | 13.73 | 0.94 | 1.388 | 2.416 | 9.361 | 2.8962 | 28.99 | 5.7 | 10.9 | 2019-06-12
2019-06-13 | Click Here | 0:00 | 6.22 | 5.01 | 5.09 | 4.98 | 5 | 6.72 | 6.85 | 1.53 | 1.94 | 2.07 | 2.34 | 47 | 39 | 15 | 0 | 0 | 0 | 0.221 | 0.378 | 0.479 | 0.068 | 0.118 | 0.174 | 12.4 | 35 | 32.6 | 31.2 | 39.3 | 24.8 | 70 | 65.2 | 62.4 | 78.6 | 3.13 | 2.61 | 3 | 6.5 | 0.021 | 16.6 | 12.6 | 0.60878 | 60.3 | 92.4 | 0.2201 | 0.036 | 13.94 | 13.15 | 14.1 | 0.95 | 1.399 | 2.405 | 9.593 | 2.9688 | 31.55 | 5.7 | 10.9 | 2019-06-13
2019-06-14 | Click Here | 0:00 | 6.17 | 5.14 | 5.1 | 5.11 | 5.17 | 6.88 | 6.74 | 1.62 | 1.98 | 2.17 | 2.43 | 47 | 36 | 26 | 2 | 0 | 0 | 0.267 | 0.417 | 0.688 | 0.071 | 0.109 | 0.17 | 12.2 | 34.8 | 30.9 | 30.2 | 40.2 | 24.4 | 69.6 | 61.8 | 60.4 | 80.4 | 3.06 | 2.7 | 3.2 | 6.1 | 0.037 | 16.5 | 12.6 | 0.69106 | 60.4 | 88.4 | 0.2195 | 0.0513 | 14.208 | 12.419 | 13.389 | 0.97 | 1.354 | 2.396 | 9.152 | 3.0211 | 30 | 5.8 | 11.2 | 2019-06-14
2019-06-15 | Click Here | 0:00 | 6.19 | 5.19 | 5.1 | 5.2 | 5.25 | 7.15 | 7.12 | 1.57 | 1.88 | 1.91 | 2.17 | 41 | 33 | 10 | 0 | 0 | 0 | 0.214 | 0.382 | 0.299 | 0.044 | 0.134 | 0.216 | 12.6 | 35.3 | 31.1 | 31.7 | 41 | 25.2 | 70.6 | 62.2 | 63.4 | 82 | 3.17 | 2.63 | 3.2 | 6.4 | 0.036 | 16.6 | 12.6 | 0.7563 | 60.8 | 91.9 | 0.2159 | 0 | 13.19 | 12.24 | 13.23 | 0.99 | 0 | 0 | 0 | 3.0263 | 29.45 | 5.8 | 11.2 | 2019-06-15
2019-06-16 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-06-16
2019-06-17 | Click Here | 0:00 | 6.04 | 5.25 | 5.09 | 5.16 | 5.47 | 7.96 | 7.32 | 1.71 | 1.93 | 2.11 | 2.16 | 40 | 33 | 8 | 0 | 0 | 0 | 0.235 | 0.392 | 0.276 | 0.065 | 0.206 | 0.197 | 13 | 33.2 | 31.1 | 38.4 | 41.2 | 26 | 66.4 | 62.2 | 76.8 | 82.4 | 3.2 | 2.43 | 2.6 | 6 | 0.114 | 17.3 | 12.3 | 0.6953 | 61.9 | 90.3 | 0.2082 | 0.0439 | 14.62 | 13.3 | 14.75 | 1.45 | 1.334 | 2.323 | 9.864 | 2.9353 | 28.64 | 5.8 | 11.2 | 2019-06-17
2019-06-18 | Click Here | 0:00 | 5.82 | 5.13 | 5.23 | 5.1 | 5.12 | 7.99 | 7.47 | 1.54 | 1.9 | 2.17 | 2.15 | 39 | 32 | 8 | 0 | 0 | 0 | 0.264 | 0.398 | 0.23 | 0.059 | 0.205 | 0.174 | 13 | 35 | 31.2 | 30.8 | 40.8 | 26 | 70 | 64.2 | 61.6 | 81.6 | 3.18 | 2.73 | 2.7 | 5.8 | 0.16 | 17 | 12.4 | 0.38826 | 61.8 | 89.9 | 0.2086 | 0.0459 | 14.13 | 14.2 | 14.2 | 0 | 1.375 | 2.318 | 10 | 2.6083 | 28.87 | 5.8 | 11.2 | 2019-06-18
2019-06-19 | Click Here | 0:00 | 5.94 | 5.16 | 5.14 | 5.15 | 5.2 | 7.81 | 7.67 | 1.61 | 1.98 | 2.09 | 2.23 | 37 | 30 | 7 | 0 | 0 | 0 | 0.217 | 0.306 | 0.215 | 0.052 | 0.092 | 0.087 | 12.9 | 35.2 | 30.9 | 30.5 | 41.6 | 25.8 | 70.4 | 61.8 | 61 | 83.2 | 3.17 | 2.69 | 3 | 6.1 | 0.099 | 16.9 | 12.4 | 0.73598 | 62 | 91.9 | 0.2049 | 0.0364 | 15.032 | 14.194 | 15.194 | 0.981 | 1.465 | 2.316 | 10 | 3.006 | 29.44 | 5.8 | 10.8 | 2019-06-19
2019-06-20 | Click Here | 0:00 | 6 | 5.17 | 5.14 | 5.19 | 5.24 | 7.49 | 7.77 | 1.69 | 2.04 | 2.19 | 2.43 | 40 | 32 | 10 | 0 | 0 | 0 | 0.176 | 0.297 | 0.211 | 0.041 | 0.084 | 0.146 | 13.6 | 36.3 | 33.4 | 33 | 42.4 | 27.2 | 72.6 | 66.8 | 66 | 84.8 | 3.14 | 2.74 | 3.9 | 6.4 | 0.047 | 18.8 | 13.4 |  | 60.9 | 90.8 | 0.2147 | 0.0418 | 13.9 | 13.96 | 13.96 | 0 | 1.441 | 2.314 | 10 |  | 28.92 | 5.8 | 10.8 | 2019-06-20
2019-06-21 | Click Here | 0:00 | 6.38 | 5.36 | 5.16 | 5.2 | 5.21 | 6.64 | 7.52 | 1.51 | 2.01 | 2.08 | 2.37 | 38 | 29 | 12 | 0 | 0 | 0 | 0.261 | 0.427 | 0.304 | 0.051 | 0.08 | 0.116 | 13.1 | 35.1 | 33.4 | 33.2 | 41.1 | 26.2 | 70.2 | 66.8 | 66.4 | 82.2 | 2.94 | 2.68 | 3.6 | 6.2 | 0.036 | 17.8 | 13.7 | 0.90914 | 60.7 | 91 | 0.2145 | 0.0416 | 13.58 | 12.72 | 13.7 | 0.98 | 1.3 | 2.311 | 9.161 | 3.0691 | 27.07 | 5.8 | 10.8 | 2019-06-21
2019-06-22 | Click Here | 0:00 | 6.4 | 5.2 | 5.2 | 5.07 | 5.06 | 7.14 | 7.22 | 1.59 | 1.85 | 1.84 | 1.66 | 39 | 30 | 10 | 0 | 0 | 0 | 0.314 | 0.603 | 0.232 | 0.083 | 0.091 | 0.086 | 12.5 | 35.3 | 33 | 32.8 | 43.1 | 25 | 70.6 | 66 | 65.6 | 86.2 | 2.99 | 2.71 | 3.4 | 6 | 0.028 | 16.6 | 13.3 | 1.2411 | 62.2 | 90.4 | 0.205 | 0.0438 | 13.02 | 12.22 | 13.14 | 0.94 | 0 | 0 | 0 | 2.9811 | 29.25 | 6 | 10.8 | 2019-06-22
2019-06-23 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 1.3111 | 0 | 0 | 0 | 0 | 13.217 | 12.279 | 13.256 | 0.977 | 1.267 | 2.311 | 9.19 | 3.0311 | 0 | 6 | 10.8 | 2019-06-23
2019-06-24 | Click Here | 0:00 | 6.1 | 5.27 | 5.21 | 5.69 | 5.75 | 8.24 | 7.3 | 1.59 | 1.93 | 1.86 | 1.65 | 34 | 23 | 8 | 0 | 0 | 0 | 0.326 | 0.803 | 0.214 | 0.061 | 0.084 | 0.099 | 12.3 | 34.1 | 32.2 | 32.4 | 41.5 | 24.6 | 68.2 | 64.4 | 64.8 | 83 | 3.15 | 2.68 | 3.2 | 5.9 | 0.034 | 16 | 13.3 | 1.2872 | 61.6 | 91.9 | 0.2103 | 0.0365 | 14.2 | 13.36 | 14.35 | 0.99 | 1.325 | 2.362 | 9.733 | 2.9972 | 29.12 | 6 | 10.8 | 2019-06-24
2019-06-25 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-06-25
2019-06-26 | Click Here | 0:00 | 6.21 | 5.21 | 5.18 | 5.02 | 5.05 | 6.68 | 8.16 | 1.78 | 1.91 | 2.05 | 1.44 | 31 | 25 | 10 | 1 | 0 | 0 | 0.296 | 0.563 | 0.326 | 0.081 | 0.113 | 0.124 | 12.6 | 34.8 | 32.2 | 32.3 | 40.7 | 25.2 | 69.6 | 64.4 | 64.6 | 81.4 | 3.09 | 2.51 | 3.1 | 6.4 | 0.029 | 16.5 | 13.4 | 1.1222 | 61.4 | 90.4 | 0.2105 | 0.0436 | 15.1 | 14.29 | 15.24 | 0.95 | 1.329 | 2.298 | 10 | 2.8022 | 27.2 | 6 | 9.8 | 2019-06-26
2019-06-27 | Click Here | 0:00 | 6.14 | 5.05 | 5.22 | 4.97 | 5.01 | 6.5 | 7.28 | 1.74 | 1.93 | 2.06 | 2.13 | 30 | 24 | 9 | 0 | 0 | 0 | 0.261 | 0.326 | 0.342 | 0.062 | 0.098 | 0.137 | 13.2 | 34.6 | 33.1 | 32.3 | 40.6 | 26.4 | 68.2 | 66.2 | 64.6 | 81.2 | 3.13 | 2.61 | 3.3 | 6.6 | 0.031 | 17.4 | 13.5 | 0.1136 | 64.6 | 90.6 | 0.2103 | 0.0434 | 14.84 | 14.06 | 15.03 | 0.97 | 1.427 | 2.303 | 10.33 | 1.9936 | 29.7 | 6 | 9.8 | 2019-06-27
2019-06-28 | Click Here | 0:00 | 5.77 | 5.29 | 5.11 | 5.15 | 5.25 | 7.95 | 7.08 | 1.36 | 1.64 | 1.92 | 2.02 | 30 | 23 | 8 | 0 | 0 | 0 | 0.559 | 0.318 | 0.679 | 0.059 | 0.091 | 0.05 | 13.7 | 34.9 | 33.4 | 33.8 | 42.4 | 27.4 | 69.8 | 66.8 | 67.6 | 84.8 | 3.06 | 2.45 | 3.2 | 6.4 | 0.033 | 18.7 | 14.5 | 0.72425 | 47.8 | 91.2 | 0.3197 | 0.0421 | 14.47 | 14.6 | 14.6 | 0 | 1.412 | 2.301 | 10.887 | 2.6742 | 28.17 | 6 | 10 | 2019-06-28
2019-06-29 | Click Here | 0:00 | 5.81 | 5.24 | 5.27 | 5.13 | 5.27 | 7.62 | 7.7 | 1.66 | 1.98 | 1.94 | 1.96 | 29 | 22 | 7 | 0 | 0 | 0 | 0.572 | 0.359 | 0.688 | 0.061 | 0.086 | 0.098 | 13.7 | 34.1 | 33.3 | 33.1 | 39.4 | 27.4 | 68.2 | 66.6 | 66.2 | 78.8 | 3.29 | 2.61 | 3.2 | 6.1 | 0.043 | 18.9 | 14.6 |  | 47.6 | 90.8 | 0.3207 | 0.0441 | 14.5 | 13.63 | 14.61 | 0.98 | 0 | 0 | 0 |  | 28.87 | 6 | 9.7 | 2019-06-29
2019-06-30 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-06-30
2019-07-01 | Click Here | 0:00 | 6.11 | 5.14 | 5.27 | 5.09 | 5.15 | 6.91 | 7.89 | 1.76 | 2.08 | 2.11 | 2.42 | 30 | 24 | 9 | 0 | 0 | 0 | 0.371 | 0.284 | 0.632 | 0.059 | 0.061 | 0.063 | 14.1 | 37.2 | 34.2 | 33.4 | 44.1 | 28.2 | 74.4 | 68.4 | 66.8 | 88.2 | 3.24 | 2.69 | 3 | 6.3 | 0.038 | 19.8 | 15.5 | 0.47959 | 47.8 | 91 | 0.3205 | 0.0439 | 13.81 | 12.92 | 13.88 | 0.96 | 1.284 | 2.311 | 9.511 | 2.9496 | 28.13 | 6 | 9.7 | 2019-07-01
2019-07-02 | Click Here | 0:00 | 6.79 | 5.3 | 5.31 | 5.12 | 5.15 | 7.14 | 6.99 | 1.57 | 1.65 | 1.71 | 2 | 34 | 28 | 11 | 1 | 0 | 0 | 0.374 | 0.296 | 0.642 | 0.078 | 0.074 | 0.061 | 13.4 | 34.4 | 33.1 | 32.9 | 43.5 | 26.8 | 68.8 | 66.2 | 65.8 | 87 | 3.26 | 2.74 | 3.2 | 6 | 0.04 | 17.9 | 15.2 | 0.93437 | 59.4 | 89.2 | 0.2262 | 0.0495 | 13.99 | 13.11 | 14.1 | 0.99 | 1.285 | 2.296 | 9.529 | 3.0544 | 26.76 | 6 | 9.7 | 2019-07-02
2019-07-03 | Click Here | 0:00 | 6.1 | 5.26 | 5.32 | 5.24 | 5.29 | 7.81 | 7.13 | 1.56 | 1.72 | 2.09 | 1.82 | 36 | 29 | 10 | 0 | 0 | 0 | 0.542 | 0.294 | 0.697 | 0.163 | 0.279 | 0.063 | 13.1 | 35.2 | 31.8 | 31.7 | 42.5 | 26.2 | 70.4 | 63.6 | 63.4 | 85 | 3.16 | 2.56 | 3.3 | 5.8 | 0.161 | 16.8 | 14.5 | 0.54327 | 59.1 | 91.5 | 0.228 | 0.0382 | 13.81 | 12.9 | 13.87 | 0.97 | 1.296 | 2.293 | 9.737 | 2.4833 | 28.64 | 5.8 | 9.7 | 2019-07-03
2019-07-04 | Click Here | 0:00 | 5.82 | 5.37 | 5.24 | 5.25 | 5.31 | 8 | 7.73 | 1.64 | 1.92 | 2.1 | 2.04 | 34 | 27 | 9 | 0 | 0 | 0 | 0.511 | 0.288 | 0.627 | 0.063 | 0.079 | 0.054 | 13.2 | 34.6 | 32.3 | 32.2 | 42.4 | 26.4 | 69.2 | 64.6 | 64.4 | 84.8 | 3.28 | 2.44 | 3.2 | 5.9 | 0.086 | 17 | 14.7 | 0.45439 | 58.9 | 91.3 | 0.2286 | 0.0389 | 13.98 | 13.17 | 14.1 | 0.94 | 1.32 | 2.22 | 10 | 2.5844 | 29.11 | 5.8 | 9.6 | 2019-07-04
2019-07-05 | Click Here | 0:00 | 5.94 | 5.3 | 5.34 | 5.29 | 5.34 | 7.68 | 7.85 | 1.7 | 1.99 | 2.11 | 2.17 | 38 | 30 | 7 | 0 | 0 | 0 | 0.31 | 0.276 | 0.517 | 0.07 | 0.074 | 0.051 | 13.5 | 35.1 | 32.5 | 32.2 | 41.9 | 27 | 70.2 | 65 | 64.4 | 83.8 | 3.29 | 2.5 | 3.4 | 6.1 | 0.069 | 17.1 | 14.8 | 0.73007 | 59 | 91.9 | 0.2279 | 0.0351 | 14.45 | 13.528 | 14.478 | 0.95 | 1.367 | 2.136 | 10 | 3.0201 | 29.6 | 5.8 | 9.4 | 2019-07-05
2019-07-06 | Click Here | 0:00 | 5.89 | 5.24 | 5.28 | 5.3 | 5.34 | 7.37 | 7.54 | 1.44 | 1.77 | 1.94 | 1.69 | 34 | 26 | 7 | 0 | 0 | 0 | 0.224 | 0.317 | 0.637 | 0.059 | 0.246 | 1.09 | 12.9 | 34.6 | 32.2 | 31.7 | 41.5 | 25.8 | 69.2 | 64.4 | 63.7 | 83 | 3.18 | 2.47 | 2.9 | 6.1 | 0.041 | 17.1 | 14.9 | 0.65895 | 58.7 | 91.4 | 0.2296 | 0.0383 | 13.41 | 12.48 | 13.43 | 0.95 | 0 | 0 | 0 | 3.289 | 29.62 | 5.8 | 9.4 | 2019-07-06
2019-07-07 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-07-07
2019-07-08 | Click Here | 0:00 | 5.99 | 5.38 | 5.29 | 5.27 | 5.27 | 8.02 | 7.89 | 1.59 | 1.77 | 2.1 | 2.22 | 40 | 32 | 8 | 0 | 0 | 0 | 0.103 | 0.306 | 1.12 | 0.158 | 0.261 | 0.069 | 13.8 | 35.3 | 33.5 | 33 | 44.8 | 27.6 | 70.6 | 67 | 66 | 89.6 | 3.26 | 2.29 | 3.1 | 5.8 | 0.168 | 18.9 | 15.4 | 0.43689 | 59.9 | 90.7 | 0.2223 | 0.042 | 15.27 | 14.42 | 15.39 | 0.97 | 1.586 | 2.194 | 10.64 | 2.7769 | 29.11 | 5.8 | 9.4 | 2019-07-08
2019-07-09 | Click Here | 0:00 | 5.99 | 5.3 | 5.37 | 5.2 | 5.28 | 7.85 | 7.47 | 1.6 | 1.8 | 2.15 | 2.66 | 37 | 30 | 9 | 0 | 0 | 0 | 0.626 | 0.333 | 1.36 | 0.161 | 0.245 | 0.066 | 13.9 | 35.4 | 33.8 | 33 | 43.6 | 27.8 | 70.8 | 67.6 | 66 | 87.2 | 3.21 | 2.43 | 3 | 5.9 | 0.096 | 19.3 | 15.8 | 0.72751 | 59.6 | 90.4 | 0.2234 | 0.0425 | 14.73 | 13.98 | 14.92 | 0.94 | 1.521 | 2.294 | 10.165 | 3.0075 | 29.11 | 5.8 | 9 | 2019-07-09
2019-07-10 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-07-10
2019-07-11 | Click Here | 0:00 | 6.01 | 5.27 | 5.34 | 5.29 | 5.34 | 7.52 | 7.69 | 1.57 | 1.86 | 2.09 | 2.32 | 40 | 33 | 8 | 0 | 0 | 0 | 0.347 | 0.331 | 0.996 | 0.104 | 0.174 | 0.069 | 13.5 | 34.9 | 34.2 | 33.6 | 44 | 27 | 69.8 | 68.4 | 67.2 | 88 | 3.16 | 2.51 | 2.8 | 5.7 | 0.087 | 19.3 | 15.7 | 0.88066 | 59.7 | 90.9 | 0.2229 | 0.0414 | 13.39 | 12.51 | 13.44 | 0.93 | 1.426 | 2.327 | 8.778 | 3.1207 | 29.55 | 5.8 | 9 | 2019-07-11
2019-07-12 | Click Here | 0:00 | 6.28 | 5.53 | 5.35 | 5.26 | 5.34 | 6.87 | 7.56 | 1.53 | 1.86 | 1.94 | 1.96 | 39 | 33 | 9 | 0 | 0 | 0 | 0.314 | 0.306 | 0.712 | 0.061 | 0.113 | 0.064 | 13.6 | 35.3 | 32.2 | 31.6 | 43.4 | 27.2 | 70.6 | 64.4 | 63.2 | 86.8 | 3.1 | 2.67 | 3 | 6.1 | 0.052 | 17.3 | 15.2 | 0.88221 | 59.9 | 91.2 | 0.2228 | 0.0411 | 15.12 | 14.25 | 15.21 | 0.96 | 1.477 | 2.324 | 10 | 3.0222 | 27.51 | 5.8 | 9 | 2019-07-12
2019-07-13 | Click Here | 0:00 | 5.99 | 5.15 | 5.13 | 5.04 | 5.18 | 6.8 | 6.67 | 1.61 | 1.91 | 2.04 | 2.08 | 38 | 32 | 12 | 1 | 0 | 0 | 0.263 | 0.278 | 0.731 | 0.082 | 0.108 | 0.064 | 13.8 | 35.3 | 33.8 | 33 | 43.6 | 27.6 | 70.6 | 67.6 | 66 | 87.2 | 3.07 | 2.61 | 2.9 | 5.8 | 0.042 | 18 | 15.5 | 0.83331 | 58.9 | 91 | 0.2297 | 0.0408 | 14.17 | 13.28 | 14.27 | 0.99 | 0 | 0 | 0 | 3.0033 | 29.31 | 5.6 | 9 | 2019-07-13
2019-07-14 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.64819 | 0 | 0 | 0 | 0 | 14.232 | 13.267 | 14.267 | 0.972 | 1.393 | 2.307 | 10 | 2.9782 | 0 | 5.6 | 9.2 | 2019-07-14
2019-07-15 | Click Here | 0:00 | 6.04 | 5.17 | 5.11 | 5.07 | 5.14 | 6.74 | 5.1 | 1.8 | 2.07 | 2.2 | 2.51 | 37 | 30 | 11 | 0 | 0 | 0 | 0.222 | 0.267 | 0.698 | 0.074 | 0.107 | 0.059 | 13.5 | 35.7 | 32.6 | 30.9 | 44.3 | 27 | 71.4 | 65.2 | 61.8 | 88.6 | 3.14 | 2.58 | 2.9 | 6.4 | 0.058 | 18.9 | 16.5 | 0.41536 | 60.1 | 91.1 | 0.2198 | 0.041 | 14.215 | 13.378 | 14.347 | 0.969 | 1.499 | 2.301 | 9.603 | 2.9654 | 29.59 | 5.6 | 9.2 | 2019-07-15
2019-07-16 | Click Here | 0:00 | 5.94 | 5.16 | 5.11 | 5.11 | 5.2 | 7.2 | 7.4 | 1.68 | 1.84 | 2.09 | 2.51 | 39 | 33 | 13 | 0 | 0 | 0 | 0.198 | 0.289 | 0.744 | 0.069 | 0.112 | 0.084 | 14.6 | 37.5 | 34.9 | 34.1 | 44.9 | 29.2 | 75 | 69.8 | 68.2 | 89.8 | 3.22 | 2.44 | 3.2 | 6.4 | 0.081 | 19.1 | 16.6 | 0.35872 | 59.1 | 89.1 | 0.2284 | 0.0499 | 14.82 | 13.92 | 14.91 | 0.99 | 1.429 | 2.291 | 10.2 | 2.9487 | 29.09 | 5.6 | 9.2 | 2019-07-16
2019-07-17 | Click Here | 0:00 | 6.15 | 5.32 | 5.11 | 5.03 | 5.02 | 6.86 | 7.63 | 1.71 | 1.94 | 2.1 | 3.06 | 39 | 33 | 13 | 0 | 0 | 0 | 0.314 | 0.357 | 0.813 | 0.086 | 0.114 | 0.062 | 14.5 | 36.4 | 35.3 | 34.9 | 45.6 | 29 | 72.8 | 70.6 | 69.8 | 91.2 | 3.11 | 2.71 | 3 | 6.1 | 0.033 | 19.4 | 16.6 | 0.038713 | 59.8 | 91.4 | 0.2229 | 0.0409 | 14.792 | 13.908 | 14.882 | 0.974 | 1.517 | 2.289 | 10 | 3.0087 | 29.56 | 5.6 | 9.2 | 2019-07-17
2019-07-18 | Click Here | 0:00 | 6.45 | 5.33 | 5.07 | 5.09 | 5.17 | 6.91 | 7.03 | 1.65 | 1.91 | 2.04 | 2.96 | 40 | 34 | 9 | 0 | 0 | 0 | 0.252 | 0.267 | 0.508 | 0.073 | 0.109 | 0.068 | 14.7 | 37.3 | 35.9 | 35.2 | 46 | 29.4 | 74.6 | 71.8 | 70.4 | 92 | 3.01 | 2.61 | 2.9 | 6.3 | 0.047 | 19.9 | 17.1 | 0.6159 | 58.5 | 85.8 | 0.2325 | 0.0662 | 13.69 | 12.81 | 13.77 | 0.96 | 1.476 | 2.293 | 9.041 | 3.1259 | 29.69 | 5.6 | 9.2 | 2019-07-18
2019-07-19 | Click Here | 0:00 | 6.11 | 5.27 | 5.4 | 5.11 | 5.16 | 7.71 | 7.03 | 1.52 | 1.7 | 2.07 | 2.11 | 41 | 33 | 10 | 0 | 0 | 0 | 0.277 | 0.318 | 0.521 | 0.069 | 0.112 | 0.072 | 14.6 | 36.4 | 35.6 | 36.1 | 45.4 | 29.2 | 72.8 | 71.2 | 72.2 | 90.8 | 3.21 | 2.44 | 3.1 | 6.1 | 0.059 | 19.8 | 17.3 | 0.77297 | 58.1 | 88.4 | 0.2331 | 0.0497 | 14.15 | 13.12 | 14.28 | 1.16 | 1.53 | 2.287 | 7.052 | 2.823 | 29.11 | 5.6 | 9.2 | 2019-07-19
2019-07-20 | Click Here | 0:00 | 6.23 | 5.31 | 5.25 | 5.22 | 5.26 | 7.62 | 7.45 | 1.64 | 1.79 | 2.04 | 2.09 | 40 | 33 | 11 | 0 | 0 | 0 | 0.288 | 0.329 | 0.543 | 0.067 | 0.145 | 0.128 | 14.5 | 34.6 | 34.4 | 35.2 | 46.2 | 29 | 69.2 | 68.8 | 70.4 | 92.4 | 3.5 | 2.55 | 3 | 6.2 | 0.061 | 19.9 | 17.4 |  | 58.3 | 89 | 0.233 | 0.0491 | 13.63 | 12.66 | 13.65 | 0.99 | 0 | 0 | 0 |  | 29.34 | 5.6 | 9 | 2019-07-20
2019-07-21 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-07-21
2019-07-22 | Click Here | 0:00 | 6.05 | 5.18 | 5.29 | 4.96 | 5.02 | 4.9 | 5.52 | 1.66 | 1.87 | 2.12 | 2.15 | 40 | 32 | 10 | 0 | 0 | 0 | 0.263 | 0.296 | 0.594 | 0.061 | 0.121 | 0.063 | 14.6 | 35.8 | 34.7 | 34.2 | 36.1 | 29.2 | 71.6 | 69.4 | 68.4 | 72.2 | 3.46 | 2.59 | 2.9 | 5.2 | 0.057 | 18.9 | 17.1 | 0.92679 | 58.1 | 89.4 | 0.2328 | 0.0487 | 14.209 | 13.171 | 14.221 | 1.05 | 1.332 | 2.21 | 7.687 | 3.0168 | 29.98 | 5.6 | 9 | 2019-07-22
2019-07-23 | Click Here | 0:00 | 6.2 | 5.37 | 5.17 | 5.06 | 5.07 | 6.63 | 7.47 | 1.58 | 1.81 | 1.99 | 2.04 | 39 | 33 | 12 | 0 | 0 | 0 | 0.261 | 0.286 | 0.632 | 0.068 | 0.216 | 0.114 | 14.5 | 36.1 | 34.9 | 35 | 46.4 | 29 | 72.2 | 69.8 | 70 | 92.8 | 3.38 | 2.62 | 3 | 5.5 | 0.048 | 18.9 | 17.1 | 0.95074 | 60.7 | 90.4 | 0.2166 | 0.0436 | 14.18 | 13.3 | 14.28 | 0.98 | 1.444 | 2.167 | 9.689 | 3.0107 | 29.69 | 5.6 | 9 | 2019-07-23
2019-07-24 | Click Here | 0:00 | 5.97 | 5.23 | 5.15 | 5.14 | 5.19 | 7.79 | 7.13 | 1.65 | 1.75 | 2.12 | 2.03 | 36 | 29 | 9 | 0 | 0 | 0 | 0.523 | 0.281 | 0.963 | 0.148 | 0.256 | 0.104 | 14.8 | 36.2 | 35 | 34.7 | 46.7 | 29.4 | 72.4 | 70 | 69.4 | 93.4 | 3.24 | 2.43 | 3.6 | 4.8 | 0.124 | 19.4 | 17.2 | 0.61427 | 61.6 | 91.2 | 0.2102 | 0.04 | 14.1 | 13.15 | 14.13 | 0.98 | 1.474 | 2.167 | 7.908 | 2.6643 | 28.64 | 5.4 | 9.4 | 2019-07-24
2019-07-25 | Click Here | 0:00 | 5.82 | 5.18 | 5.23 | 5.14 | 5.17 | 7.66 | 7.67 | 1.6 | 1.76 | 2.09 | 2.17 | 36 | 29 | 10 | 0 | 0 | 0 | 0.464 | 0.274 | 0.71 | 0.151 | 0.149 | 0.106 | 14.9 | 36.7 | 35.4 | 35 | 46 | 29.8 | 73.4 | 70.8 | 70 | 92 | 3.23 | 2.63 | 3.4 | 5 | 0.127 | 19.6 | 17.4 | 0.82283 | 62.2 | 91.3 | 0.2057 | 0.0398 | 15.041 | 14.112 | 15.092 | 0.98 | 1.545 | 2.151 | 8.274 | 3.0128 | 28.87 | 5.4 | 9 | 2019-07-25
2019-07-26 | Click Here | 0:00 | 5.99 | 5.24 | 5.17 | 5.22 | 5.29 | 7.69 | 7.76 | 1.65 | 1.82 | 2.14 | 2.16 | 35 | 27 | 12 | 0 | 0 | 0 | 0.277 | 0.162 | 0.695 | 0.067 | 0.127 | 0.114 | 15 | 36.4 | 34.9 | 34.5 | 46.5 | 30 | 72.8 | 69.8 | 69 | 93 | 3.36 | 2.59 | 3 | 5.4 | 0.099 | 19.8 | 17.5 | 0.80496 | 61.9 | 91.9 | 0.2107 | 0.0368 | 14.718 | 13.729 | 14.71 | 0.981 | 1.641 | 2.155 | 7.789 | 3.045 | 29.18 | 5.4 | 9 | 2019-07-26
2019-07-27 | Click Here | 0:00 | 5.99 | 5.19 | 5.15 | 5.34 | 5.39 | 7.44 | 7.54 | 1.62 | 1.83 | 2.09 | 2.11 | 32 | 24 | 14 | 0 | 0 | 0 | 0.241 | 0.196 | 0.796 | 0.042 | 0.146 | 0.217 | 15.1 | 34.9 | 33.8 | 33.4 | 45.6 | 30.2 | 69.8 | 67.6 | 66.8 | 91.2 | 3.41 | 2.64 | 2.9 | 6.1 | 0.087 | 19.9 | 17.7 | 0.87925 | 62 | 91.5 | 0.21 | 0.0384 | 14.58 | 13.64 | 14.61 | 0.97 | 0 | 0 | 0 | 3.0092 | 29.88 | 5.4 | 9 | 2019-07-27
2019-07-28 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-07-28
2019-07-29 | Click Here | 0:00 | 6.07 | 5.31 | 5.11 | 5.06 | 5.14 | 7.56 | 7.5 | 1.48 | 1.69 | 2.01 | 2.21 | 33 | 26 | 13 | 0 | 0 | 0 | 0.525 | 0.252 | 1.32 | 0.142 | 0.312 | 0.189 | 15.4 | 38.3 | 37.4 | 36.9 | 45.8 | 30.8 | 76.6 | 74.8 | 73.8 | 91.6 | 3.21 | 2.39 | 3.1 | 6 | 0.056 | 21.4 | 18.6 | 0.31417 | 62.5 | 91.9 | 0.2042 | 0.0364 | 18.08 | 17.23 | 18.2 | 0.97 | 1.74 | 2.367 | 13.12 | 2.4442 | 29.57 | 5.4 | 9 | 2019-07-29
2019-07-30 | Click Here | 0:00 | 6.12 | 5.35 | 5.3 | 5.18 | 5.19 | 7.51 | 7.62 | 1.48 | 1.7 | 1.89 | 2.08 | 32 | 25 | 30 | 3 | 0 | 0 | 0.509 | 0.248 | 1.94 | 0.224 | 0.374 | 0.227 | 15.8 | 35.3 | 36.9 | 37.6 | 47.8 | 31.6 | 70.6 | 73.8 | 75.2 | 95.6 | 3.4 | 2.55 | 3.2 | 5.8 | 0.064 | 22.2 | 18.7 | 0.57366 | 62.7 | 92.1 | 0.2037 | 0.0352 | 17.75 | 15.18 | 16.8 | 1.62 | 1.682 | 2.399 | 11.099 | 2.7037 | 29.11 | 5.4 | 9 | 2019-07-30
2019-07-31 | Click Here | 0:00 | 6.09 | 5.23 | 5.39 | 5.24 | 5.31 | 7.54 | 7.72 | 1.49 | 1.76 | 1.94 | 2.25 | 34 | 25 | 26 | 3 | 0 | 0 | 0.419 | 0.246 | 2.01 | 0.216 | 0.198 | 0.11 | 15.5 | 38.5 | 34.7 | 35.3 | 47.1 | 31 | 77 | 69.4 | 70.6 | 94.2 | 3.14 | 2.61 | 2.9 | 6.2 | 0.059 | 21.3 | 18.8 | 0.65993 | 63.5 | 92.4 | 0.1971 | 0.0341 | 18.962 | 16.178 | 17.134 | 0.956 | 1.695 | 2.392 | 12.091 | 2.8099 | 29.41 | 5.4 | 9 | 2019-07-31
2019-08-01 | Click Here | 0:00 | 6.11 | 5.17 | 5.24 | 5.26 | 5.34 | 7.11 | 7.02 | 1.4 | 1.67 | 2.07 | 2.19 | 32 | 24 | 6 | 0 | 0 | 0 | 0.296 | 0.241 | 0.291 | 0.101 | 0.21 | 0.318 | 15.8 | 47.5 | 46.2 | 43.4 | 49.9 | 31.6 | 95 | 92.4 | 86.8 | 99.8 | 3.05 | 2.47 | 3.1 | 5.7 | 0.0219 | 21.6 | 18.8 | 1.2013 | 61.6 | 89.9 | 0.2103 | 0.047 | 16.79 | 15.94 | 16.9 | 0.96 | 1.762 | 2.412 | 11.766 | 3.3913 | 28.64 | 5.4 | 9 | 2019-08-01
2019-08-02 | Click Here | 0:00 | 6.16 | 5.1 | 0 | 4.93 | 4.96 | 7.4 | 6.86 | 1.51 | 1.72 | 2 | 2.8 | 34 | 25 | 8 | 0 | 0 | 0 | 0.284 | 0.249 | 0.306 | 0.096 | 0.192 | 0.233 | 16.2 | 42.6 | 41.1 | 40.8 | 49.5 | 32.4 | 85.2 | 82.2 | 81.6 | 89 | 3.13 | 2.63 | 3 | 5.9 | 0.052 | 22.8 | 19.3 | 0.70953 | 61.4 | 90 | 0.2105 | 0.0467 | 15.708 | 14.701 | 15.683 | 0.982 | 1.72 | 2.411 | 10.57 | 2.8995 | 31.9 | 5.4 | 9 | 2019-08-02
2019-08-03 | Click Here | 0:00 | 6.09 | 5.16 | 5.2 | 5.22 | 5.27 | 7.26 | 7.51 | 1.54 | 1.77 | 2.04 | 2.16 | 36 | 28 | 7 | 0 | 0 | 0 | 0.289 | 0.241 | 0.298 | 0.043 | 0.17 | 0.194 | 16.4 | 41.9 | 41.2 | 40.5 | 49.7 | 32.8 | 83.8 | 82 | 81 | 99.4 | 3.11 | 2.59 | 3.1 | 6.1 | 0.059 | 22.8 | 19.4 | 0.66486 | 61.2 | 92.4 | 0.2121 | 0.0341 | 15.604 | 14.581 | 15.558 | 0.977 | 1.688 | 2.213 | 10.58 | 2.8649 | 30.33 | 5.4 | 9 | 2019-08-03
2019-08-04 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.70593 | 0 | 0 | 0 | 0 | 14.406 | 13.323 | 14.3 | 0.977 | 1.475 | 2.411 | 9.437 | 2.8859 | 30.01 | 5.4 | 9 | 2019-08-04
2019-08-05 | Click Here | 0:00 | 6.14 | 5.19 | 5.22 | 5.39 | 5.54 | 7.64 | 7.75 | 1.61 | 1.93 | 2.09 | 2.19 | 34 | 26 | 7 | 0 | 0 | 0 | 0.219 | 0.267 | 0.306 | 0.047 | 0.168 | 0.214 | 16.1 | 38.7 | 38.4 | 37.9 | 48.6 | 32.2 | 77.4 | 76.8 | 75.8 | 97.2 | 3.13 | 2.49 | 3.1 | 5.9 | 0.067 | 22.6 | 19.5 | 0.66567 | 61 | 92.9 | 0.2106 | 0.0319 | 14.404 | 13.376 | 14.354 | 0.978 | 1.48 | 2.417 | 9.088 | 2.8657 | 30.41 | 5.4 | 9 | 2019-08-05
2019-08-06 | Click Here | 0:00 | 6.04 | 5.14 | 5.22 | 5.29 | 5.39 | 7.49 | 7.62 | 1.56 | 1.87 | 2.11 | 2.17 | 36 | 29 | 9 | 0 | 0 | 0 | 0.231 | 0.264 | 0.321 | 0.044 | 0.164 | 0.221 | 15.8 | 37.2 | 36.9 | 36.4 | 47.7 | 31.6 | 74.4 | 73.8 | 72.8 | 95.4 | 3.27 | 2.61 | 3.1 | 6.1 | 0 | 22.7 | 19.6 | 0.93432 | 61.9 | 92.1 | 0.2074 | 0.0367 | 13.8 | 12.74 | 13.7 | 0.96 | 1.424 | 2.407 | 7.629 | 3.0643 | 30.53 | 5.4 | 9 | 2019-08-06
2019-08-07 | Click Here | 0:00 | 6.2 | 5.14 | 5.23 | 4.86 | 4.83 | 6.46 | 7.67 | 1.5 | 1.85 | 2.06 | 2.18 | 35 | 29 | 10 | 0 | 0 | 0 | 0.221 | 0.246 | 0.362 | 0.051 | 0.143 | 0.204 | 15.8 | 40 | 38.6 | 38.8 | 49.7 | 31.6 | 80 | 77.2 | 77.6 | 99.4 | 3.28 | 2.57 | 3 | 5.9 | 0.053 | 21 | 19.1 | 0.86783 | 61.7 | 92.4 | 0.2076 | 0.0364 | 15.14 | 14.116 | 15.094 | 0.978 | 1.443 | 2.405 | 10.268 | 2.8878 | 31.57 | 5.4 | 9 | 2019-08-07
2019-08-08 | Click Here | 0:00 | 6.07 | 5.26 | 5.23 | 5 | 5.01 | 6.81 | 7.35 | 1.55 | 1.73 | 1.84 | 2.11 | 34 | 0 | 11 | 0 | 0 | 0 | 0.216 | 0.232 | 0.316 | 0.073 | 0.143 | 0.117 | 16 | 39.8 | 39 | 38.7 | 50.6 | 32 | 79.6 | 78 | 77.4 | 100.2 | 3.22 | 2.59 | 3 | 6.2 | 0.048 | 21.5 | 19.2 | 0.60746 | 63.2 | 89.2 | 0.199 | 0.0496 | 17.18 | 16.22 | 17.19 | 0.97 | 1.57 | 2.392 | 12.258 | 2.7775 | 31.03 | 5.4 | 9.4 | 2019-08-08
2019-08-09 | Click Here | 0:00 | 6.2 | 5.23 | 5.19 | 5.13 | 5.18 | 7.77 | 7.06 | 1.57 | 1.68 | 2.09 | 2.08 | 33 | 26 | 10 | 0 | 0 | 0 | 0.414 | 0.038 | 0.463 | 0.155 | 0.254 | 0.163 | 16.3 | 39.7 | 38.4 | 38.3 | 49.9 | 32.6 | 79.4 | 76.8 | 76.6 | 99.8 | 3.26 | 2.44 | 3.1 | 5.9 | 0.122 | 22 | 19.5 | 0.45786 | 63.9 | 92.2 | 0.1943 | 0.035 | 14.99 | 13.98 | 14.96 | 0.98 | 1.538 | 2.393 | 8.22 | 2.5779 | 29.34 | 5.1 | 9.5 | 2019-08-09
2019-08-10 | Click Here | 0:00 | 6.16 | 5.29 | 5.25 | 5.17 | 5.23 | 7.45 | 7.66 | 1.64 | 1.79 | 2.18 | 2.21 | 33 | 26 | 9 | 0 | 0 | 0 | 0.434 | 0.102 | 0.419 | 0.101 | 0.214 | 0.123 | 16.4 | 39 | 38.1 | 38.5 | 48.7 | 32.8 | 78 | 76.2 | 77 | 97.4 | 3.21 | 2.36 | 3 | 6 | 0.114 | 21.9 | 19.4 |  | 63.8 | 92.3 | 0.1946 | 0.0347 | 13.2 | 13.04 | 13.04 | 0 | 0 | 0 | 0 |  | 29.11 | 5.1 | 9.2 | 2019-08-10
2019-08-11 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-08-11
2019-08-12 | Click Here | 0:00 | 6.22 | 5.31 | 5.24 | 4.99 | 5.02 | 6.63 | 7.46 | 1.56 | 1.72 | 2.15 | 5 | 32 | 27 | 11 | 1 | 0 | 0 | 0.416 | 0.104 | 0.538 | 0.097 | 0.197 | 0.163 | 16.2 | 39.8 | 37.6 | 38 | 49.6 | 32.4 | 79.6 | 75.2 | 76 | 99.2 | 3.17 | 2.42 | 3.1 | 6.2 | 0.091 | 21.3 | 19.5 | 0.021518 | 63.6 | 92.1 | 0.1948 | 0.0349 | 14.534 | 13.414 | 14.396 | 0.982 | 1.494 | 2.387 | 9.533 | 3.0315 | 30.24 | 5.1 | 9.2 | 2019-08-12
2019-08-13 | Click Here | 0:00 | 6.29 | 5.32 | 5.22 | 5.02 | 5.05 | 6.73 | 6.94 | 1.71 | 1.87 | 2.01 | 2.23 | 33 | 27 | 10 | 0 | 0 | 0 | 0.399 | 0.084 | 0.732 | 0.074 | 0.184 | 0.163 | 15.7 | 38 | 37.1 | 37.2 | 49.6 | 31.4 | 76 | 74.2 | 74.4 | 99.2 | 3.22 | 2.58 | 3 | 6.1 | 0.081 | 20.8 | 19.3 | 0.85751 | 63.8 | 89.1 | 0.1946 | 0.0502 | 15.03 | 13.98 | 14.98 | 1 | 1.494 | 2.387 | 11.099 | 3.0075 | 29.96 | 5 | 9.3 | 2019-08-13
2019-08-14 | Click Here | 0:00 | 5.96 | 5.08 | 5.14 | 4.93 | 5.05 | 7.78 | 7.15 | 1.68 | 1.83 | 2.18 | 2.22 | 31 | 25 | 8 | 0 | 0 | 0 | 0.463 | 0.095 | 0.484 | 0.127 | 0.275 | 0.172 | 15.5 | 38.1 | 36.7 | 36.4 | 48.5 | 31 | 76.2 | 73.4 | 72.8 | 97 | 3.21 | 2.51 | 3.1 | 5.9 | 0.114 | 20.3 | 18.9 | 0.86511 | 64.6 | 91.5 | 0.1896 | 0.0384 | 13.88 | 12.83 | 13.78 | 0.95 | 1.494 | 2.387 | 7.908 | 3.1051 | 30.04 | 4.8 | 9.6 | 2019-08-14
2019-08-15 | Click Here | 0:00 | 6.19 | 5.22 | 5.14 | 5.09 | 5.23 | 7.74 | 7.75 | 1.73 | 1.9 | 2.2 | 2.26 | 31 | 25 | 8 | 0 | 0 | 0 | 0.48 | 0.144 | 0.554 | 0.132 | 0.265 | 0.232 | 15.7 | 38.5 | 36.9 | 36.7 | 48.2 | 31.4 | 77 | 73.8 | 73.4 | 96.4 | 3.18 | 2.48 | 3 | 6 | 0.094 | 20.4 | 18.8 | 1.0022 | 64.4 | 91.6 | 0.1903 | 0.0381 | 14.41 | 13.42 | 14.37 | 0.95 | 1.494 | 2.387 | 7.908 | 3.2822 | 30.04 | 4.8 | 9.3 | 2019-08-15
2019-08-16 | Click Here | 0:00 | 6.07 | 5.29 | 5.24 | 5.44 | 5.52 | 7.47 | 7.56 | 1.8 | 2.04 | 2.2 | 2.29 | 33 | 24 | 8 | 0 | 0 | 0 | 0.324 | 0.128 | 0.432 | 0.074 | 0.172 | 0.189 | 15.6 | 38.6 | 37 | 36.3 | 47.7 | 31.2 | 77.2 | 74 | 72.6 | 95.4 | 3.19 | 2.47 | 3.2 | 6.2 | 0.094 | 20.7 | 19 | 0.75486 | 66.3 | 90.4 | 0.1782 | 0.0434 | 13.56 | 13.43 | 13.43 | 0 | 1.494 | 2.387 | 9.549 | 3.0249 | 30.64 | 4.8 | 9 | 2019-08-16
2019-08-17 | Click Here | 0:00 | 6.01 | 5.24 | 5.23 | 5.3 | 5.31 | 7.61 | 7.43 | 1.74 | 1.94 | 2.17 | 2.27 | 30 | 22 | 7 | 0 | 0 | 0 | 0.296 | 0.104 | 0.414 | 0.061 | 0.196 | 0.237 | 15.4 | 38.4 | 36.4 | 35.8 | 48.1 | 30.8 | 76.8 | 72.8 | 71.6 | 96.2 | 3.34 | 2.49 | 3 | 6.7 | 0.104 | 20.7 | 19.1 | 1.0095 | 66 | 91.9 | 0.1804 | 0.0374 | 13.32 | 12.21 | 13.18 | 0.97 | 0 | 0 | 0 | 3.2795 | 29.88 | 4.8 | 9 | 2019-08-17
2019-08-18 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-08-18
2019-08-19 | Click Here | 0:00 | 6.15 | 5.26 | 5.23 | 5.11 | 5.14 | 7.45 | 7.45 | 1.76 | 1.92 | 2.17 | 2.11 | 27 | 21 | 6 | 0 | 0 | 0 | 0.432 | 0.094 | 0.569 | 0.125 | 0.298 | 0.234 | 15.6 | 38 | 37.1 | 36.9 | 48.2 | 31.2 | 76 | 74.2 | 73.8 | 96.4 | 3.26 | 2.55 | 3.2 | 5.9 | 0.091 | 20.4 | 19.1 | 0.97255 | 66.2 | 90.9 | 0.1762 | 0.0411 | 14.07 | 13.02 | 14 | 0.98 | 1.494 | 2.387 | 7.908 | 3.1525 | 29.34 | 4.8 | 9 | 2019-08-19
2019-08-20 | Click Here | 0:00 | 6.27 | 5.22 | 5.24 | 5.05 | 5.13 | 7.38 | 7.39 | 1.73 | 1.95 | 2.2 | 2.06 | 28 | 22 | 7 | 0 | 0 | 0 | 0.437 | 0.11 | 0.402 | 0.13 | 0.317 | 0.312 | 16 | 39.4 | 38.1 | 37.3 | 47.6 | 32 | 78.8 | 76.2 | 74.6 | 95.2 | 3.07 | 2.47 | 3.1 | 6 | 0.059 | 21.4 | 19.6 | 0.95016 | 66.3 | 92.2 | 0.178 | 0.035 | 14.42 | 13.41 | 14.39 | 0.98 | 1.494 | 2.387 | 7.908 | 3.2102 | 28.87 | 4.8 | 9 | 2019-08-20
2019-08-21 | Click Here | 0:00 | 6.19 | 5.18 | 5.25 | 5.1 | 5.17 | 7.38 | 7.5 | 1.7 | 1.89 | 2.2 | 2.29 | 31 | 24 | 8 | 0 | 0 | 0 | 0.392 | 0.134 | 0.417 | 0.112 | 0.209 | 0.234 | 15.9 | 40 | 38.6 | 37.5 | 48.1 | 31.8 | 80 | 77.2 | 75 | 96.2 | 3.16 | 2.54 | 3.3 | 6.1 | 0.061 | 21.2 | 19.5 | 1.0369 | 66.2 | 92.6 | 0.1784 | 0.0336 | 14.869 | 13.817 | 14.785 | 0.968 | 1.494 | 2.387 | 9.936 | 3.2769 | 29.16 | 4.8 | 9 | 2019-08-21
2019-08-22 | Click Here | 0:00 | 6.09 | 5.19 | 5.25 | 5.19 | 5.26 | 7.42 | 7.44 | 1.74 | 1.94 | 2.2 | 2.27 | 29 | 21 | 10 | 1 | 0 | 0 | 0.296 | 0.104 | 0.396 | 0.061 | 0.204 | 0.296 | 16.1 | 39.6 | 38.2 | 37.7 | 47.9 | 32.2 | 79.2 | 76.4 | 75.4 | 95.8 | 3.17 | 2.59 | 3.1 | 6.2 | 0.067 | 21.2 | 19.6 | 0.73487 | 66.7 | 92.2 | 0.1741 | 0.0354 | 16.05 | 14.12 | 16.07 | 1.95 | 1.494 | 2.387 | 7.908 | 3.5449 | 29.68 | 4.8 | 9 | 2019-08-22
2019-08-23 | Click Here | 0:00 | 6.12 | 5.29 | 5.28 | 4.98 | 5.02 | 6.51 | 7.51 | 1.75 | 2.03 | 2.09 | 2.82 | 32 | 26 | 12 | 1 | 0 | 0 | 0.374 | 0.097 | 0.492 | 0.096 | 0.194 | 0.228 | 16 | 38.3 | 37.1 | 37 | 49.1 | 32 | 76.6 | 74.2 | 74 | 98.2 | 3.2 | 2.68 | 3 | 5.9 | 0.073 | 20.5 | 19.3 | 0.90006 | 66.4 | 92.8 | 0.1782 | 0.0332 | 14.424 | 13.328 | 14.308 | 0.98 | 1.494 | 2.387 | 9.447 | 3.1901 | 30.97 | 4.8 | 9 | 2019-08-23
2019-08-24 | Click Here | 0:00 | 6.1 | 5.04 | 5.17 | 4.89 | 4.97 | 6.46 | 7.14 | 1.82 | 1.91 | 1.96 | 1.97 | 31 | 26 | 11 | 1 | 0 | 0 | 0.261 | 0.095 | 0.671 | 0.096 | 0.198 | 0.256 | 15.9 | 38.5 | 37.4 | 36.4 | 48.3 | 31.8 | 79 | 74.8 | 72.8 | 96.6 | 3.18 | 2.66 | 3 | 5.8 | 0.086 | 20.3 | 19.2 | 1.3235 | 65.2 | 88.9 | 0.1856 | 0.0511 | 13.1 | 12.09 | 13.02 | 0.93 | 0 | 0 | 0 | 3.3635 | 30.35 | 4.6 | 9.4 | 2019-08-24
2019-08-25 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 1.4716 | 0 | 0 | 0 | 0 | 14.35 | 13.198 | 14.175 | 0.977 | 1.494 | 2.387 | 9.317 | 3.3216 | 0 | 4.1 | 9.7 | 2019-08-25
2019-08-26 | Click Here | 0:00 | 6.07 | 5.34 | 5.22 | 5.17 | 5.24 | 5.29 | 5.24 | 1.8 | 2.04 | 1.98 | 2.02 | 30 | 26 | 14 | 2 | 0 | 0 | 0.314 | 0.124 | 0.692 | 0.089 | 0.286 | 0.124 | 16.1 | 38.8 | 37 | 36.7 | 48.8 | 32.2 | 77.6 | 74 | 73.4 | 97.6 | 3.02 | 2.59 | 3.4 | 5.9 | 0.104 | 20.2 | 19.1 | 2.5339 | 65 | 89.9 | 0.1862 | 0.0448 | 16.42 | 11.34 | 12.3 | 0.96 | 1.494 | 2.387 | 7.459 | 4.4139 | 29.49 | 4.1 | 9.7 | 2019-08-26
2019-08-27 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-08-27
2019-08-28 | Click Here | 0:00 | 6.09 | 4.96 | 5.17 | 4.87 | 4.89 | 6.63 | 7.69 | 1.87 | 2.1 | 1.96 | 1.89 | 31 | 26 | 15 | 1 | 0 | 0 | 0.327 | 0.146 | 0.701 | 0.101 | 0.318 | 0.473 | 15.6 | 38.4 | 37.1 | 36.8 | 47.7 | 31.2 | 76.8 | 74.2 | 73.2 | 95.4 | 3.09 | 2.67 | 3.2 | 5.7 | 0.093 | 19.6 | 18.6 | 1.0139 | 65.2 | 90.1 | 0.186 | 0.0446 | 15.21 | 14.08 | 15.08 | 1 | 1.494 | 2.387 | 7.908 | 2.8439 | 30.41 | 4.1 | 9.7 | 2019-08-28
2019-08-29 | Click Here | 0:00 | 6.03 | 4.87 | 5.18 | 4.86 | 4.88 | 6.59 | 6.84 | 1.92 | 2.05 | 1.9 | 1.8 | 33 | 28 | 16 | 3 | 0 | 0 | 0.299 | 0.236 | 0.816 | 0.098 | 0.244 | 0.327 | 15.4 | 36.1 | 35.1 | 35.5 | 47.3 | 30.8 | 72.2 | 70.2 | 71 | 94.6 | 3.17 | 2.56 | 3.1 | 5.8 | 0.097 | 18.6 | 18.4 | 1.4102 | 66.1 | 90.4 | 0.1794 | 0.0436 | 13.87 | 12.74 | 13.7 | 0.96 | 1.494 | 2.387 | 8.859 | 3.3002 | 29.62 | 4.1 | 9.9 | 2019-08-29
2019-08-30 | Click Here | 0:00 | 5.79 | 4.96 | 5.01 | 4.95 | 5.02 | 7.3 | 6.98 | 1.87 | 2.05 | 2.2 | 1.86 | 35 | 28 | 13 | 0 | 0 | 0 | 0.453 | 0.228 | 0.973 | 0.134 | 0.467 | 0.389 | 15.3 | 36.2 | 34.5 | 35.2 | 46.9 | 30.6 | 72.4 | 69 | 70.4 | 93.8 | 3.21 | 2.37 | 3.2 | 6 | 0.041 | 18.3 | 18 | 1.4886 | 66.5 | 92 | 0.1767 | 0.0361 | 13.33 | 12.24 | 13.18 | 0.94 | 1.494 | 2.387 | 7.908 | 3.5986 | 28.87 | 4.1 | 10.3 | 2019-08-30
2019-08-31 | Click Here | 0:00 | 5.99 | 5.21 | 5.01 | 5.07 | 5.11 | 7.44 | 7.24 | 1.73 | 1.94 | 2.2 | 2.19 | 34 | 27 | 12 | 0 | 0 | 0 | 0.482 | 0.226 | 0.765 | 0.128 | 0.368 | 0.303 | 15.3 | 36.1 | 34.8 | 34.7 | 45 | 30.6 | 72.2 | 69.6 | 69.4 | 90 | 3.27 | 2.47 | 3 | 5.7 | 0.046 | 18.4 | 17.9 |  | 66.4 | 92.1 | 0.1769 | 0.0358 | 13.88 | 12.76 | 13.7 | 0.94 | 0 | 0 | 0 |  | 28.64 | 4.1 | 10.3 | 2019-08-31
2019-09-01 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-09-01
2019-09-02 | Click Here | 0:00 | 6.08 | 4.93 | 5.22 | 4.77 | 4.78 | 6.71 | 7.36 | 1.74 | 2.02 | 2.1 | 2.19 | 34 | 26 | 14 | 1 | 0 | 0 | 0.414 | 0.184 | 0.813 | 0.116 | 0.314 | 0.538 | 15.1 | 36.6 | 35.1 | 35.7 | 46.6 | 30.2 | 73.2 | 70.2 | 71.4 | 93.2 | 3.24 | 2.51 | 3.1 | 5.8 | 0.042 | 18.1 | 18 | 1.5402 | 66.7 | 92 | 0.1746 | 0.0359 | 14.634 | 8.924 | 10.88 | 1.956 | 1.494 | 2.387 | 7.908 | 3.6802 | 29.78 | 4.1 | 10.3 | 2019-09-02
2019-09-03 | Click Here | 0:00 | 6.01 | 5.04 | 5.03 | 5.08 | 5.1 | 7.09 | 7.15 | 1.62 | 1.96 | 2.01 | 1.96 | 35 | 30 | 16 | 1 | 0 | 0 | 0.368 | 0.224 | 0.798 | 0.109 | 0.268 | 0.341 | 14.8 | 35.9 | 34.2 | 35.1 | 46.2 | 29.6 | 71.8 | 68.4 | 70.2 | 92.4 | 3.15 | 2.59 | 3 | 6.1 | 0.054 | 18.2 | 18 | 0.44317 | 66.4 | 92.2 | 0.1771 | 0.0347 | 14.42 | 13.33 | 14.32 | 0.99 | 1.494 | 2.387 | 9.449 | 2.4032 | 29.89 | 4.1 | 10.6 | 2019-09-03
2019-09-04 | Click Here | 0:00 | 5.72 | 4.95 | 5.02 | 5.02 | 5.06 | 7.49 | 6.99 | 1.58 | 1.8 | 2.2 | 2.02 | 36 | 28 | 17 | 1 | 0 | 0 | 0.625 | 0.338 | 1.71 | 0.144 | 0.503 | 0.456 | 15.1 | 36.8 | 32.9 | 32.4 | 47.1 | 30.2 | 73.6 | 65.8 | 64.8 | 94.2 | 3.18 | 2.34 | 3.2 | 6.2 | 0.067 | 18 | 17.4 | 1.4953 | 66.9 | 91.2 | 0.1745 | 0.0397 | 15.07 | 12.67 | 13.66 | 0.99 | 1.494 | 2.387 | 7.908 | 3.5553 | 29.57 | 4.1 | 10.6 | 2019-09-04
2019-09-05 | Click Here | 0:00 | 6.06 | 5.15 | 5 | 5.09 | 5.09 | 7.52 | 7.54 | 1.61 | 1.86 | 2.12 | 2.18 | 22 | 16 | 4 | 0 | 0 | 0 | 0.548 | 0.313 | 0.45 | 0.129 | 0.375 | 0.407 | 15.5 | 36 | 33.9 | 34.9 | 46.4 | 31 | 72 | 67.8 | 69.8 | 92.8 | 3.35 | 2.39 | 3 | 5.9 | 0.065 | 18.8 | 17.6 | 0.988 | 64.3 | 87.4 | 0.1915 | 0.0581 | 15.78 | 13.23 | 14.17 | 0.94 | 1.494 | 2.387 | 7.908 | 3.178 | 29.34 | 4.1 | 10.4 | 2019-09-05
2019-09-06 | Click Here | 0:00 | 6.02 | 5.08 | 4.97 | 5.14 | 5.16 | 7.54 | 7.61 | 1.57 | 1.88 | 2.17 | 2.23 | 36 | 29 | 5 | 0 | 0 | 0 | 0.467 | 0.303 | 0.342 | 0.069 | 0.204 | 0.401 | 15.1 | 36.8 | 35 | 34.7 | 45.9 | 30.2 | 73.6 | 70 | 69.4 | 91.8 | 3.14 | 2.59 | 2.9 | 5.6 | 0.061 | 17.9 | 17.8 | 0.94514 | 67.4 | 91.9 | 0.1709 | 0.0405 | 13.852 | 12.678 | 13.646 | 0.966 | 1.494 | 2.389 | 8.795 | 3.1251 | 29.34 | 4.1 | 10.4 | 2019-09-06
2019-09-07 | Click Here | 0:00 | 6.09 | 5.14 | 5.08 | 5.19 | 5.22 | 7.49 | 7.62 | 1.65 | 1.99 | 2.09 | 2.18 | 30 | 22 | 4 | 0 | 0 | 0 | 0.317 | 0.267 | 0.319 | 0.079 | 0.298 | 0.315 | 15.6 | 37.1 | 35.4 | 35.2 | 46.5 | 31.2 | 74.2 | 70.8 | 70.4 | 93 | 3.43 | 2.69 | 3.2 | 6.1 | 0.047 | 17.7 | 17.6 | 0.93015 | 67.5 | 92.6 | 0.1701 | 0.0371 | 13.07 | 11.91 | 12.88 | 0.97 | 0 | 0 | 0 | 3.1101 | 31.34 | 4.1 | 10.4 | 2019-09-07
2019-09-08 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-09-08
2019-09-09 | Click Here | 0:00 | 5.95 | 5.05 | 5.11 | 5.05 | 5.09 | 7.27 | 7.19 | 1.74 | 1.87 | 2.16 | 2.05 | 92 | 25 | 12 | 2 | 0 | 0 | 4.7 | 0.342 | 0.761 | 0.128 | 0.456 | 0.431 | 12.8 | 34.2 | 32.1 | 32.5 | 42.5 | 25.6 | 68.4 | 64.2 | 65 | 85 | 3.15 | 1.96 | 2.8 | 4.2 | 0.015 | 14.8 | 16.2 | 0.87545 | 67.4 | 91 | 0.1704 | 0.0406 | 13.76 | 12.71 | 13.7 | 0.99 | 1.441 | 2.154 | 9.875 | 2.8354 | 29.34 | 4.1 | 10.4 | 2019-09-09
2019-09-10 | Click Here | 0:00 | 5.96 | 5.12 | 5.08 | 5.08 | 5.09 | 7.26 | 7.38 | 1.71 | 1.86 | 2.13 | 1.9 | 65 | 22 | 12 | 0 | 0 | 0 | 2.74 | 0.257 | 0.661 | 0.129 | 0.508 | 0.496 | 12.7 | 34.1 | 32 | 32.1 | 43.4 | 25.4 | 68.2 | 64 | 64.2 | 86.8 | 3.35 | 2.09 | 3 | 5.2 | 0.018 | 14.2 | 15.7 | 1.0753 | 66.8 | 89.9 | 0.175 | 0.0462 | 14.17 | 13.05 | 14.05 | 1 | 1.396 | 2.152 | 9.813 | 3.1453 | 30.04 | 4.1 | 10.4 | 2019-09-10
2019-09-11 | Click Here | 0:00 | 5.89 | 5.14 | 5.08 | 5.12 | 5.15 | 7.41 | 7.61 | 1.69 | 1.88 | 2.12 | 2.17 | 42 | 35 | 15 | 0 | 0 | 0 | 1.68 | 0.227 | 0.596 | 0.121 | 0.31 | 0.436 | 13.4 | 34.4 | 31.7 | 32 | 41.8 | 26.8 | 68.8 | 63.4 | 64 | 83.6 | 3.25 | 2.24 | 3.1 | 5.5 | 0.024 | 14.2 | 15.7 | 0.91436 | 67 | 90.4 | 0.1729 | 0.044 | 13.33 | 12.152 | 13.131 | 0.979 | 1.385 | 2.15 | 9.729 | 3.0744 | 29.88 | 4.1 | 10.4 | 2019-09-11
2019-09-12 | Click Here | 0:00 | 6.04 | 5.12 | 5.05 | 5.16 | 5.18 | 7.47 | 7.61 | 1.66 | 1.98 | 2.2 | 2.15 | 60 | 44 | 13 | 2 | 1 | 0 | 2.55 | 0.276 | 0.745 | 0.12 | 0.311 | 0.42 | 12.9 | 36.1 | 32.1 | 32.5 | 44.5 | 25.8 | 72.2 | 64.2 | 65 | 89 | 3.16 | 2.41 | 3.1 | 5.7 | 0.054 | 15 | 15.5 | 1.0761 | 67.6 | 89.6 | 0.1696 | 0.0476 | 14.31 | 12.26 | 14.22 | 1.96 | 1.4 | 2.148 | 9.613 | 3.2661 | 30.14 | 4.1 | 10.4 | 2019-09-12
2019-09-13 | Click Here | 0:00 | 6.06 | 4.81 | 5.05 | 4.79 | 4.84 | 6.63 | 7.25 | 1.74 | 2.01 | 2.23 | 2.29 | 58 | 47 | 14 | 1 | 0 | 0 | 1.73 | 0.256 | 0.616 | 0.103 | 0.321 | 0.527 | 12.6 | 37.3 | 34.1 | 33.4 | 43.4 | 25.2 | 74.6 | 68.2 | 66.8 | 83.8 | 3.2 | 2.59 | 3 | 5.8 | 0.047 | 14.1 | 15.1 | 1.4114 | 67.2 | 90 | 0.1727 | 0.0472 | 13.146 | 11.094 | 13.04 | 1.946 | 1.319 | 2.151 | 8.735 | 3.3414 | 32.98 | 4.1 | 10.4 | 2019-09-13
2019-09-14 | Click Here | 0:00 | 6.16 | 4.85 | 5.13 | 4.87 | 4.89 | 6.28 | 7.35 | 1.76 | 1.94 | 1.94 | 1.7 | 57 | 49 | 16 | 1 | 0 | 0 | 1.24 | 0.216 | 0.673 | 0.096 | 0.344 | 0.691 | 12.8 | 36 | 33.5 | 33.2 | 44.3 | 25.6 | 72 | 67 | 66.4 | 88.6 | 3.14 | 2.63 | 3.1 | 6 | 0.051 | 14.1 | 15 | 1.3784 | 67.5 | 91.2 | 0.1724 | 0.0404 | 12.16 | 11.05 | 12.01 | 0.96 | 0 | 0 | 0 | 3.1184 | 31.66 | 4.1 | 10.7 | 2019-09-14
2019-09-15 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 1.2196 | 0 | 0 | 0 | 0 | 13.204 | 12.038 | 13.014 | 0.976 | 0 | 0 | 0 | 3.0096 | 0 | 4.3 | 11 | 2019-09-15
2019-09-16 | Click Here | 0:00 | 5.99 | 5.21 | 4.94 | 5.18 | 5.19 | 6.49 | 6.72 | 1.7 | 2 | 2.11 | 1.63 | 56 | 41 | 11 | 2 | 0 | 0 | 0.512 | 0.147 | 0.541 | 0.113 | 0.3 | 0.501 | 13.3 | 34.8 | 33.7 | 32.9 | 43.1 | 26.6 | 69.6 | 67.4 | 65.8 | 86.2 | 3.15 | 2.61 | 3.1 | 5.8 | 0.101 | 15.1 | 15.5 | 1.34 | 66.8 | 89.4 | 0.175 | 0.0484 | 13.803 | 12.744 | 13.718 | 0.974 | 1.292 | 2.15 | 9.166 | 2.97 | 30.53 | 4.3 | 11 | 2019-09-16
2019-09-17 | Click Here | 0:00 | 5.95 | 5.16 | 5.22 | 5.26 | 5.27 | 6.81 | 6.55 | 1.75 | 1.99 | 2.17 | 1.65 | 61 | 40 | 15 | 1 | 0 | 0 | 0.467 | 0.174 | 0.499 | 0.112 | 0.271 | 0.526 | 14.1 | 35.1 | 33.6 | 33.1 | 44.4 | 28.2 | 70.2 | 67.2 | 66.2 | 88.8 | 3.14 | 2.49 | 2.8 | 5.7 | 0.089 | 15 | 15.4 | 0.92583 | 66.5 | 90.9 | 0.1767 | 0.0438 | 12.02 | 11.89 | 11.89 | 0 | 1.375 | 2.149 | 7.235 | 2.5258 | 29.92 | 4.3 | 11 | 2019-09-17
2019-09-18 | Click Here | 0:00 | 6.1 | 4.92 | 5.2 | 4.87 | 4.9 | 6.42 | 6.28 | 1.83 | 2.05 | 2.16 | 1.58 | 58 | 46 | 13 | 0 | 0 | 0 | 0.438 | 0.217 | 0.501 | 0.104 | 0.344 | 0.736 | 12.9 | 34 | 32.9 | 31.9 | 42 | 25.8 | 68 | 65.8 | 63.8 | 84 | 3.22 | 2.51 | 3 | 5.4 | 0.072 | 14 | 14.6 | 1.1832 | 68.2 | 87.6 | 0.1661 | 0.0573 | 14.439 | 12.803 | 14.274 | 1.471 | 1.371 | 2.149 | 9.283 | 3.1932 | 29.9 | 4.3 | 11 | 2019-09-18
2019-09-19 | Click Here | 0:00 | 6.19 | 5.08 | 5.06 | 4.98 | 5.01 | 6.57 | 6.97 | 1.98 | 2.15 | 2.2 | 2.24 | 41 | 33 | 14 | 1 | 0 | 0 | 1.08 | 0.236 | 0.982 | 0.091 | 0.307 | 0.516 | 12.6 | 31.8 | 30.5 | 31 | 43.7 | 25.2 | 63.6 | 61 | 62 | 87.4 | 3.14 | 2.6 | 3.2 | 5.7 | 0.063 | 12.7 | 13.9 | 0.71285 | 65.6 | 95.3 | 0.1827 | 0.0206 | 14.03 | 13.89 | 13.89 | 0 | 1.405 | 2.14 | 10.345 | 2.8829 | 31.08 | 4.5 | 11.8 | 2019-09-19
2019-09-20 | Click Here | 0:00 | 6.06 | 5.12 | 5.05 | 5.13 | 5.09 | 7.72 | 7.33 | 1.8 | 1.97 | 2.09 | 2.05 | 34 | 27 | 14 | 0 | 0 | 0 | 0.829 | 0.101 | 1.02 | 0.132 | 0.398 | 0.292 | 12.8 | 33 | 31.3 | 31.9 | 45.1 | 25.6 | 66 | 62.6 | 63.8 | 90.2 | 3.2 | 2.49 | 3.1 | 5.8 | 0.13 | 12.9 | 14.1 | 0.68432 | 68.1 | 91 | 0.1666 | 0.0406 | 13.76 | 12.63 | 13.6 | 0.97 | 1.367 | 2.146 | 9.898 | 2.7743 | 30.51 | 4.5 | 12 | 2019-09-20
2019-09-21 | Click Here | 0:00 | 6.16 | 5.23 | 5.08 | 5.15 | 5.11 | 7.65 | 7.39 | 1.75 | 1.98 | 2.2 | 1.79 | 32 | 26 | 12 | 0 | 0 | 0 | 0.932 | 0.28 | 0.744 | 0.133 | 0.363 | 0.31 | 13.6 | 35.8 | 31.7 | 32.2 | 44.5 | 28.2 | 71.6 | 63.4 | 64.4 | 89 | 3.05 | 2.38 | 3.2 | 5.9 | 0.113 | 15.4 | 14.3 |  | 68 | 91.2 | 0.1671 | 0.0409 | 13.21 | 12.12 | 13.1 | 0.98 | 0 | 0 | 0 |  | 30.28 | 4.5 | 11.7 | 2019-09-21
2019-09-22 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-09-22
2019-09-23 | Click Here | 0:00 | 6.11 | 5.14 | 5.19 | 5.05 | 5.03 | 6.67 | 7.6 | 1.76 | 2.01 | 2.14 | 1.58 | 34 | 28 | 14 | 1 | 0 | 0 | 0.817 | 0.226 | 0.704 | 0.101 | 0.331 | 0.326 | 13.5 | 36.2 | 31.8 | 32 | 42.9 | 27 | 72.4 | 63.6 | 64 | 85.8 | 3.08 | 2.41 | 3.1 | 5.6 | 0.083 | 15.3 | 14.2 | 1.2812 | 63.5 | 89.7 | 0.197 | 0.0472 | 14.324 | 12.218 | 14.172 | 1.954 | 1.356 | 2.153 | 8.709 | 3.2012 | 30.52 | 4.5 | 11.5 | 2019-09-23
2019-09-24 | Click Here | 0:00 | 6.04 | 5.02 | 5.19 | 4.96 | 5.01 | 6.83 | 6.96 | 1.91 | 2.1 | 2.14 | 2.12 | 33 | 26 | 13 | 0 | 0 | 0 | 0.762 | 0.173 | 0.691 | 0.097 | 0.314 | 0.336 | 13.9 | 37.1 | 32.5 | 31.8 | 45.4 | 27.8 | 74.2 | 65 | 63.6 | 90.8 | 2.97 | 2.52 | 3 | 5.9 | 0.066 | 16.1 | 14.5 | 0.81301 | 67 | 89.5 | 0.1739 | 0.0481 | 13.73 | 13.56 | 13.56 | 0 | 1.377 | 2.201 | 9.982 | 2.953 | 30.58 | 4.5 | 11.8 | 2019-09-24
2019-09-25 | Click Here | 0:00 | 6.06 | 5.14 | 5.11 | 5.09 | 5.1 | 7.88 | 6.91 | 2.2 | 2.2 | 2.15 | 2.63 | 33 | 27 | 12 | 0 | 0 | 0 | 0.767 | 0.204 | 0.656 | 0.094 | 0.306 | 0.324 | 13.7 | 36.5 | 33.1 | 32.4 | 45.6 | 27.4 | 73 | 66.2 | 64.8 | 91.2 | 3.04 | 2.44 | 3.1 | 5.8 | 0.062 | 14.8 | 14.4 | 0.76425 | 68.1 | 90.9 | 0.1673 | 0.0416 | 12.89 | 11.76 | 12.69 | 0.93 | 1.483 | 2.198 | 9.127 | 2.8942 | 30.51 | 4.5 | 11.8 | 2019-09-25
2019-09-26 | Click Here | 0:00 | 6 | 5.18 | 5.11 | 5.13 | 5.18 | 7.35 | 6.83 | 1.85 | 2.01 | 2.2 | 2.1 | 33 | 26 | 11 | 0 | 0 | 0 | 0.735 | 0.316 | 0.662 | 0.137 | 0.55 | 0.48 | 13.4 | 32.3 | 31.1 | 31.2 | 41.6 | 26.8 | 64.6 | 62.2 | 62.4 | 83.2 | 3.09 | 2.51 | 3 | 5.7 | 0.027 | 14.6 | 13.9 | 0.95606 | 71.5 | 93.5 | 0.1452 | 0.0288 | 14.18 | 13.06 | 14.06 | 1 | 1.679 | 2.094 | 9.267 | 3.0661 | 30.28 | 4.5 | 11 | 2019-09-26
2019-09-27 | Click Here | 0:00 | 6.07 | 5.24 | 5.18 | 5.17 | 5.2 | 7.35 | 8.07 | 2.17 | 2.2 | 2.2 | 2.05 | 37 | 29 | 14 | 0 | 0 | 0 | 0.361 | 0.297 | 0.617 | 0.074 | 0.198 | 0.441 | 13.6 | 33.9 | 31.5 | 32.3 | 43.4 | 27.2 | 67.8 | 63 | 64.6 | 86.8 | 3.09 | 2.51 | 3.2 | 6.9 | 0.067 | 14.7 | 13.8 | -0.02974 | 71 | 90 | 0.1487 | 0.0458 | 13.681 | 12.524 | 13.504 | 0.98 | 1.712 | 2.023 | 8.356 | 2.0703 | 30.64 | 4.5 | 11 | 2019-09-27
2019-09-28 | Click Here | 0:00 | 6 | 5.21 | 5.16 | 5.24 | 5.29 | 7.41 | 7.5 | 1.75 | 1.99 | 2.09 | 2.05 | 35 | 27 | 12 | 0 | 0 | 0 | 0.304 | 0.397 | 0.671 | 0.092 | 0.267 | 0.497 | 14.1 | 34.2 | 30.9 | 31.3 | 44.7 | 28.2 | 68.4 | 61.8 | 62.6 | 89.4 | 3.11 | 2.47 | 3.2 | 5.9 | 0.072 | 14.6 | 13.6 | 1.0494 | 69.9 | 90.9 | 0.149 | 0.041 | 12.97 | 11.89 | 12.82 | 0.93 | 0 | 0 | 0 | 3.1994 | 30.38 | 4.5 | 11 | 2019-09-28
2019-09-29 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-09-29
2019-09-30 | Click Here | 0:00 | 5.93 | 5.06 | 5.15 | 5.11 | 5.1 | 7.22 | 7.14 | 1.9 | 2.03 | 2.2 | 2.15 | 34 | 26 | 11 | 0 | 0 | 0 | 0.753 | 0.259 | 0.998 | 0.141 | 0.432 | 0.554 | 13.7 | 34.7 | 31 | 31.9 | 42.3 | 27.4 | 69.4 | 62 | 63.8 | 84.6 | 3.13 | 2.38 | 3.1 | 5.8 | 0.023 | 14 | 13.8 | 0.73802 | 68.8 | 100 | 0.1619 | 0 | 14.05 | 12.88 | 13.85 | 0.97 | 1.682 | 2.103 | 9.279 | 2.798 | 30.04 | 4.5 | 11 | 2019-09-30
2019-10-01 | Click Here | 0:00 | 6.14 | 5.24 | 5.04 | 5.19 | 5.22 | 7.55 | 7.14 | 1.82 | 2.07 | 2.2 | 1.87 | 34 | 27 | 16 | 0 | 0 | 0 | 0.72 | 0.263 | 0.921 | 0.152 | 0.451 | 0.548 | 13.8 | 36 | 30.6 | 31.1 | 42.4 | 27.6 | 72 | 61.2 | 62.2 | 84.8 | 3.13 | 2.47 | 3 | 5.9 | 0.04 | 12.9 | 13.1 | 0.94274 | 67.2 | 87.3 | 0.1724 | 0.0587 | 13.5 | 12.3 | 13.29 | 0.99 | 1.676 | 3.014 | 8.7 | 3.0927 | 30.51 | 4.5 | 11 | 2019-10-01
2019-10-02 | Click Here | 0:00 | 6.12 | 5.29 | 5.26 | 5.32 | 5.39 | 7.84 | 8.29 | 1.87 | 2.05 | 2.2 | 2.24 | 37 | 30 | 19 | 0 | 0 | 0 | 0.694 | 0.237 | 0.827 | 0.096 | 0.211 | 0.235 | 14.2 | 35.8 | 31.4 | 32 | 42.6 | 28.4 | 71.6 | 62.8 | 64 | 87.2 | 3.09 | 2.54 | 3.2 | 6.4 | 0.052 | 12.8 | 13 | 0.66114 | 67.7 | 91.4 | 0.1699 | 0.0426 | 14.321 | 13.17 | 14.142 | 0.972 | 1.644 | 2.373 | 9.182 | 3.0511 | 30.3 | 4.8 | 11 | 2019-10-02
2019-10-03 | Click Here | 0:00 | 6.04 | 5.19 | 5.25 | 5.21 | 5.28 | 7.59 | 7.71 | 1.77 | 1.99 | 2.2 | 2.25 | 37 | 31 | 17 | 0 | 0 | 0 | 0.547 | 0.367 | 0.84 | 0.096 | 0.304 | 0.387 | 13.8 | 35.7 | 30.1 | 30.4 | 42.3 | 27.6 | 71.4 | 60.2 | 60.8 | 84.6 | 3.05 | 2.49 | 3.1 | 5.7 | 0.074 | 12.3 | 12.7 | 0.67205 | 67.3 | 91.7 | 0.1719 | 0.0376 | 14.18 | 12.93 | 13.94 | 1.01 | 1.612 | 2.356 | 8.775 | 2.942 | 30.39 | 4.8 | 10.8 | 2019-10-03
2019-10-04 | Click Here | 0:00 | 5.92 | 5.14 | 5.27 | 5.08 | 5.13 | 6.89 | 7.76 | 1.84 | 2.03 | 2.2 | 2.18 | 39 | 33 | 16 | 1 | 0 | 0 | 0.542 | 0.347 | 0.791 | 0.103 | 0.3 | 0.396 | 12.8 | 35.6 | 29.3 | 29.6 | 44 | 25.6 | 71.2 | 58.6 | 59.2 | 88 | 3.15 | 2.51 | 3 | 5.8 | 0.082 | 11.7 | 12.1 | 0.8058 | 67.5 | 91.9 | 0.1717 | 0.0374 | 13.353 | 12.183 | 13.158 | 0.975 | 1.61 | 2.317 | 8.183 | 3.0058 | 29.84 | 4.8 | 10.8 | 2019-10-04
2019-10-05 | Click Here | 0:00 | 5.96 | 5.1 | 5.16 | 5.07 | 5.09 | 7.04 | 7.22 | 1.81 | 2 | 2.11 | 1.93 | 38 | 32 | 15 | 0 | 0 | 0 | 0.461 | 0.297 | 0.762 | 0.113 | 0.274 | 0.308 | 13.3 | 35.9 | 29.3 | 29.2 | 43.4 | 26.6 | 71.8 | 58.6 | 58.4 | 86.8 | 3.11 | 2.44 | 3.1 | 5.9 | 0.073 | 11.5 | 11.7 | 0.83317 | 67.3 | 91.7 | 0.1719 | 0.0376 | 13.15 | 12 | 12.9 | 0.9 | 0 | 0 | 0 | 2.9132 | 30.15 | 4.8 | 10.8 | 2019-10-05
2019-10-06 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.80497 | 0 | 0 | 0 | 0 | 14.053 | 12.856 | 12.386 | 0.98 | 1.471 | 2.338 | 8.779 | 2.935 | 0 | 4.8 | 10.9 | 2019-10-06
2019-10-07 | Click Here | 0:00 | 6.04 | 5.1 | 5.15 | 5.12 | 5.14 | 7.2 | 7.59 | 1.79 | 2.01 | 2.17 | 2.2 | 35 | 29 | 17 | 0 | 0 | 0 | 0.396 | 0.225 | 0.79 | 0.104 | 0.196 | 0.221 | 13.1 | 35 | 29.2 | 28.7 | 42.8 | 26.2 | 70 | 58.4 | 57.4 | 85.6 | 3.19 | 2.47 | 3 | 6.2 | 0.066 | 11.5 | 11.5 | 0.66617 | 67.7 | 90.6 | 0.1705 | 0.0426 | 13.851 | 12.588 | 13.568 | 0.98 | 1.655 | 2.266 | 8.619 | 2.8662 | 30.19 | 4.8 | 10.8 | 2019-10-07
2019-10-08 | Click Here | 0:00 | 6.04 | 5.23 | 5.15 | 5.41 | 5.47 | 8.19 | 7.62 | 1.86 | 2.1 | 2.17 | 2.15 | 37 | 30 | 21 | 1 | 0 | 0 | 0.509 | 0.406 | 0.917 | 0.112 | 0.177 | 0.236 | 13.8 | 35.8 | 30.2 | 30.4 | 42.9 | 27.6 | 71.6 | 60.4 | 60.8 | 85.8 | 3 | 2.51 | 2.9 | 5.4 | 0.157 | 12.8 | 11.6 | 0.73414 | 67.7 | 92.1 | 0.1694 | 0.0357 | 15.57 | 12.58 | 13.52 | 0.94 | 1.639 | 2.24 | 8.497 | 2.9441 | 30.47 | 4.8 | 10.8 | 2019-10-08
2019-10-09 | Click Here | 0:00 | 5.98 | 5.14 | 5.18 | 5.07 | 5.14 | 7.03 | 8.09 | 1.89 | 2.16 | 2.2 | 2.23 | 38 | 33 | 23 | 3 | 1 | 0 | 0.492 | 0.337 | 1.021 | 0.128 | 0.181 | 0.227 | 13.6 | 34.4 | 30.6 | 30.2 | 44.1 | 27.2 | 68.8 | 61.2 | 60.4 | 88.2 | 3.06 | 2.62 | 3 | 5.7 | 0.136 | 12.9 | 11.8 | 0.64673 | 67.9 | 91.9 | 0.1692 | 0.0359 | 14.744 | 12.161 | 12.986 | 0.825 | 1.533 | 2.277 | 8.616 | 2.9567 | 28.68 | 4.8 | 10.8 | 2019-10-09
2019-10-10 | Click Here | 0:00 | 6.05 | 4.9 | 5.33 | 4.97 | 5.1 | 7.25 | 7.11 | 1.73 | 2 | 2.01 | 2.24 | 37 | 32 | 15 | 1 | 0 | 0 | 0.481 | 0.347 | 0.603 | 0.081 | 0.173 | 0.194 | 14.1 | 32.7 | 29.5 | 29.7 | 42.7 | 28.2 | 65.4 | 59 | 59.4 | 85.4 | 3.1 | 2.54 | 2.9 | 5.9 | 0.113 | 12.2 | 11.8 | 0.55932 | 67.7 | 92 | 0.1694 | 0.0358 | 13.51 | 12.43 | 13.4 | 0.97 | 1.565 | 2.305 | 8.56 | 2.8993 | 30.42 | 4.8 | 10.8 | 2019-10-10
2019-10-11 | Click Here | 0:00 | 6.37 | 5.27 | 5.03 | 5.13 | 5.15 | 7.58 | 6.7 | 1.76 | 1.82 | 2.1 | 2.16 | 36 | 29 | 12 | 0 | 0 | 0 | 0.561 | 0.366 | 0.499 | 0.127 | 0.312 | 0.25 | 14.2 | 33.3 | 30.1 | 29.7 | 41.5 | 28.4 | 66.6 | 60.2 | 59.4 | 83 | 3.15 | 2.39 | 3 | 5.8 | 0.094 | 12.5 | 11.8 | 0.51218 | 67.8 | 92.6 | 0.1687 | 0.0332 | 13.53 | 12.27 | 13.23 | 0.96 | 1.603 | 2.331 | 7.965 | 2.6922 | 30.51 | 4.8 | 10.8 | 2019-10-11
2019-10-12 | Click Here | 0:00 | 6.29 | 5.31 | 5.24 | 5.16 | 5.2 | 7.59 | 7.65 | 1.69 | 1.85 | 2.05 | 2.01 | 34 | 0 | 13 | 0 | 0 | 0 | 0.365 | 0.213 | 0.501 | 0.119 | 0.264 | 0.215 | 14.2 | 32.9 | 31 | 30.1 | 41.4 | 28.4 | 65.8 | 62 | 60.2 | 82.8 | 2.98 | 2.47 | 3 | 5.9 | 0.098 | 12.4 | 11.6 | 0.37269 | 67.4 | 92.1 | 0.1695 | 0.0347 | 14.1 | 12.89 | 13.9 | 1.01 | 1.46 | 2.361 | 8.325 | 2.5627 | 0 | 4.8 | 10.8 | 2019-10-12
2019-10-13 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-10-13
2019-10-14 | Click Here | 0:00 | 6.22 | 5.26 | 5.25 | 5.1 | 5.12 | 7.04 | 8.03 | 1.73 | 1.98 | 2.09 | 2.12 | 36 | 30 | 11 | 0 | 0 | 0 | 0.371 | 0.237 | 0.487 | 0.093 | 0.152 | 0.146 | 14.6 | 34.5 | 30.9 | 31.1 | 45 | 29.2 | 69 | 61.8 | 62.2 | 90 | 2.99 | 2.52 | 2.9 | 6.2 | 0.081 | 13.6 | 12.2 | 0.95134 | 67.6 | 92.3 | 0.1693 | 0.0344 | 14.026 | 12.011 | 13.96 | 1.949 | 1.513 | 2.372 | 8.844 | 3.1913 | 30.85 | 4.8 | 10.8 | 2019-10-14
2019-10-15 | Click Here | 0:00 | 6.17 | 5.21 | 5.29 | 5.15 | 5.16 | 7.69 | 7.73 | 1.76 | 2.01 | 2.11 | 2.16 | 38 | 31 | 9 | 0 | 0 | 0 | 0.394 | 0.237 | 0.47 | 0.068 | 0.172 | 0.257 | 15.1 | 34.7 | 31.1 | 31.4 | 44.9 | 30.2 | 69.4 | 62.2 | 62.8 | 89.8 | 3.16 | 2.49 | 3 | 5.9 | 0.074 | 13.5 | 12 | 0.49856 | 67.7 | 92.6 | 0.1689 | 0.0324 | 12.82 | 12.52 | 12.52 | 0 | 1.516 | 2.369 | 8.635 | 2.7186 | 30.77 | 4.8 | 10.8 | 2019-10-15
2019-10-16 | Click Here | 0:00 | 5.93 | 5.3 | 5.28 | 5.26 | 5.28 | 7.97 | 7.72 | 1.76 | 1.89 | 2.09 | 2.15 | 27 | 21 | 6 | 0 | 0 | 0 | 0.581 | 0.439 | 0.125 | 0.122 | 0.203 | 0.179 | 14.4 | 34.6 | 30.1 | 30.4 | 45.1 | 28.8 | 69.2 | 60.2 | 60.8 | 90.2 | 3.13 | 2.36 | 3.1 | 6 | 0.19 | 12.7 | 11.6 | 0.54331 | 67.8 | 91.4 | 0.1683 | 0.039 | 13.17 | 11.85 | 12.82 | 0.97 | 1.573 | 2.342 | 8.401 | 2.7033 | 30.28 | 4.8 | 10.8 | 2019-10-16
2019-10-17 | Click Here | 0:00 | 6.27 | 5.38 | 5.36 | 5.27 | 5.22 | 7.56 | 7.53 | 1.72 | 1.89 | 2.15 | 2.1 | 29 | 23 | 15 | 2 | 0 | 0 | 0.548 | 0.403 | 0.563 | 0.128 | 0.21 | 0.171 | 14.3 | 31.7 | 29.9 | 29.8 | 43.6 | 28.6 | 63.4 | 59.8 | 59.6 | 87.2 | 2.96 | 2.46 | 3 | 5.8 | 0.181 | 12.6 | 11.7 | 0.63655 | 67.9 | 92.2 | 0.1682 | 0.0353 | 13.99 | 12.75 | 13.74 | 0.99 | 1.504 | 2.349 | 8.3 | 2.8266 | 30.51 | 4.8 | 10.4 | 2019-10-17
2019-10-18 | Click Here | 0:00 | 6.14 | 5.34 | 5.31 | 5.19 | 5.17 | 7.12 | 7 | 1.8 | 1.94 | 2.09 | 2.11 | 34 | 26 | 14 | 0 | 0 | 0 | 0.474 | 0.397 | 0.471 | 0.101 | 0.196 | 0.255 | 14.6 | 32 | 30.2 | 29.9 | 43.9 | 29.2 | 64 | 60.4 | 59.8 | 87.8 | 3.09 | 2.51 | 3.2 | 6 | 0.107 | 12.6 | 11.5 | 0.66274 | 68 | 93.1 | 0.1674 | 0.0307 | 12.556 | 11.509 | 12.492 | 0.983 | 1.579 | 2.36 | 8.087 | 2.8027 | 30.26 | 4.8 | 10.4 | 2019-10-18
2019-10-19 | Click Here | 0:00 | 6.19 | 5.3 | 5.23 | 5.14 | 5.12 | 7.41 | 7.37 | 1.77 | 1.9 | 2.14 | 2.07 | 39 | 31 | 14 | 1 | 0 | 0 | 0.39 | 0.407 | 0.468 | 0.081 | 0.104 | 0.176 | 15.1 | 32.6 | 30.4 | 30 | 43.7 | 30.2 | 65.2 | 60.8 | 60 | 87.4 | 3.01 | 2.47 | 3 | 5.7 | 0.097 | 12.5 | 11.6 | 0.82711 | 67.4 | 92.5 | 0.172 | 0.0341 | 13.26 | 11.93 | 12.93 | 1 | 0 | 0 | 0 | 2.9371 | 29.86 | 4.8 | 10.4 | 2019-10-19
2019-10-20 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-10-20
2019-10-21 | Click Here | 0:00 | 6.11 | 5.38 | 5.3 | 5.3 | 5.33 | 7.92 | 7.44 | 1.76 | 1.93 | 2.07 | 1.96 | 29 | 23 | 14 | 2 | 0 | 0 | 0.615 | 0.447 | 0.716 | 0.12 | 0.195 | 0.149 | 14.2 | 34.1 | 29.5 | 29.7 | 43.7 | 28.4 | 68.2 | 59 | 59.4 | 87.4 | 3.07 | 2.39 | 2.9 | 5.8 | 0.197 | 11.9 | 11.3 | 0.56561 | 66.1 | 91.9 | 0.1795 | 0.0367 | 13.55 | 12.3 | 13.24 | 0.94 | 1.54 | 2.392 | 8.216 | 2.6856 | 30.98 | 4.8 | 10.4 | 2019-10-21
2019-10-22 | Click Here | 0:00 | 6.13 | 5.26 | 5.32 | 5.28 | 5.34 | 7.79 | 7.38 | 1.59 | 1.74 | 1.93 | 1.92 | 28 | 22 | 13 | 0 | 0 | 0 | 0.599 | 0.384 | 0.834 | 0.122 | 0.206 | 0.156 | 15.4 | 35.5 | 30.3 | 30.5 | 43.2 | 30.8 | 71 | 60.6 | 61 | 86.4 | 3.1 | 2.44 | 3.1 | 6 | 0.182 | 13.7 | 11.2 | 1.0748 | 63 | 90.6 | 0.2005 | 0.0426 | 13.89 | 12.66 | 13.62 | 0.96 | 1.521 | 2.392 | 8.386 | 3.0048 | 30.51 | 4.8 | 10 | 2019-10-22
2019-10-23 | Click Here | 0:00 | 6.08 | 5.3 | 5.33 | 5.27 | 5.29 | 7.54 | 7.78 | 1.63 | 1.79 | 1.94 | 1.99 | 30 | 24 | 16 | 1 | 0 | 0 | 0.479 | 0.367 | 0.791 | 0.11 | 0.191 | 0.187 | 15.2 | 34.9 | 30.5 | 30.7 | 44.1 | 30.4 | 69.8 | 61 | 61.4 | 88.2 | 3.04 | 2.47 | 3 | 5.7 | 0.117 | 13.5 | 11.1 | 0.81896 | 62.7 | 91 | 0.2029 | 0.0407 | 13.272 | 11.964 | 12.932 | 0.968 | 1.456 | 2.373 | 8.597 | 2.829 | 30.42 | 4.8 | 10 | 2019-10-23
2019-10-24 | Click Here | 0:00 | 6.13 | 5.39 | 5.33 | 5.22 | 5.24 | 6.95 | 7.72 | 1.42 | 1.71 | 1.94 | 2.03 | 34 | 27 | 14 | 1 | 0 | 0 | 0.413 | 0.357 | 0.695 | 0.086 | 0.157 | 0.219 | 14.8 | 34.9 | 29.8 | 29.9 | 42.1 | 29.6 | 69.8 | 59.6 | 59.8 | 84.2 | 3.12 | 2.54 | 3 | 5.7 | 0.079 | 13.6 | 11.2 | 0.77929 | 63.6 | 91.1 | 0.1948 | 0.0402 | 13.28 | 12.03 | 12.97 | 0.94 | 1.516 | 2.529 | 8.598 | 2.8293 | 29.83 | 4.8 | 9.8 | 2019-10-24
2019-10-25 | Click Here | 0:00 | 6.11 | 5.41 | 5.41 | 5.19 | 5.25 | 6.75 | 7 | 1.66 | 1.91 | 1.97 | 2 | 35 | 28 | 16 | 1 | 0 | 0 | 0.442 | 0.386 | 0.713 | 0.104 | 0.161 | 0.173 | 14 | 35.4 | 29.1 | 29.3 | 42.9 | 28 | 70.8 | 58.2 | 58.6 | 85.8 | 3.01 | 2.6 | 3.1 | 5.9 | 0.091 | 12.2 | 10.9 | 0.72511 | 63.8 | 91.3 | 0.1946 | 0.04 | 13.042 | 11.797 | 12.773 | 0.976 | 1.494 | 2.39 | 8.808 | 2.7851 | 30.16 | 4.8 | 10 | 2019-10-25
2019-10-26 | Click Here | 0:00 | 6.15 | 5.3 | 5.38 | 5.12 | 5.16 | 6.67 | 6.69 | 1.6 | 1.92 | 1.96 | 1.94 | 38 | 31 | 15 | 0 | 0 | 0 | 0.493 | 0.419 | 0.691 | 0.084 | 0.213 | 0.24 | 13.7 | 34.7 | 28.7 | 28.9 | 41.7 | 27.4 | 69.4 | 57.4 | 57.8 | 83.4 | 3.07 | 2.57 | 3 | 5.6 | 0.104 | 11.2 | 10.7 | 0.9007 | 63.6 | 91.9 | 0.1948 | 0.0367 | 13.33 | 12.06 | 13.02 | 0.96 | 0 | 0 | 0 | 2.8407 | 29.45 | 4.8 | 10 | 2019-10-26
2019-10-27 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.8665 | 0 | 0 | 0 | 0 | 13.776 | 12.486 | 13.462 | 0.976 | 1.498 | 2.354 | 8.242 | 2.7965 | 0 | 4.8 | 10.3 | 2019-10-27
2019-10-28 | Click Here | 0:00 | 6.09 | 5.28 | 5.29 | 5.16 | 5.2 | 7.19 | 7.36 | 1.67 | 1.98 | 2.01 | 1.96 | 39 | 31 | 14 | 0 | 0 | 0 | 0.407 | 0.456 | 0.647 | 0.079 | 0.176 | 0.237 | 14.1 | 35 | 28.8 | 28.9 | 42.4 | 28.2 | 70 | 57.6 | 57.8 | 84.8 | 3.12 | 2.59 | 3.1 | 5.8 | 0.098 | 11.1 | 10.5 | 0.84362 | 63.9 | 92.4 | 0.1987 | 0.0335 | 13.98 | 12.659 | 13.638 | 0.979 | 1.623 | 2.432 | 7.917 | 2.7536 | 30.6 | 4.8 | 10.3 | 2019-10-28
2019-10-29 | Click Here | 0:00 | 6.13 | 5.21 | 5.3 | 5.17 | 5.19 | 7.29 | 7.36 | 1.62 | 1.89 | 1.93 | 1.94 | 39 | 0 | 17 | 1 | 0 | 0 | 0.371 | 0.406 | 0.704 | 0.101 | 0.137 | 0.206 | 13.9 | 34.7 | 28.5 | 28.7 | 41.6 | 27.8 | 69.4 | 57 | 57.4 | 83.2 | 3.05 | 2.49 | 3 | 6.1 | 0.104 | 10.9 | 10.3 | 0.78652 | 64 | 92.1 | 0.198 | 0.0348 | 13.86 | 12.62 | 13.59 | 0.97 | 1.575 | 2.504 | 8.541 | 2.7765 | 30.29 | 4.8 | 10.3 | 2019-10-29
2019-10-30 | Click Here | 0:00 | 6.09 | 5.33 | 5.3 | 5.14 | 5.18 | 7.28 | 7.42 | 1.7 | 1.99 | 2.09 | 2.17 | 37 | 30 | 19 | 1 | 0 | 0 | 0.309 | 0.457 | 0.691 | 0.104 | 0.141 | 0.217 | 14.2 | 35.4 | 29.3 | 29.6 | 44.7 | 28.4 | 70.8 | 58.6 | 59.2 | 89.4 | 3.16 | 2.59 | 2.9 | 5.8 | 0.084 | 10.7 | 10.3 | 0.85622 | 63.7 | 92.4 | 0.1995 | 0.0334 | 13.458 | 12.17 | 13.18 | 1.01 | 1.575 | 2.504 | 7.854 | 2.8262 | 30.48 | 4.8 | 10.3 | 2019-10-30
2019-10-31 | Click Here | 0:00 | 6.07 | 5.27 | 5.32 | 5.17 | 5.2 | 7.29 | 7.56 | 1.67 | 1.88 | 2.09 | 2.14 | 37 | 29 | 19 | 0 | 0 | 0 | 0.334 | 0.386 | 0.619 | 0.117 | 0.147 | 0.199 | 14.3 | 35.1 | 28.8 | 29 | 43.9 | 28.6 | 70.2 | 57.6 | 58 | 47.8 | 3.11 | 2.49 | 2.9 | 5.7 | 0.076 | 10.7 | 10.4 | 0.69639 | 0 | 0 | 0 | 0 | 13.67 | 12.53 | 13.46 | 0.93 | 1.575 | 2.504 | 8.451 | 2.7164 | 30.72 | 4.8 | 10.3 | 2019-10-31
2019-11-01 | Click Here | 0:00 | 5.92 | 5.35 | 5.34 | 5.23 | 5.27 | 7.84 | 7.45 | 1.72 | 1.83 | 2.02 | 1.93 | 36 | 29 | 20 | 1 | 0 | 0 | 0.818 | 0.585 | 1.21 | 0.125 | 0.189 | 0.161 | 14.3 | 33.2 | 29.3 | 28.7 | 41.7 | 28.6 | 66.4 | 58.6 | 57.4 | 83.4 | 3.14 | 2.34 | 3 | 5.8 | 0.181 | 11.9 | 10 | 0.60211 | 66.5 | 92.2 | 0.1771 | 0.0349 | 13.8 | 12.55 | 13.51 | 0.96 | 1.575 | 2.504 | 7.854 | 2.6321 | 30.51 | 4.8 | 10.3 | 2019-11-01
2019-11-02 | Click Here | 0:00 | 6.01 | 5.34 | 5.31 | 5.26 | 5.29 | 7.71 | 7.67 | 1.73 | 1.91 | 2.07 | 1.96 | 37 | 30 | 18 | 0 | 0 | 0 | 1.401 | 1.984 | 1.17 | 0.116 | 0.254 | 0.226 | 14.4 | 32.6 | 29.4 | 29 | 41.5 | 28.8 | 65.2 | 58.8 | 58 | 83 | 3.2 | 2.51 | 3.1 | 5.9 | 0.172 | 11.8 | 10.1 | 0.7583 | 66.3 | 91.9 | 0.1785 | 0.0361 | 14.6 | 13.45 | 14.41 | 0.96 | 0 | 0 | 0 | 2.8283 | 30.04 | 4.8 | 10 | 2019-11-02
2019-11-03 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-11-03
2019-11-04 | Click Here | 0:00 | 5.86 | 5.14 | 5.28 | 5.1 | 5.19 | 7.23 | 7.45 | 1.67 | 1.81 | 1.98 | 2.12 | 35 | 28 | 14 | 0 | 0 | 0 | 0.869 | 0.758 | 0.97 | 0.104 | 0.345 | 0.301 | 14.3 | 32 | 31.1 | 30 | 40.9 | 28.6 | 64 | 62.2 | 60 | 81.8 | 3.18 | 2.38 | 3.1 | 5.8 | 0.112 | 11.6 | 10 | 0.95964 | 66.5 | 92.3 | 0.1773 | 0.0352 | 13.943 | 12.213 | 13.668 | 1.455 | 1.575 | 2.504 | 7.854 | 2.9296 | 30.51 | 4.8 | 10 | 2019-11-04
2019-11-05 | Click Here | 0:00 | 5.92 | 5.17 | 5.12 | 5.13 | 5.21 | 7.41 | 7.71 | 1.65 | 1.86 | 1.96 | 1.98 | 33 | 26 | 15 | 0 | 0 | 0 | 0.627 | 0.589 | 0.684 | 0.097 | 0.319 | 0.447 | 14.7 | 32.4 | 30.8 | 30.2 | 41.1 | 29.4 | 64.8 | 61.6 | 60.4 | 82.2 | 3.04 | 2.41 | 3 | 6 | 0.098 | 11.4 | 9.9 | 0.57392 | 66.1 | 92.9 | 0.1791 | 0.0317 | 13.98 | 13.72 | 13.72 | 0 | 1.575 | 2.504 | 9.641 | 2.5539 | 30.72 | 4.8 | 10 | 2019-11-05
2019-11-06 | Click Here | 0:00 | 5.64 | 4.69 | 5.13 | 4.81 | 5.34 | 7.81 | 7.56 | 1.78 | 1.9 | 2.06 | 1.95 | 35 | 28 | 18 | 1 | 0 | 0 | 1.31 | 0.448 | 1.73 | 0.145 | 0.299 | 0.334 | 13.9 | 33.9 | 29.8 | 28.4 | 42.3 | 27.8 | 67.8 | 59.6 | 56.8 | 84.6 | 3 | 2.44 | 3.1 | 6 | 0.151 | 11.3 | 9.7 | 1.0031 | 64.9 | 93.2 | 0.1874 | 0.0306 | 13.75 | 12.5 | 13.48 | 0.98 | 1.575 | 2.504 | 8.421 | 2.8831 | 30.28 | 4.8 | 10 | 2019-11-06
2019-11-07 | Click Here | 0:00 | 6.14 | 5.36 | 5.32 | 5.17 | 5.21 | 7.57 | 7.45 | 1.69 | 1.88 | 2.02 | 1.98 | 37 | 30 | 20 | 1 | 0 | 0 | 3.54 | 2.439 | 3.14 | 0.156 | 0.609 | 0.488 | 13.9 | 33.6 | 30.1 | 28.6 | 41.9 | 27.8 | 67.2 | 60.2 | 57.2 | 83.8 | 3.05 | 2.38 | 2.9 | 5.8 | 0.143 | 11.1 | 9.5 | 0.97987 | 64.6 | 92.9 | 0.1882 | 0.032 | 13.762 | 12.565 | 13.546 | 0.981 | 1.575 | 2.504 | 7.854 | 2.8299 | 30.51 | 5.2 | 9.8 | 2019-11-07
2019-11-08 | Click Here | 0:00 | 6.04 | 5.27 | 5.32 | 5.2 | 5.29 | 7.69 | 7.8 | 1.72 | 1.94 | 1.92 | 1.68 | 39 | 32 | 18 | 0 | 0 | 0 | 2.19 | 1.326 | 2.91 | 0.137 | 0.417 | 0.281 | 14.1 | 33.9 | 29.9 | 29.4 | 42.4 | 28.2 | 67.8 | 59.8 | 58.8 | 84.8 | 3.07 | 2.42 | 3 | 5.9 | 0.129 | 11 | 9.4 | 0.96291 | 64.7 | 93 | 0.1875 | 0.0316 | 13.361 | 12.071 | 13.052 | 0.981 | 1.575 | 2.504 | 7.854 | 2.8129 | 30.86 | 5.2 | 9.8 | 2019-11-08
2019-11-09 | Click Here | 0:00 | 6.04 | 5.24 | 5.35 | 5.17 | 5.19 | 7.47 | 7.79 | 1.64 | 1.86 | 1.94 | 1.77 | 39 | 32 | 19 | 1 | 0 | 0 | 1.17 | 1.207 | 2.46 | 0.117 | 0.298 | 0.346 | 13.9 | 32.6 | 28.7 | 29.1 | 42.5 | 27.8 | 65.2 | 57.4 | 58.2 | 85 | 3.17 | 2.57 | 2.9 | 6.1 | 0.141 | 10.9 | 9.4 | 0.99427 | 64.6 | 92.4 | 0.1882 | 0.0357 | 13.078 | 12.07 | 13.06 | 0.99 | 0 | 0 | 0 | 2.8143 | 30.39 | 5.2 | 9.8 | 2019-11-09
2019-11-10 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-11-10
2019-11-11 | Click Here | 0:00 | 5.83 | 5.27 | 5.34 | 5.23 | 5.37 | 7.7 | 7.66 | 1.79 | 1.98 | 1.98 | 1.71 | 37 | 30 | 18 | 1 | 0 | 0 | 1.38 | 1.143 | 2.13 | 0.194 | 0.421 | 0.457 | 12.6 | 30.9 | 29.4 | 27.3 | 38.6 | 25.2 | 61.8 | 58.8 | 54.6 | 77.2 | 3.03 | 2.51 | 3.1 | 6 | 0.133 | 10.6 | 7.6 | 0.74794 | 64.8 | 93.3 | 0.1875 | 0.0303 | 14.69 | 13.61 | 14.51 | 0.9 | 0 | 0 | 0 | 2.6479 | 31.45 | 5.2 | 9.8 | 2019-11-11
2019-11-12 | Click Here | 0:00 | 5.79 | 5.2 | 5.31 | 5.24 | 5.3 | 7.65 | 7.15 | 1.75 | 1.82 | 1.88 | 1.82 | 45 | 38 | 62 | 8 | 7 | 0 | 1.35 | 1.029 | 4.84 | 0.537 | 0.599 | 0.583 | 12.6 | 30.8 | 29 | 27.2 | 38.3 | 25.2 | 61.6 | 58 | 54.4 | 76.6 | 3.18 | 2.47 | 3.1 | 5.8 | 0.048 | 8.1 | 7.4 | 0.87561 | 63.6 | 91.4 | 0.1964 | 0.0384 | 15.52 | 12.97 | 13.94 | 0.97 | 1.575 | 2.504 | 7.854 | 2.8556 | 30.98 | 5.2 | 9.6 | 2019-11-12
2019-11-13 | Click Here | 0:00 | 5.95 | 5.26 | 5.3 | 5.2 | 5.24 | 7.37 | 7.42 | 1.69 | 1.89 | 1.92 | 1.97 | 41 | 34 | 57 | 3 | 1 | 0 | 1.44 | 1.07 | 2.94 | 0.212 | 0.37 | 0.442 | 12.9 | 31.1 | 29.1 | 28.6 | 39.4 | 25.8 | 62.2 | 58.2 | 57.2 | 78.8 | 3.13 | 2.51 | 3 | 5.7 | 0.056 | 9 | 7.1 | 0.74909 | 61.9 | 92.2 | 0.2074 | 0.0352 | 16.252 | 13.968 | 14.934 | 0.966 | 1.575 | 2.504 | 7.854 | 2.7491 | 30.27 | 5.2 | 9.6 | 2019-11-13
2019-11-14 | Click Here | 0:00 | 5.91 | 5.19 | 5.26 | 5.2 | 5.25 | 7.36 | 7.42 | 1.77 | 1.94 | 2.04 | 2.1 | 39 | 33 | 10 | 0 | 0 | 0 | 0.94 | 1.241 | 0.426 | 0.079 | 0.247 | 0.365 | 12.6 | 31.7 | 28.6 | 27.4 | 37.5 | 25.2 | 63.4 | 57.2 | 54.8 | 75 | 3.19 | 2.59 | 3.1 | 5.8 | 0.047 | 8.6 | 7.8 | 0.72793 | 58.7 | 92.2 | 0.2329 | 0.035 | 13.84 | 12.61 | 13.59 | 0.98 | 1.575 | 2.504 | 7.854 | 2.8579 | 29.92 | 5.2 | 9.6 | 2019-11-14
2019-11-15 | Click Here | 0:00 | 5.81 | 4.9 | 5.21 | 4.88 | 4.92 | 6.24 | 7.11 | 1.71 | 1.92 | 2 | 2.03 | 37 | 30 | 11 | 1 | 0 | 0 | 0.913 | 0 | 0.452 | 0.069 | 0.257 | 0.321 | 12.6 | 33.4 | 29 | 27.1 | 36.2 | 25.2 | 66.8 | 58 | 54.2 | 72.4 | 3.13 | 2.62 | 3 | 5.9 | 0.052 | 8.7 | 6.9 | 0.77018 | 58.9 | 92.5 | 0.2327 | 0.0347 | 13.46 | 12.27 | 13.24 | 0.97 | 1.575 | 2.504 | 7.854 | 2.8402 | 30.64 | 5.2 | 9.6 | 2019-11-15
2019-11-16 | Click Here | 0:00 | 5.87 | 5.09 | 5.38 | 5.1 | 5.2 | 6.25 | 6.87 | 1.62 | 1.9 | 1.97 | 1.88 | 39 | 33 | 13 | 0 | 0 | 0 | 0.901 | 0 | 0.473 | 0.072 | 0.306 | 0.443 | 12.1 | 30.9 | 29.9 | 27.5 | 36.5 | 24.2 | 61.8 | 59.8 | 55 | 63 | 3.18 | 2.54 | 3.1 | 5.8 | 0.072 | 7 | 6.7 | 0.89626 | 55.6 | 87.6 | 0.2543 | 0.0572 | 13.34 | 12.18 | 13.13 | 0.95 | 0 | 0 | 0 | 2.8463 | 30.65 | 5.2 | 9.6 | 2019-11-16
2019-11-17 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 13.79 | 12.5 | 13.47 | 0.97 | 0 | 0 | 0 |  | 0 | 5.2 | 9.8 | 2019-11-17
2019-11-18 | Click Here | 0:00 | 5.92 | 5.07 | 5.04 | 5.15 | 5.21 | 7.04 | 7.2 | 1.64 | 1.94 | 1.92 | 1.98 | 36 | 28 | 11 | 0 | 0 | 0 | 0.869 | 0 | 0.427 | 0.061 | 0.284 | 0.401 | 12.5 | 30.7 | 30.2 | 28.9 | 37.3 | 25 | 61.4 | 60.4 | 57.8 | 74.6 | 3.19 | 2.49 | 3 | 6.1 | 0.081 | 6.9 | 6.7 | 0.93155 | 55.9 | 95.7 | 0.2521 | 0.0187 | 13.106 | 11.763 | 12.745 | 0.982 | 1.575 | 2.504 | 7.854 | 2.8815 | 30.4 | 5.2 | 9.8 | 2019-11-18
2019-11-19 | Click Here | 0:00 | 5.91 | 5.17 | 5.07 | 5.2 | 5.24 | 7.65 | 7.05 | 1.76 | 1.94 | 1.97 | 1.99 | 39 | 32 | 14 | 1 | 0 | 0 | 0.624 | 0.001 | 0.495 | 0.061 | 0.417 | 0.893 | 12.5 | 32 | 30.6 | 31 | 36.5 | 25 | 64 | 61.2 | 62 | 73 | 3.14 | 2.49 | 3 | 5.7 | 0.071 | 7.6 | 6.1 | 1.0016 | 62.7 | 109.7 | 0.2029 | 0.04 | 13.39 | 12.21 | 13.2 | 0.99 | 1.575 | 2.504 | 8.131 | 2.9516 | 30.68 | 5.2 | 9.8 | 2019-11-19
2019-11-20 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-11-20
2019-11-21 | Click Here | 0:00 | 6.01 | 5.19 | 5.13 | 5.22 | 5.24 | 7.47 | 7.51 | 1.77 | 1.99 | 2.04 | 2.13 | 41 | 33 | 11 | 0 | 0 | 0 | 0.476 | 0 | 0.422 | 0.054 | 0.304 | 0.418 | 12.2 | 32.4 | 29.9 | 30.6 | 35.8 | 24.4 | 64.8 | 59.8 | 61.2 | 71.6 | 3.16 | 2.51 | 3 | 5.7 | 0.109 | 7.6 | 6 | 0.79757 | 63 | 99.8 | 0.2001 | 0.0009 | 12.89 | 12.57 | 12.57 | 0 | 1.575 | 2.504 | 8.491 | 2.7876 | 30.38 | 5.2 | 9.8 | 2019-11-21
2019-11-22 | Click Here | 0:00 | 6.08 | 5.15 | 5.15 | 5.1 | 5.03 | 7.25 | 7.47 | 1.65 | 1.89 | 2.02 | 2.04 | 53 | 45 | 19 | 3 | 0 | 0 | 1.39 | 1.127 | 0.847 | 0.135 | 1.69 | 0.421 | 13.2 | 32.2 | 27.3 | 27.5 | 37.1 | 26.4 | 64.4 | 54.6 | 55 | 74.2 | 4.04 | 5.34 | 3.2 | 6.1 | 0.026 | 9.2 | 5.8 | 0.97064 | 56.2 | 88.6 | 0.2496 | 0.0524 | 13.16 | 12.08 | 13.04 | 0.96 | 1.575 | 2.504 | 8.001 | 2.9006 | 30.04 | 5.2 | 9.8 | 2019-11-22
2019-11-23 | Click Here | 0:00 | 6.05 | 5.17 | 5.15 | 5.14 | 5.21 | 7.47 | 7.52 | 1.71 | 1.93 | 2.1 | 2.13 | 45 | 38 | 16 | 1 | 0 | 0 | 0.841 | 0.796 | 0.644 | 0.112 | 0.756 | 0.605 | 13.1 | 32 | 27.4 | 27.1 | 38 | 26.2 | 64 | 54.8 | 54.2 | 76 | 3.79 | 4.38 | 3.1 | 6.1 | 0.031 | 9.1 | 5.7 |  | 56.1 | 89.5 | 0.2498 | 0.0516 | 11.69 | 11.66 | 12.65 | 0.99 | 0 | 0 | 0 |  | 30.28 | 5.2 | 9.8 | 2019-11-23
2019-11-24 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-11-24
2019-11-25 | Click Here | 0:00 | 5.79 | 4.86 | 5.12 | 4.9 | 4.89 | 6.26 | 7.36 | 1.69 | 1.91 | 2.07 | 2.08 | 43 | 35 | 14 | 1 | 0 | 0 | 0.792 | 0.683 | 0.612 | 0.104 | 0.497 | 0.469 | 12.4 | 33.5 | 28.1 | 28 | 37 | 24.8 | 67 | 56.2 | 56 | 74 | 3.68 | 2.62 | 3 | 6.6 | 0.042 | 6.9 | 5.6 | 0.77938 | 50.8 | 87.2 | 0.2935 | 0.0592 | 13.494 | 12.243 | 13.22 | 0.977 | 1.575 | 2.504 | 7.854 | 2.8194 | 29.17 | 5.2 | 9.8 | 2019-11-25
2019-11-26 | Click Here | 0:00 | 6.04 | 5.24 | 5.23 | 5.13 | 5.16 | 6.28 | 6.77 | 1.74 | 1.96 | 1.9 | 1.92 | 45 | 38 | 12 | 0 | 0 | 0 | 0.732 | 0.667 | 0.739 | 0.104 | 0.535 | 0.527 | 11.9 | 30.5 | 26.4 | 26.2 | 36.1 | 23.8 | 61 | 52.8 | 52.4 | 72.2 | 3.51 | 4.03 | 3.1 | 5.7 | 0.38 | 5.9 | 5.5 | 0.81671 | 55.7 | 87.9 | 0.2541 | 0.557 | 12.9 | 11.75 | 12.73 | 0.98 | 1.575 | 2.504 | 7.671 | 2.8967 | 29.64 | 5.2 | 9.9 | 2019-11-26
2019-11-27 | Click Here | 0:00 | 5.97 | 5.31 | 5.23 | 5.23 | 5.24 | 7.4 | 6.94 | 1.83 | 1.91 | 1.97 | 1.87 | 45 | 37 | 16 | 3 | 0 | 0 | 0.86 | 0.624 | 0.903 | 0.139 | 0.523 | 0.581 | 11.6 | 26.6 | 26.7 | 26.2 | 36.9 | 23.2 | 53.2 | 53.4 | 52.4 | 73.8 | 3.25 | 3.85 | 3 | 5.8 | 0.008 | 5.6 | 5.4 | 0.58576 | 56.8 | 88.8 | 0.2454 | 0.0516 | 13.42 | 12.2 | 13.16 | 0.96 | 1.575 | 2.504 | 7.854 | 2.6258 | 30.51 | 5.2 | 10.3 | 2019-11-27
2019-11-28 | Click Here | 0:00 | 5.56 | 5.05 | 5.15 | 5.08 | 5.21 | 7.49 | 7.27 | 1.75 | 1.87 | 1.89 | 1.73 | 49 | 40 | 17 | 2 | 0 | 0 | 0.709 | 0.561 | 1.17 | 0.139 | 0.515 | 0.503 | 12.5 | 34.7 | 27.2 | 26.4 | 36.1 | 25 | 69.4 | 54.4 | 52.8 | 72.2 | 3.28 | 3.84 | 3.1 | 5.9 | 0.009 | 7.1 | 5.2 | 0.41759 | 57.1 | 89.2 | 0.2446 | 0.0495 | 12.98 | 12.68 | 12.68 | 0 | 0 | 0 | 0 | 2.4476 | 30.28 | 5.2 | 10.3 | 2019-11-28
2019-11-29 | Click Here | 0:00 | 5.79 | 5.1 | 5.02 | 5.17 | 5.23 | 7.29 | 7.36 | 1.69 | 1.9 | 2.04 | 2.18 | 43 | 37 | 14 | 1 | 0 | 0 | 0.492 | 0.537 | 1.07 | 0.109 | 0.476 | 0.567 | 12.7 | 34.4 | 27 | 26.8 | 37.4 | 25.4 | 68.8 | 54 | 53.6 | 74.8 | 3.27 | 3.57 | 3 | 6 | 0.01 | 7 | 5.2 | 0.77583 | 57.7 | 90 | 0.2409 | 0.0461 | 12.751 | 11.578 | 12.545 | 0.967 | 0 | 0 | 0 | 2.8758 | 29.4 | 5.2 | 10.3 | 2019-11-29
2019-11-30 | Click Here | 0:00 | 5.87 | 5.17 | 5.08 | 5.19 | 5.22 | 7.54 | 7.66 | 1.77 | 2.04 | 2.17 | 2.2 | 49 | 41 | 17 | 2 | 0 | 0 | 0.604 | 0.718 | 0.784 | 0.107 | 0.401 | 0.601 | 12.4 | 34.7 | 27.2 | 27 | 36.8 | 24.8 | 69.4 | 54.4 | 54 | 73.6 | 3.11 | 3.8 | 3.1 | 5.8 | 0.072 | 6.9 | 5.1 | 0.67108 | 57.4 | 89.7 | 0.2437 | 0.0476 | 13.45 | 12.29 | 13.24 | 0.95 | 0 | 0 | 0 | 2.8511 | 30.62 | 5.2 | 10.3 | 2019-11-30
2019-12-01 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-12-01
2019-12-02 | Click Here | 0:00 | 5.18 | 4.11 | 5.08 | 4.06 | 4.23 | 7.25 | 7.44 | 1.76 | 1.96 | 2.09 | 2.25 | 54 | 47 | 25 | 1 | 0 | 0 | 1.08 | 0.805 | 1.54 | 0.153 | 0.421 | 0.449 | 11.7 | 31.4 | 26.3 | 26.1 | 35.7 | 23.4 | 62.8 | 52.6 | 52.2 | 71.4 | 3.36 | 3.46 | 3 | 5.7 | 0.041 | 5.8 | 5.1 | 0.56235 | 53.6 | 88.5 | 0.2708 | 0.0528 | 13.69 | 12.65 | 13.65 | 1 | 1.575 | 2.504 | 7.854 | 2.5324 | 29.11 | 5.5 | 10.3 | 2019-12-02
2019-12-03 | Click Here | 0:00 | 6.17 | 5.06 | 5.07 | 5.2 | 5.25 | 7.55 | 7.58 | 1.72 | 1.87 | 2 | 1.81 | 49 | 42 | 18 | 1 | 0 | 0 | 0.996 | 0.832 | 1.21 | 0.183 | 0.518 | 0.513 | 11.8 | 31 | 26.2 | 26.3 | 35 | 23.6 | 62 | 52.4 | 52.6 | 70 | 3.53 | 3.78 | 2.9 | 5.6 | 0.011 | 6.3 | 4.8 | 1.0789 | 56.3 | 89.4 | 0.2493 | 0.0486 | 12.9 | 11.82 | 12.79 | 0.97 | 1.575 | 2.504 | 7.854 | 3.0489 | 30.98 | 5.5 | 10.3 | 2019-12-03
2019-12-04 | Click Here | 0:00 | 6.1 | 5.15 | 5.03 | 5.4 | 5.49 | 8.3 | 7.21 | 1.7 | 1.93 | 1.97 | 2.01 | 58 | 50 | 17 | 1 | 0 | 0 | 0.541 | 0.67 | 0.677 | 0.109 | 0.4 | 0.508 | 12.1 | 34.4 | 27 | 26.1 | 36.2 | 24.2 | 68.8 | 54 | 52.2 | 72.4 | 3.41 | 4.03 | 3.2 | 5.9 | 0.104 | 6.7 | 5 | 0.67992 | 54 | 91.8 | 0.2674 | 0.0368 | 13.49 | 12.47 | 13.41 | 0.94 | 0 | 0 | 0 | 2.8099 | 29.88 | 5.5 | 10.3 | 2019-12-04
2019-12-05 | Click Here | 0:00 | 5.47 | 4.95 | 5.12 | 5.03 | 5.08 | 7.42 | 7.72 | 1.77 | 1.95 | 2.06 | 2.13 | 47 | 40 | 16 | 0 | 0 | 0 | 0.58 | 0.561 | 0.96 | 0.154 | 0.557 | 0.549 | 12.2 | 30.9 | 27.1 | 26.6 | 34.7 | 24.4 | 61.8 | 54.2 | 53.2 | 69.4 | 3.37 | 3.93 | 3.1 | 5.9 | 0.013 | 5.7 | 5 | 0.62452 | 56.5 | 89.6 | 0.2502 | 0.0479 | 12.4 | 12.08 | 12.08 | 0 | 1.575 | 2.504 | 7.854 | 2.7345 | 0 | 5.5 | 10.3 | 2019-12-05
2019-12-06 | Click Here | 0:00 | 6.12 | 5.14 | 5.13 | 5.18 | 5.27 | 6.84 | 7.38 | 1.79 | 1.99 | 2.16 | 2.21 | 46 | 39 | 17 | 1 | 0 | 0 | 0.531 | 0.527 | 0.837 | 0.114 | 0.562 | 0.538 | 11.9 | 34 | 27.5 | 27 | 37.6 | 23.8 | 68 | 55 | 54 | 75.2 | 3.34 | 4.11 | 3 | 5.7 | 0.024 | 5.4 | 4.9 | 0.9624 | 52.2 | 87.5 | 0.2817 | 0.0585 | 13.36 | 11.59 | 13.5 | 1.91 | 1.575 | 2.504 | 7.854 | 3.1024 | 27.71 | 5.5 | 10.3 | 2019-12-06
2019-12-07 | Click Here | 0:00 | 6.07 | 5.13 | 5.1 | 5.19 | 5.24 | 7.24 | 7.31 | 1.82 | 2.03 | 2.1 | 2.16 | 49 | 41 | 16 | 1 | 0 | 0 | 0.511 | 0.574 | 0.799 | 0.104 | 0.504 | 0.562 | 12.2 | 33.9 | 28.1 | 27.7 | 37.5 | 24.4 | 67.8 | 56.2 | 55.4 | 75 | 3.29 | 4.08 | 3.1 | 5.8 | 0.037 | 5.4 | 4.8 | 0.63143 | 52.6 | 88.3 | 0.2794 | 0.0539 | 13.39 | 12.17 | 13.13 | 0.96 | 0 | 0 | 0 | 2.8814 | 30.38 | 5.5 | 10.3 | 2019-12-07
2019-12-08 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.60772 | 0 | 0 | 0 | 0 | 13.409 | 12.13 | 13.103 | 0.973 | 0 | 0 | 0 | 2.8677 | 0 | 5.5 | 10.3 | 2019-12-08
2019-12-09 | Click Here | 0:00 | 6.07 | 5.14 | 5.09 | 5.19 | 5.24 | 7.49 | 7.4 | 1.82 | 2.07 | 2.2 | 2.34 | 47 | 40 | 17 | 1 | 0 | 0 | 0.543 | 0.567 | 0.797 | 0.104 | 0.371 | 0.457 | 12.3 | 33.8 | 26.7 | 27.2 | 38.1 | 24.6 | 67.6 | 53.4 | 54.4 | 76.2 | 3.32 | 4.1 | 3.1 | 5.7 | 0.057 | 5.3 | 4.8 | 0.84834 | 53.1 | 89.9 | 0.2779 | 0.0477 | 14.25 | 12.16 | 14.11 | 1.95 | 0 | 0 | 0 | 3.1283 | 30.6 | 5.5 | 10.3 | 2019-12-09
2019-12-10 | Click Here | 0:00 | 6.01 | 5.19 | 5.25 | 5.3 | 5.4 | 7.29 | 7.4 | 1.77 | 1.96 | 2.09 | 2.13 | 49 | 43 | 19 | 2 | 0 | 0 | 0.496 | 0.514 | 0.798 | 0.112 | 0.394 | 0.452 | 12.2 | 34.1 | 26.9 | 27.4 | 37.7 | 24.4 | 68.2 | 53.8 | 54.8 | 75.4 | 3.31 | 4.09 | 3.1 | 5.9 | 0.054 | 5.9 | 5.2 | 0.53433 | 57.1 | 90.3 | 0.2446 | 0.0441 | 13.6 | 13.35 | 13.35 | 0 | 1.575 | 2.504 | 7.854 | 2.7743 | 31.26 | 5.5 | 10.3 | 2019-12-10
2019-12-11 | Click Here | 0:00 | 6.32 | 5.12 | 5.23 | 5.26 | 5.27 | 5.47 | 5.99 | 1.72 | 1.91 | 2.07 | 2.14 | 50 | 42 | 20 | 3 | 1 | 0 | 0.471 | 0.443 | 0.914 | 0.136 | 0.493 | 0.508 | 12 | 35.4 | 28.7 | 26.9 | 29.1 | 24 | 70.8 | 57.4 | 53.8 | 58.2 | 3.24 | 4.04 | 3 | 5.8 | 0.042 | 6.2 | 4.7 | 0.81686 | 55.1 | 89.3 | 0.2586 | 0.0487 | 13.525 | 12.402 | 13.38 | 0.978 | 1.575 | 2.504 | 7.884 | 2.9469 | 30.49 | 5.5 | 10.3 | 2019-12-11
2019-12-12 | Click Here | 0:00 | 6.22 | 5.1 | 5.24 | 5.14 | 5.19 | 6.5 | 7.09 | 1.78 | 2.03 | 2.14 | 2.26 | 49 | 42 | 18 | 1 | 0 | 0 | 0.462 | 0.436 | 0.896 | 0.121 | 0.613 | 0.664 | 11.4 | 35.1 | 28 | 26.4 | 35.3 | 22.8 | 70.2 | 56 | 52.8 | 70.6 | 3.3 | 4.07 | 3.1 | 5.5 | 0.068 | 5.7 | 4.7 | 0.83955 | 55.3 | 89.6 | 0.2584 | 0.0484 | 13.8 | 12.64 | 13.63 | 0.99 | 1.575 | 2.504 | 9.551 | 3.0095 | 30.97 | 5.5 | 10.3 | 2019-12-12
2019-12-13 | Click Here | 0:00 | 5.53 | 4.97 | 5.37 | 5.17 | 5.23 | 7.07 | 7.05 | 1.74 | 1.91 | 2.08 | 2.2 | 52 | 45 | 21 | 3 | 0 | 0 | 0.643 | 0.459 | 1.36 | 0.148 | 0.711 | 0.766 | 11.6 | 31.5 | 26.1 | 27.8 | 35.6 | 23.2 | 63 | 52.2 | 55.6 | 71.2 | 3.37 | 3.96 | 3.1 | 5.7 | 0.024 | 6.1 | 4.6 | 0.12118 | 53.5 | 89.1 | 0.2728 | 0.05 | 14.02 | 12.91 | 13.86 | 0.95 | 0 | 0 | 0 | 2.1712 | 30.28 | 5.5 | 10.3 | 2019-12-13
2019-12-14 | Click Here | 0:00 | 5.37 | 5.01 | 5.14 | 5.02 | 5.06 | 7.11 | 7.09 | 1.71 | 1.87 | 1.97 | 1.84 | 50 | 43 | 19 | 1 | 0 | 0 | 0.656 | 0.495 | 1.33 | 0.152 | 0.537 | 0.576 | 11.7 | 28.8 | 26.3 | 27.6 | 34.9 | 23.4 | 57.6 | 52.6 | 55.2 | 69.8 | 3.24 | 3.45 | 3 | 5.9 | 0.029 | 6 | 4.5 | 0.46267 | 53.7 | 90.2 | 0.272 | 0.0489 | 13.81 | 12.8 | 13.75 | 0.95 | 0 | 0 | 0 | 2.5027 | 30.51 | 5.5 | 10.3 | 2019-12-14
2019-12-15 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-12-15
2019-12-16 | Click Here | 0:00 | 6.13 | 5.21 | 5.2 | 5.24 | 5.27 | 6.94 | 7.32 | 1.76 | 2.01 | 2.07 | 2.14 | 49 | 43 | 20 | 2 | 0 | 0 | 0.526 | 0.397 | 0.994 | 0.113 | 0.606 | 0.684 | 12.4 | 33.2 | 26.2 | 36.9 | 36.4 | 24.8 | 66.4 | 52.4 | 53.8 | 72.8 | 3.22 | 3.71 | 3.1 | 5.8 | 0.033 | 6.9 | 4.5 | 0.81061 | 56.3 | 90.1 | 0.2494 | 0.0452 | 14.268 | 12.607 | 14.297 | 1.69 | 0 | 0 | 0 | 2.9706 | 30.93 | 5.5 | 10.3 | 2019-12-16
2019-12-17 | Click Here | 0:00 | 6.17 | 5.14 | 5.18 | 5.23 | 5.26 | 5.4 | 5.81 | 1.7 | 1.86 | 1.96 | 1.91 | 50 | 44 | 26 | 4 | 1 | 0 | 0.432 | 0.443 | 1.612 | 0.118 | 0.307 | 0.16 | 12.7 | 30.9 | 26.3 | 27 | 30 | 25.4 | 61.8 | 52.6 | 54 | 60 | 3.25 | 3.87 | 3 | 5.1 | 0.028 | 7.8 | 4.6 | 0.54219 | 56.5 | 90 | 0.2492 | 0.0453 | 15.69 | 13 | 13.94 | 0.94 | 1.575 | 2.504 | 8.921 | 2.7722 | 30.8 | 5.6 | 10.3 | 2019-12-17
2019-12-18 | Click Here | 0:00 | 5.89 | 5.14 | 5.17 | 5.24 | 5.27 | 4.97 | 5.54 | 1.83 | 1.96 | 1.98 | 2.33 | 48 | 41 | 24 | 3 | 0 | 0 | 0.638 | 0.473 | 2.67 | 0.307 | 0.207 | 0.145 | 12.4 | 33.8 | 26.2 | 26.6 | 30.4 | 24.8 | 67.6 | 52.4 | 53.2 | 60.8 | 3.01 | 3.16 | 3.1 | 5.4 | 0.249 | 7.3 | 4.3 | 0.32002 | 53 | 88.8 | 0.2755 | 0.0514 | 14.82 | 13.04 | 13.04 | 0 | 1.575 | 2.504 | 7.854 | 2.38 | 31.22 | 5.6 | 10.3 | 2019-12-18
2019-12-19 | Click Here | 0:00 | 5.89 | 5.25 | 5.23 | 5.27 | 5.28 | 4.82 | 5.54 | 1.83 | 1.91 | 1.9 | 1.96 | 47 | 40 | 18 | 1 | 0 | 0 | 0.605 | 0.462 | 1.32 | 0.265 | 0.234 | 0.16 | 12.3 | 30 | 26.4 | 28.9 | 30.8 | 24.6 | 60 | 52.8 | 57.8 | 61.6 | 3.27 | 3.61 | 3.1 | 5.5 | 0.227 | 7 | 4.6 | 0.79908 | 53.6 | 89.4 | 0.2706 | 0.0484 | 13.735 | 12.609 | 13.584 | 0.975 | 0 | 0 | 0 | 2.8391 | 30.98 | 5.6 | 10.3 | 2019-12-19
2019-12-20 | Click Here | 0:00 | 5.96 | 5.31 | 5.24 | 5.36 | 5.39 | 7 | 6.54 | 1.87 | 2.04 | 2.06 | 2.12 | 44 | 37 | 13 | 0 | 0 | 0 | 0.441 | 0.426 | 0.492 | 0.092 | 0.241 | 0.596 | 12.6 | 30.4 | 26.2 | 28.6 | 34.8 | 25.2 | 60.8 | 52.4 | 57.2 | 69.6 | 3.26 | 3.99 | 3 | 5.9 | 0.17 | 6.8 | 4.5 | 0.84215 | 53.9 | 91.7 | 0.2684 | 0 | 14.103 | 13.107 | 14.08 | 0.973 | 0 | 0 | 0 | 2.9421 | 30.38 | 5.6 | 10.3 | 2019-12-20
2019-12-21 | Click Here | 0:00 | 6 | 5.19 | 5.23 | 5.31 | 5.34 | 7.65 | 7.71 | 1.84 | 1.99 | 2.09 | 2.14 | 54 | 46 | 10 | 0 | 0 | 0 | 0.389 | 0.411 | 0.317 | 0.054 | 0.347 | 0.456 | 12.2 | 30 | 26.5 | 27.9 | 35.3 | 24.4 | 60 | 53 | 55.8 | 70.6 | 3.09 | 3.86 | 2.9 | 5.8 | 0.117 | 6.6 | 4.4 | 0.88244 | 54.2 | 90.4 | 0.2663 | 0.041 | 13.55 | 12.42 | 13.38 | 0.96 | 0 | 0 | 0 | 2.9824 | 30.4 | 5.6 | 10.3 | 2019-12-21
2019-12-22 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2019-12-22
2019-12-23 | Click Here | 0:00 | 5.91 | 5.18 | 5.19 | 5.25 | 5.27 | 7.34 | 8.34 | 1.75 | 1.95 | 2.2 | 1.87 | 50 | 42 | 21 | 5 | 0 | 0 | 0.554 | 0.404 | 1.07 | 0.168 | 0.545 | 0.517 | 12.4 | 34.1 | 26.3 | 27.2 | 38.4 | 24.8 | 68.2 | 52.6 | 54.4 | 76.8 | 3.05 | 3.19 | 3.1 | 6 | 0.029 | 7.2 | 4.7 | 0.5424 | 52.8 | 89.4 | 0.2774 | 0.0485 | 14.18 | 13.11 | 14.09 | 0.98 | 1.575 | 2.504 | 7.854 | 2.6724 | 31.45 | 5.6 | 10.1 | 2019-12-23
2019-12-24 | Click Here | 0:00 | 5.96 | 5.23 | 5.19 | 5.26 | 5.28 | 7.45 | 6.98 | 1.95 | 2.08 | 2.13 | 2.56 | 49 | 41 | 18 | 1 | 0 | 0 | 0.519 | 0.39 | 1.12 | 0.14 | 0.498 | 0.454 | 12.9 | 33 | 26.3 | 26.8 | 30.5 | 25.8 | 66 | 52.6 | 53.6 | 61 | 2.97 | 3.61 | 3 | 5.8 | 0.033 | 7.9 | 4.4 | 0.65787 | 53.1 | 89.6 | 0.2758 | 0.0474 | 14.093 | 13.113 | 14.091 | 0.978 | 0 | 0 | 0 | 2.8979 | 30.51 | 5.6 | 10.1 | 2019-12-24
2019-12-25 | Click Here | 0:00 | 6.04 | 5.17 | 5.22 | 5.24 | 5.26 | 7.76 | 7.99 | 1.92 | 2.16 | 2.11 | 2.04 | 51 | 42 | 15 | 0 | 0 | 0 | 0.404 | 0.386 | 0.674 | 0.104 | 0.399 | 0.514 | 13.1 | 33.4 | 26.7 | 26.9 | 31.4 | 26.2 | 66.8 | 53.4 | 53.8 | 62.8 | 3.09 | 3.79 | 3.1 | 6 | 0.041 | 7.7 | 4.3 | 0.8477 | 53.7 | 90.9 | 0.2704 | 0.041 | 13.081 | 11.754 | 12.732 | 0.978 | 0 | 0 | 0 | 2.9077 | 30.76 | 5.6 | 10.1 | 2019-12-25
2019-12-26 | Click Here | 0:00 | 5.94 | 5.17 | 5.21 | 5.29 | 5.31 | 7.98 | 8 | 1.89 | 2.1 | 2.12 | 2.19 | 48 | 40 | 14 | 1 | 0 | 0 | 0.319 | 0.347 | 0.681 | 0.113 | 0.424 | 0.501 | 12.6 | 32.9 | 25.6 | 26.1 | 32.4 | 25.2 | 65.8 | 51.2 | 52.2 | 64.8 | 3.21 | 4.33 | 3 | 6.2 | 0.076 | 7.6 | 4.2 | 0.80165 | 53.9 | 91.4 | 0.2689 | 0.0381 | 13.59 | 12.42 | 13.39 | 0.97 | 1.575 | 2.504 | 7.854 | 2.9017 | 30.63 | 5.6 | 10.1 | 2019-12-26
2019-12-27 | Click Here | 0:00 | 6.14 | 5.11 | 5.22 | 5.19 | 5.22 | 6.24 | 7.83 | 1.72 | 1.91 | 1.94 | 1.9 | 49 | 43 | 16 | 1 | 0 | 0 | 0.342 | 0.336 | 0.693 | 0.094 | 0.468 | 0.524 | 12.2 | 35.1 | 26.5 | 27 | 35.2 | 24.4 | 70.2 | 53 | 54 | 70.4 | 3.18 | 4.43 | 2.9 | 6.4 | 0.063 | 5.9 | 4.4 | 1.169 | 53.7 | 91.2 | 0.269 | 0.0383 | 14.15 | 13.14 | 14.12 | 0.98 | 1.575 | 2.504 | 7.854 | 3.179 | 30.69 | 5.6 | 9.9 | 2019-12-27
2019-12-28 | Click Here | 0:00 | 6.12 | 5.16 | 5.23 | 5.21 | 5.24 | 6.83 | 7.04 | 1.75 | 1.96 | 2.07 | 2.04 | 48 | 43 | 15 | 1 | 0 | 0 | 0.369 | 0.361 | 0.671 | 0.091 | 0.414 | 0.503 | 12.1 | 34.8 | 26.3 | 26.8 | 35.6 | 24.2 | 69.6 | 52.6 | 53.6 | 71.2 | 3.23 | 4.31 | 3 | 6 | 0.054 | 5.9 | 4.5 | 0.86896 | 53.9 | 91.5 | 0.2689 | 0.038 | 14.52 | 13.49 | 14.47 | 0.98 | 0 | 0 | 0 | 2.929 | 30.69 | 5.6 | 9.9 | 2019-12-28
2019-12-29 | Click Here | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0.78424 | 0 | 0 | 0 | 0 | 13.802 | 12.534 | 13.503 | 0.969 | 0 | 0 | 0 | 2.9042 | 0 | 5.6 | 9.9 | 2019-12-29
2019-12-30 | Click Here | 0:00 | 6.09 | 5.24 | 5.19 | 5.3 | 5.34 | 7.01 | 6.76 | 1.82 | 2.04 | 2.17 | 2.32 | 49 | 42 | 15 | 1 | 0 | 0 | 0.247 | 0.331 | 0.691 | 0.113 | 0.46 | 0.691 | 12.7 | 35.1 | 26.7 | 27.2 | 33.4 | 25.4 | 70.2 | 53.4 | 54.4 | 66.8 | 3.18 | 4.06 | 2.9 | 5.7 | 0.107 | 6.5 | 4.8 | 0.75732 | 54.9 | 92 | 0.2599 | 0.0361 | 14.048 | 12.923 | 13.898 | 0.975 | 0 | 0 | 0 | 2.9373 | 30.06 | 5.6 | 9.9 | 2019-12-30
2019-12-31 | Click Here | 0:00 | 6.09 | 5.17 | 5.22 | 5.24 | 5.27 | 7.04 | 7.18 | 1.84 | 2.07 | 2.1 | 2.25 | 51 | 43 | 13 | 0 | 0 | 0 | 0.267 | 0.304 | 0.541 | 0.113 | 0.472 | 0.584 | 12.5 | 34.8 | 26.4 | 27 | 34.2 | 25 | 69.6 | 52.8 | 54 | 68.4 | 3.07 | 4.05 | 3.1 | 6.1 | 0.096 | 6.5 | 4.7 | 0.94734 | 55.1 | 91.8 | 0.2571 | 0.0389 | 14.03 | 12.97 | 13.94 | 0.97 | 1.575 | 2.504 | 7.854 | 3.0873 | 30.44 | 5.6 | 9.9 | 2019-12-31
|  |  | pH | [6 empty] | Chlorine |  |  |  | Colour | [5 empty] | Turbidity | [5 empty] | Total Dissolved Solids |  |  |  |  | Conductivity |  |  |  |  | Hardness |  | Alkalinity |  | Aluminum | Temperature |  | Cl Demand | UVT |  | UVA |  | Flows withinin plant |  |  |  | Flows from plant |  |  | Chemical Dosages
|  |  | Raw | PTC | PTC (OL) | SWC | Filter | Finish (OL) | Finish | Free | Total | Sample | Analyzer | Raw A | Raw T | SWC A | Filter A | Finish A | Finish T | Raw | Raw (OL) | SWC | Filter | Finish | Finish (OL) | Raw | PTC | SWC | Filter | Finish | Raw | PTC | SWC | Filter | Finish | Raw | Finish | Raw | Finish | Finish (Free) | Raw | Finish |  | Raw | Filter | Raw | Filter | Raw | Finish | Filter | Backwash | Bishop's | Botwood | GFW | Chlorine | Alum | Lime (Pre) | Lime (Post)
January 2019 Average |  |  | 6.02 | 5.42 | 5.36 | 5.45 | 5.45 | 6.83 | 7.13 | 1.64 | 1.97 | 1.91 | 1.94 | 56.24 | 49.24 | 18.4 | 1.5 | 1 | #DIV/0! | 0.34 | 0.48 | 1 | 0.13 | 0.27 | 0.46 | 13.85 | 33.38 | 26.36 | 27.4 | 37.22 | 27.7 | 66.77 | 52.71 | 54.8 | 74.44 | 3.24 | 18.22 | 3.37 | 6.05 | 0.11 | 6.8 | 3.35 | 1.07 | 48.6 | 88.55 | 0.32 | 0.05 | 14.69 | 12.73 | 13.79 | 1.1 | 1.63 | 2.45 | 8.52 | 3.01 | 29.52 | 5.06 | 10.59
February 2019 Average |  |  | 5.89 | 5.43 | 5.4 | 5.49 | 5.52 | 7.29 | 7.26 | 1.79 | 2.04 | 2.06 | 2.06 | 52.96 | 46.5 | 16.71 | 1.45 | #DIV/0! | #DIV/0! | 0.24 | 0.35 | 0.71 | 0.1 | 0.21 | 0.34 | 13.63 | 32.5 | 26.58 | 26.77 | 40.09 | 27.25 | 64.99 | 53.17 | 53.54 | 80.18 | 3.16 | 16.24 | 3.5 | 6.07 | 0.08 | 6.46 | 3.37 | 0.73 | 49.07 | 90.41 | 0.32 | 0.04 | 14.72 | 13.62 | 14.52 | 1.01 | 1.66 | 2.73 | 9.08 | 2.79 | 29.47 | 5.16 | 10.58
March 2019 Average |  |  | 5.9 | 5.35 | 5.35 | 5.41 | 5.47 | 7.05 | 7.27 | 1.66 | 1.95 | 1.92 | 1.89 | 54.5 | 47.81 | 21.19 | 1.56 | 2 | #DIV/0! | 0.23 | 0.31 | 0.93 | 0.11 | 0.28 | 0.54 | 15.38 | 33.85 | 27.22 | 27.62 | 39.38 | 30.76 | 65.85 | 54.44 | 55.24 | 78.94 | 2.92 | 7.53 | 4.08 | 7.2 | 0.12 | 7.11 | 3.51 | 0.89 | 48.14 | 88.18 | 0.32 | 0.05 | 15.14 | 13.93 | 14.89 | 1 | 1.7 | 2.74 | 9.51 | 2.83 | 30.04 | 4.16 | 10.62
April 2019 Average |  |  | 5.8 | 5.2 | 5.23 | 5.21 | 5.23 | 6.7 | 6.94 | 1.69 | 1.95 | 1.95 | 1.99 | 58.96 | 51.36 | 21.2 | 1.94 | 1.5 | #DIV/0! | 0.22 | 0.35 | 0.87 | 0.09 | 0.25 | 0.45 | 12.72 | 31.95 | 26.65 | 26.9 | 36.37 | 25.45 | 63.9 | 53.3 | 53.8 | 72.74 | 3.03 | 2.39 | 3.63 | 6.53 | 0.12 | 8.29 | 3.79 | 0.8 | 47.72 | 88.13 | 0.32 | 0.06 | 14.04 | 13.05 | 13.95 | 1.01 | 1.66 | 2.63 | 8.78 | 2.78 | 30.39 | 5.36 | 12.16
May 2019 Average |  |  | 5.9 | 5.24 | 5.26 | 5.24 | 5.29 | 7.32 | 7.37 | 1.67 | 1.94 | 1.99 | 2.04 | 50.78 | 43.26 | 17.85 | 1.7 | #DIV/0! | #DIV/0! | 0.24 | 0.31 | 0.51 | 0.07 | 0.19 | 0.25 | 11.04 | 30.83 | 26.34 | 26.34 | 34.67 | 22.19 | 61.67 | 52.68 | 52.68 | 69.34 | 3.16 | 2.82 | 3.1 | 6 | 0.04 | 11.53 | 6.33 | 0.67 | 56.87 | 90 | 0.25 | 0.05 | 13.72 | 13 | 13.82 | 1 | 1.58 | 2.51 | 8.98 | 2.7 | 29.42 | 6.11 | 10.95
June 2019 Average |  |  | 6.17 | 5.18 | 5.15 | 5.13 | 5.18 | 7.12 | 7.31 | 1.58 | 1.91 | 2 | 2.13 | 40.96 | 33.79 | 13.46 | 1.43 | 1 | #DIV/0! | 0.28 | 0.41 | 0.43 | 0.07 | 0.14 | 0.19 | 12.75 | 34.63 | 31.84 | 31.88 | 39.58 | 25.5 | 69.21 | 63.76 | 63.76 | 79.16 | 3.15 | 2.55 | 3.13 | 6.07 | 0.04 | 17.14 | 12.45 | 0.8 | 59.66 | 90.53 | 0.22 | 0.04 | 14.2 | 13.2 | 13.2 | 1.04 | 1.4 | 2.43 | 9.61 | 2.91 | 28.98 | 5.82 | 10.58
July 2019 Average |  |  | 6.08 | 5.27 | 5.24 | 5.17 | 5.22 | 7.3 | 7.31 | 1.61 | 1.83 | 2.05 | 2.22 | 36.65 | 29.62 | 11.62 | 2 | #DIV/0! | #DIV/0! | 0.35 | 0.28 | 0.85 | 0.1 | 0.17 | 0.13 | 14.26 | 35.9 | 34.23 | 33.9 | 44.45 | 28.52 | 71.8 | 68.46 | 67.8 | 88.9 | 3.24 | 2.55 | 3.07 | 5.88 | 0.07 | 19.11 | 16.49 | 0.65 | 59.62 | 90.67 | 0.22 | 0.04 | 14.71 | 13.68 | 14.68 | 1 | 1.48 | 2.27 | 9.65 | 2.92 | 29.12 | 5.64 | 9.2
August 2019 Average |  |  | 6.11 | 5.18 | 5.2 | 5.09 | 5.14 | 7.12 | 7.28 | 1.68 | 1.89 | 2.09 | 2.29 | 32.23 | 25.52 | 9.73 | 1.43 | #DIV/0! | #DIV/0! | 0.35 | 0.16 | 0.51 | 0.09 | 0.23 | 0.24 | 15.85 | 39.12 | 37.87 | 37.52 | 48.5 | 31.7 | 78.32 | 75.72 | 75.02 | 96.57 | 3.18 | 2.53 | 3.1 | 5.99 | 0.08 | 20.89 | 19.1 | 0.97 | 64.41 | 91.31 | 0.19 | 0.04 | 14.64 | 13.48 | 14.42 | 1.01 | 1.52 | 2.39 | 9.18 | 3.16 | 29.97 | 4.85 | 9.3
September 2019 Average |  |  | 6.03 | 5.08 | 5.1 | 5.07 | 5.09 | 7.14 | 7.24 | 1.78 | 1.99 | 2.14 | 2.03 | 43.52 | 31 | 12.32 | 1.27 | 1 | #DIV/0! | 1.05 | 0.25 | 0.71 | 0.11 | 0.34 | 0.45 | 13.74 | 35.23 | 32.7 | 32.78 | 44.29 | 27.53 | 70.46 | 65.41 | 65.57 | 88.46 | 3.17 | 2.45 | 3.06 | 5.76 | 0.06 | 15.37 | 15.42 | 0.99 | 67.43 | 91.17 | 0.17 | 0.04 | 13.77 | 12.35 | 13.38 | 1.16 | 1.45 | 2.2 | 9.07 | 3.01 | 30.34 | 4.28 | 10.92
October 2019 Average |  |  | 6.11 | 5.25 | 5.26 | 5.18 | 5.21 | 7.38 | 7.48 | 1.73 | 1.94 | 2.08 | 2.08 | 35.22 | 28.52 | 15.19 | 1.33 | 1 | #DIV/0! | 0.48 | 0.36 | 0.67 | 0.11 | 0.21 | 0.24 | 14.18 | 34.55 | 29.9 | 29.96 | 43.21 | 28.36 | 69.1 | 59.79 | 59.92 | 85.01 | 3.08 | 2.5 | 3.01 | 5.86 | 0.11 | 12.31 | 11.53 | 0.73 | 66.31 | 91.7 | 0.18 | 0.04 | 13.68 | 12.35 | 13.27 | 1 | 1.56 | 2.4 | 8.46 | 2.86 | 30.29 | 4.79 | 10.53
November 2019 Average |  |  | 5.91 | 5.16 | 5.21 | 5.14 | 5.21 | 7.3 | 7.38 | 1.72 | 1.91 | 1.99 | 1.97 | 40.68 | 33.48 | 18.96 | 1.94 | 4 | #DIV/0! | 1.09 | 0.93 | 1.35 | 0.13 | 0.45 | 0.45 | 13.04 | 32.27 | 28.88 | 28.17 | 38.63 | 26.07 | 64.54 | 57.77 | 56.34 | 76.86 | 3.24 | 2.94 | 3.04 | 5.91 | 0.09 | 8.91 | 7.35 | 0.81 | 60.68 | 92.24 | 0.22 | 0.06 | 13.63 | 12.47 | 13.35 | 0.99 | 1.58 | 2.5 | 8.04 | 2.8 | 30.37 | 5.12 | 9.89
December 2019 Average |  |  | 5.96 | 5.11 | 5.18 | 5.18 | 5.23 | 6.92 | 7.12 | 1.79 | 1.98 | 2.07 | 2.13 | 49.5 | 42.35 | 17.73 | 1.71 | 1 | #DIV/0! | 0.52 | 0.48 | 0.99 | 0.13 | 0.45 | 0.5 | 12.24 | 32.92 | 26.67 | 27.46 | 34.47 | 24.48 | 65.83 | 53.35 | 54.15 | 68.94 | 3.24 | 3.89 | 3.04 | 5.8 | 0.07 | 6.47 | 4.65 | 0.73 | 54.29 | 90.07 | 0.27 | 0.05 | 13.83 | 12.62 | 13.58 | 1.08 | 1.58 | 2.5 | 8.07 | 2.85 | 30.48 | 5.55 | 10.2
2019 Average |  |  | 5.99 | 5.24 | 5.25 | 5.23 | 5.27 | 7.13 | 7.26 | 1.69 | 1.94 | 2.02 | 2.06 | 45.93 | 38.57 | 16.19 | 1.62 | 1.67 | #DIV/0! | 0.45 | 0.38 | 0.79 | 0.1 | 0.27 | 0.35 | 13.56 | 33.93 | 29.61 | 29.73 | 40.08 | 27.14 | 67.71 | 59.23 | 59.4 | 79.97 | 3.15 | 5.47 | 3.26 | 6.09 | 0.08 | 11.72 | 8.99 | 0.82 | 56.94 | 90.25 | 0.25 | 0.05 | 14.23 | 13.04 | 13.97 | 1.03 | 1.56 | 2.47 | 8.95 | 2.89 | 29.87 | 5.16 | 10.44
2019 WTP Flow Assessment
| Month | Finish | BF | Botwood | GFW | Communuity Flow | Percent Diff (%) |  |  | Max Value | Min Value
| January | 12.73 | 1.63 | 2.45 | 8.52 | 12.6 | 1.021% |  | Finish | 17.23 | 8.924
| February | 13.62 | 1.66 | 2.73 | 9.08 | 13.47 | 1.101% |  | GFW | 13.12 | 5.131
| March | 13.93 | 1.7 | 2.74 | 9.51 | 13.95 | 0.1436% |  | Botwood | 3.205 | 2.023
| April | 13.05 | 1.66 | 2.63 | 8.78 | 13.07 | 0.1533% |  | Bishops | 1.984 | 1.267
| May | 13 | 1.58 | 2.51 | 8.98 | 13.07 | 0.5385%
| June | 13.2 | 1.4 | 2.43 | 9.61 | 13.44 | 1.818%
| July | 13.68 | 1.48 | 2.27 | 9.18 | 12.93 | 5.482%
| August | 13.48 | 1.5 | 2.27 | 9.75 | 13.52 | 0.2967%
| September | 12.35 | 1.45 | 2.2 | 9.07 | 12.72 | 2.996%
| October | 12.35 | 1.56 | 2.4 | 8.46 | 12.42 | 0.5668%
| November | 12.47 | 1.58 | 2.5 | 8.04 | 12.12 | 2.807%
| December | 12.62 | 1.58 | 2.5 | 8.07 | 12.15 | 3.724%
| Yr Average | 13.04 | 1.565 | 2.4692 | 8.9208 | 12.955 | 1.721%
2019 WTP UV Averages
| MONTHLY AVERAGES | UVT RAW | UVT Filter | UVA RAW | UVA Filter |  |  | Max Value | Min Value
| January | 48.6 | 88.55 | 0.323 | 0.0523 |  | UVT Raw | 72.1 | 13.7
| February | 49.07 | 90.41 | 0.315 | 0.0437 |  | UVT Filter | 109.7 | 81.1
| March | 48.14 | 88.18 | 0.319 | 0.0543 |  | UVA Raw | 0.8621 | 0.2074
| April | 47.72 | 88.13 | 0.321 | 0.055 |  | UVA Filter | 0.557 | 0.0009
| May | 56.87 | 90 | 0.046 | 0.0463
| June | 59.66 | 90.53 | 0.044 | 0.0439
| July | 59.62 | 90.67 | 0.225 | 0.0424
| August | 64.41 | 91.31 | 0.19 | 0.0396
| September | 67.43 | 91.17 | 0.171 | 0.0423
| October | 66.31 | 91.7 | 0.179 | 0.0376
| November | 60.68 | 92.24 | 0.22 | 0.06
| December | 54.29 | 90.07 | 0.27 | 0.05
| Yr Average | 56.9 | 90.2467 | 0.21858 | 0.047283
2019 WTP Averages
| MONTHLY AVERAGES | Temp. (RAW) | Temp. (Finish) | Alkalinity (RAW) | Alkalinity (Finish) | Aluminum (Finish) | Hardness (RAW) | Hardness (Finish) |  |  | Max Value | Min Value
| January | 6.8 | 3.35 | 3.37 | 6.05 | 0.111 | 3.24 | 18.22 |  | Temp. Raw | 22.8 | 3.4
| February | 6.46 | 3.37 | 3.5 | 6.07 | 0.084 | 3.16 | 16.24 |  | Temp. Finish | 19.6 | 3
| March | 7.11 | 3.51 | 4.08 | 7.2 | 0.125 | 2.92 | 7.53 |  | Alkalinity Raw | 4.9 | 2.3
| April | 8.29 | 3.79 | 3.63 | 6.53 | 0.119 | 3.03 | 2.39 |  | Alkalinity Finish | 10.2 | 3
| May | 11.53 | 6.33 | 3.1 | 6 | 0.037 | 3.16 | 2.82 |  | Hardness Raw | 4.04 | 2.45
| June | 17.14 | 12.45 | 3.13 | 6.07 | 0.044 | 3.15 | 2.55 |  | Hardness Finish | 21.6 | 1.58
| July | 19.11 | 16.49 | 3.07 | 5.88 | 0.075 | 3.24 | 2.55
| August | 20.89 | 19.1 | 3.1 | 5.99 | 0.077 | 3.18 | 2.53
| September | 15.37 | 15.42 | 3.06 | 5.76 | 0.061 | 3.17 | 2.45
| October | 12.31 | 11.53 | 3.01 | 5.86 | 0.105 | 3.08 | 2.5
| November | 8.91 | 7.35 | 3.04 | 5.91 | 0.095 | 3.24 | 2.94
| December | 6.47 | 4.65 | 3.04 | 5.8 | 0.07 | 3.24 | 3.89
| Average | 11.6992 | 8.945 | 3.2608 | 6.0933 | 0.083583 | 3.1508 | 5.5508
2019 WTP Averages
| MONTHLY AVERAGES | TDS (RAW) | TDS (Finish) | Conduct. (RAW) | Conduct. (Finish) |  |  | Max Value | Min Value
| January | 13.85 | 37.22 | 27.7 | 74.44 |  | TDS (RAW) | 17.2 | 9.7
| February | 13.63 | 40.09 | 27.25 | 80.18 |  | TDS (Finish) | 50.6 | 28.6
| March | 15.38 | 39.38 | 30.76 | 78.94 |  | Conduct. (RAW) | 34.4 | 19.8
| April | 12.72 | 36.37 | 25.45 | 72.74 |  | Conduct. (Finish) | 100.2 | 47.8
| May | 11.04 | 34.67 | 22.19 | 69.34
| June | 12.75 | 39.58 | 25.5 | 79.16
| July | 14.26 | 44.45 | 28.52 | 88.9
| August | 15.85 | 48.5 | 31.7 | 96.57
| September | 13.74 | 44.29 | 27.53 | 88.46
| October | 14.18 | 43.21 | 28.36 | 85.01
| November | 13.04 | 38.63 | 26.07 | 76.86
| December | 12.23 | 34.47 | 24.48 | 68.94
| Yr Average | 13.5558 | 40.0717 | 27.1258 | 79.9617
| 2019 WTP Averages | [8 empty] | 2019 WTP Averages
| MONTHLY AVERAGES | Color (Raw/Actual) | Color (Raw/True) |  |  | Max Value | Min Value |  |  | MONTHLY AVERAGES | Filter Turbidity | Finish Turbidity | Raw Turbidity
| January | 56.24 | 49.24 |  | Color (Raw/Actual) | 92 | 22 |  |  | January | 0.126 | 0.272 | 0.338 |  |  | >= 1 NTU Finish | 1
| February | 52.96 | 46.5 |  | Color (Raw/True) | 58 | 16 |  |  | February | 0.1 | 0.21 | 0.241
| March | 54.5 | 47.81 | [6 empty] | March | 0.111 | 0.284 | 0.233
| April | 58.96 | 51.36 | [6 empty] | April | 0.09 | 0.251 | 0.215
| May | 50.78 | 43.26 | [6 empty] | May | 0.067 | 0.187 | 0.239
| June | 40.96 | 33.79 | [6 empty] | June | 0.069 | 0.143 | 0.277
| July | 36.65 | 29.62 | [6 empty] | July | 0.1 | 0.17 | 0.35
| August | 32.23 | 25.52 | [6 empty] | August | 0.094 | 0.233 | 0.348
| September | 43.52 | 31 | [6 empty] | September | 0.111 | 0.344 | 1.045
| October | 35.22 | 28.52 | [6 empty] | October | 0.106 | 0.208 | 0.481
| November | 40.68 | 33.48 | [6 empty] | November | 0.131 | 0.453 | 1.09
| December | 49.5 | 42.35 | [6 empty] | December | 0.134 | 0.45 | 0.522
| Average | 46.0167 | 38.5375 | [6 empty] | Average | 0.10325 | 0.26708 | 0.44825
2019 Free Chlorine Assessment
| MONTHLY AVERAGES | Lab Free CL2 | Analyzer (Sample) | % Diff. | Residual Loss |  |  | Max Value | Min Value
| January | 1.64 | 1.94 | 15.46% | 0.3 |  | Free Chlorine | 2.2 | 1.03
| February | 1.79 | 2.06 | 13.11% | 0.27 |  | Analyzer Chlorine | 2.23 | 1.68
| March | 1.66 | 1.89 | 12.17% | 0.23
| April | 1.69 | 1.99 | 15.08% | 0.3
| May | 1.67 | 2.04 | 18.14% | 0.37
| June | 1.58 | 2.13 | 25.82% | 0.55
| July | 1.61 | 2.22 | 27.48% | 0.61
| August | 1.68 | 2.29 | 26.64% | 0.61
| September | 1.78 | 2.03 | 12.32% | 0.25
| October | 1.73 | 2.08 | 16.83% | 0.35
| November | 1.72 | 1.97 | 12.69% | 0.25
| December | 1.79 | 2.13 | 15.96% | 0.34
| Average | 1.695 | 2.0642 | 17.88% | 0.36917